## Validation_Report
check_id | sheet_or_area | status | finding | action_taken | source_page
VAL-001 | Unit_Specs | CORRECTED | The fields named condenser_airflow_lps/cfm contained evaporator-fan airflow values while the cfm column was condenser airflow. | Renamed them to evaporator_fan_nominal_airflow_lps/cfm and added corrected condenser-fan nominal airflow columns. | 4-5
VAL-002 | Unit_Specs | CORRECT | Nominal capacity, tonnage, weights, compressor type/quantity, refrigerant, charges, coil face areas and fan motor data agree with the SI/English physical-data tables. | No change required. | 4-5
VAL-003 | Base_Dimensions | CORRECTED | The workbook retained only H dimension; PDF also provides J and K for sizes 008-014. | Added J/K dimensions and connection/clearance notes. | 9-10
VAL-004 | Electrical_Data | CORRECT | Voltage range, RLA/LRA, OFM/IFM FLA, heater ratings, MCA, MOCP and disconnect data agree with PDF page 34. | No change required; †† text retained where applicable. | 34
VAL-005 | Electric_Heating_Capacities | ADDED | The PDF includes heater accessory part numbers and availability footnotes not represented in the original normalized sheet. | Added Electric_Heat_Part_Numbers. | 33
VAL-006 | Physical_Data_Complete | ADDED | Detailed condenser/evaporator coil, fan, filter, screen and safety-control values were present in the PDF but not fully normalized by model. | Added a complete per-model physical-data sheet. | 4-5
VAL-007 | Performance_Tables | REVIEWED | Raw performance tables from pages 15-29 are present in the workbook. | No graphical chart interpretation added, per user instruction. | 15-29
VAL-008 | Dimensions_Accessories | LIMITED | The original extraction contains OCR-like concatenated dimension text and is not reliable as a normalized table. | Kept original raw sheet for audit; structured roof-curb and connection notes are provided in Base_Dimensions. | 11-12
VAL-009 | Physical_Data_Complete | CORRECTED | High-pressure internal relief was checked by compressor type: reciprocating models 008/009/012 use 3103 kPa (450 psig); scroll models 007/014 use 3448 kPa (500 psig). | Corrected normalized values. | 4-5
VAL-010 | Model_Nomenclature | ADDED | The model-number code, coil-fin options, voltage code, packaging and QA information were graphical/text data on PDF page 3 and were not previously normalized. | Added structured nomenclature sheet. | 3
VAL-011 | Selection_Procedure | ADDED | The SI and English worked selection examples were present in PDF pages 13-14 but not previously normalized. | Added structured selection procedure sheet. | 13-14
VAL-012 | Completeness_Audit | ADDED | Every PDF page section is now mapped to one or more Excel sheets, with raw retention noted where normalization is not appropriate. | Added final audit matrix. | 1-44

## README
field | value
Source file | 50TFFProductData.pdf
Product | Carrier 50TFF007-014 Single-Package Rooftop Units
Workbook purpose | Structured extraction for product-selection software; source page retained for audit.
Units | SI and English values are retained where present in the PDF.
Performance data | Performance_Tables contains every extracted table cell from pages 15-29, indexed by page/table/row/column.
Caveat | Some PDF charts/diagrams are graphical rather than tabular; their page text is preserved in PDF_Text and the tabular values are preserved in Extracted_Tables.
Added sheets | Cooling_Capacity, Fan_Performance, Static_Pressure_Accessories, Fan_Motor_Performance, Dimensions_Accessories, Heater_Ratings, Electric_Heating_Capacities
Grid format | For performance/dimension tables each row is a source table row; col_1..col_20 preserve the table columns with page/table/row keys.
Added sheets | Cooling_Capacity, Fan_Performance, Static_Pressure_Accessories, Fan_Motor_Performance, Dimensions_Accessories, Heater_Ratings, Electric_Heating_Capacities
Grid format | For performance/dimension tables each row is a source table row; col_1..col_20 preserve the table columns with page/table/row keys.
Review status | Reviewed against PDF tables; see Validation_Report. Corrected airflow field naming/values and added structured missing data sheets.
Scope note | Charts/diagrams were not interpreted or normalized, per user instruction; raw PDF text and extracted tables remain available.
Final audit | Complete against all 44 PDF pages: see Completeness_Audit and Validation_Report.
Important scope | Performance tables, raw PDF text, and diagrams are retained. Diagrams are not interpreted, per user instruction.

## Unit_Specs
model | nominal_capacity_kw | nominal_capacity_tons | unit_weight_kg | unit_weight_lb | unit_weight_al_cu_kg | unit_weight_al_cu_lb | durablade_economizer_kg | durablade_economizer_lb | econoMi$er_kg | econoMi$er_lb | roof_curb_kg | roof_curb_lb | compressor_type | compressor_quantity | compressor_oil | refrigerant_type | charge_circuit_1 | charge_circuit_2 | condenser_face_area_sqm | evaporator_fan_nominal_airflow_lps | evaporator_fan_nominal_airflow_cfm | evaporator_fan_size | evaporator_motor_kw | max_continuous_bkw | motor_frame | fan_speed_range_rps | condenser_coil_rows_fins_m | evaporator_face_area_sqm | rated_voltage | source_page | condenser_fan_nominal_airflow_lps | condenser_fan_nominal_airflow_cfm | condenser_fan_quantity | condenser_fan_diameter_mm | condenser_fan_motor_bkw | condenser_fan_speed_rps
50TFF007 | 17.6 | 5 | 213 | 470 | 245 | 540 | 15.4 | 34 | 21 | 47 | 52 | 115 | Scroll | 1 | 1597 ml | R-22 | 3.40 kg | — | 0.97 | 1130 | 2000 | 1...254 x 254 mm | 1.12 | 1.79 | 56 | 15.50-20.08 | 2...669 | 0.51 | 400 V 3ph | 4 | 1415 | 3000 | 1 | 559 | 0.25 | 16
50TFF008 | 21.5 | 6.1 | 342 | 755 | 374 | 825 | 20 | 44 | 28 | 65 | 65 | 143 | Reciprocating | 2 | 1242 ml ea | R-22 | 2.18 kg | 2.21 kg | 1.9 | 1230 | 2600 | 1...381 x 381 mm | 1.12 | 1.79 | 56 | 10.33-14.67 | 1...669 | 0.74 | 400 V 3ph | 4 | 2880 | 6100 | 2 | 559 | 0.19 | 15.5
50TFF009 | 24.3 | 6.9 | 345 | 760 | 376 | 830 | 20 | 44 | 28 | 65 | 65 | 143 | Reciprocating | 2 | 1922 ml ea | R-22 | 3.12 kg | 4.16 kg | 1.67 | 1420 | 2600 | 1...381 x 381 mm | 1.12 | 1.79 | 56 | 10.33-14.67 | 2...669 | 0.74 | 400 V 3ph | 4 | 2880 | 6100 | 2 | 559 | 0.19 | 15.5
50TFF012 | 29.2 | 8.3 | 415 | 915 | 447 | 985 | 20 | 44 | 28 | 65 | 65 | 143 | Reciprocating | 2 | 1597 ml ea | R-22 | 3.26 kg | 3.54 kg | 1.9 | 1700 | 3500 | 1...381 x 381 mm | 1.5 | 1.79 | 56 | 11.50-15.00 | 2...669 | 0.93 | 400 V 3ph | 4 | 3050 | 6500 | 2 | 559 | 0.19 | 15.5
50TFF014 | 35.9 | 10.2 | 422 | 930 | 454 | 1000 | 20 | 44 | 28 | 65 | 65 | 143 | Scroll | 2 | 1597 ml ea | R-22 | 3.91 kg | 3.80 kg | 2.3 | 1980 | 4200 | 1...381 x 381 mm | 2.24 | 2.76 | 56 | 11.83-14.83 | 2...669 | 1.03 | 400 V 3ph | 4 | 3050 | 6500 | 2 | 559 | 0.19 | 15.5
Note on U1: From PDF Physical data (SI), page 4.
Note on AF1: Corrected from PDF Physical data (SI), page 4. Previous workbook field was mislabeled and contained evaporator fan airflow.

## Options_Accessories
item | option_factory_installed | accessory_field_installed | installation_note
Apollo Communicating Controls | X | X | Factory installed
Disconnect Switch | X |  | Factory installed
EconoMi$er | X | X | Factory installed
EconoMi$er with Power Exhaust |  | X | Field installed
Power Exhaust for EconoMi$er |  | X | Field installed
Durablade Integrated Economizer (Includes Hood) | X | X | Factory installed
Manual Outdoor-Air Damper |  | X | Field installed
Condenser Coil Grille |  | X | Field installed
Electric Heat | X |  | Factory installed
Electronic Programmable Thermostat |  | X | Field installed
25% Open Two-Position Damper |  | X | Field installed
100% Open Two-Position Damper |  | X | Field installed
Roof Curbs (Vertical and Horizontal Discharge) |  | X | Field installed
Thermostats and Subbases |  | X | Field installed
Motormaster I Head Pressure Control (Speed Control) |  | X | Field installed
Motormaster II Head Pressure Control (Fan Cycling) |  | X | Field installed
Time Guard II Control Circuit |  | X | Field installed
Thru-the-Bottom Service Connections |  | X | Field installed
Thru-the-Curb Service Connections |  | X | Field installed
Accusensor II Enthalpy Control |  | X | Field installed
Accusensor III Enthalpy Sensor |  | X | Field installed
Condenser Coil Hail Guard Assembly |  | X | Field installed
Fan/Filter Status |  | X | Field installed
Salt Spray Protection Grille (008-014) |  | X | Field installed
Logo Kit |  | X | Field installed
Outdoor-Air Enthalpy Sensor (EconoMi$er) |  | X | Field installed
Return-Air Enthalpy Sensor (EconoMi$er) |  | X | Field installed
Return-Air Temperature Sensor (EconoMi$er) |  | X | Field installed
Indoor-Air Quality (CO2) Sensor (EconoMi$er) |  | X | Field installed

## Base_Dimensions
model | std_weight_lb | std_weight_kg | durablade_lb | durablade_kg | economiser_lb | economiser_kg | corner_a_lb | corner_a_kg | corner_b_lb | corner_b_kg | corner_c_lb | corner_c_kg | corner_d_lb | corner_d_kg | dimension_h_ft_in | dimension_h_mm | dimension_j_ft_in | dimension_j_mm | dimension_k_ft_in | dimension_k_mm | connection_sizes_and_clearances | source_page
50TFF007 | 470 | 213.2 | 34 | 15.4 | 47 | 21.3 | 148 | 67.1 | 103 | 46.7 | 155 | 70.3 | 64 | 29 | 1-0 3/8 in | 315.0 mm |  |  |  |  | A 1-3/8 in [35] field power supply hole; B 2 in [51] power knockout; C 2-1/2 in [64] power knockout; D 7/8 in [22] control wiring hole; E 3/4-14 NPT condensate drain; clearances: flue/combustible 36 in, condenser coil 36 in one side/12 in other, overhead 60 in, control-box side 42 in between units. | 9
50TFF008 | 755 | 342 | 44 | 20 | 62 | 28 | 164 | 74 | 140 | 64 | 208 | 94 | 243 | 110 | 1-2 7/8 in | 378 mm | 3-5 5/16 | 1050 | 2-9 11/16 | 856 | A 1-3/8 in [35] field power supply hole; B 2-1/2 in [64] power knockout; C 1-3/4 in [44] charging port; D 7/8 in [22] control wiring hole; E 3/4-14 NPT condensate drain; F 2 in [51] power knockout. | 10
50TFF009 | 760 | 345 | 44 | 20 | 62 | 28 | 165 | 75 | 141 | 64 | 209 | 94 | 245 | 111 | 3-3 7/8 in | 1013 mm | 3-5 5/16 | 1050 | 2-9 11/16 | 856 | Same connection sizes as 50TFF008-014; see PDF page 10. | 10
50TFF012 | 915 | 415 | 44 | 20 | 62 | 28 | 199 | 90 | 170 | 77 | 252 | 114 | 294 | 134 | 2-5 7/8 in | 759 mm | 4-15/16 | 1253 | 3-0 3/8 | 924 | Same connection sizes as 50TFF008-014; see PDF page 10. | 10
50TFF014 | 930 | 422 | 44 | 20 | 62 | 28 | 202 | 92 | 172 | 78 | 256 | 116 | 300 | 136 | 1-2 7/8 in | 378 mm | 4-15/16 | 1253 | 3-0 3/8 | 924 | Same connection sizes as 50TFF008-014; see PDF page 10. | 10

## Electrical_Data
model | nominal_voltage_v | min_voltage_v | max_voltage_v | compressor_rla_a | compressor_lra_a | outdoor_fan_fla_a | indoor_fan_fla_a | electric_heat_nominal_kw | electric_heat_fla_a | mca_a | mocp_a | disconnect_fla_a | disconnect_lra_a | source_page
50TFF007 | 400 | 360 | 440 | 9.9 | 72 | 0.6 | 2.6 |  |  | 18.4 | 25 | 18 | 109 | 34
50TFF007 | 400 | 360 | 440 | 9.9 | 72 | 0.6 | 2.6 | 4.2 | 7.2 | 18.4 | 25 | 18 | 109 | 34
50TFF007 | 400 | 360 | 440 | 9.9 | 72 | 0.6 | 2.6 | 8 | 13.8 | 18.4 | 25 | 18 | 109 | 34
50TFF007 | 400 | 360 | 440 | 9.9 | 72 | 0.6 | 2.6 | 9.7 | 16.8 | 20.8 | 25 | 19 | 109 | 34
50TFF007 | 400 | 360 | 440 | 9.9 | 72 | 0.6 | 2.6 | 16 | 27.8 | 32.1 | 35 | 30 | 109 | 34
50TFF007 | 400 | 360 | 440 | 9.9 | 72 | 0.6 | 2.6 | 17.7 | 30.7 | 34.6 | 35 | 32 | 109 | 34
50TFF008 | 400 | 360 | 440 | 8.9 | 42 | 0.6 | 2.6 |  |  | 23.8 | 30 | 25 | 103 | 34
50TFF008 | 400 | 360 | 440 | 8.9 | 42 | 0.6 | 2.6 | 9.7 | 13.9 | 23.8 | 30 | 25 | 103 | 34
50TFF008 | 400 | 360 | 440 | 8.9 | 42 | 0.6 | 2.6 | 11.5 | 16.5 | 23.9 | 25 | 25 | 103 | 34
50TFF008 | 400 | 360 | 440 | 8.9 | 42 | 0.6 | 2.6 | 19.3 | 27.8 | 38.1 | 40 | 35 | 103 | 34
50TFF008 | 400 | 360 | 440 | 8.9 | 42 | 0.6 | 2.6 | 22.9 | 33.1 | 44.6 | 45 | 41 | 103 | 34
50TFF008 | 400 | 360 | 440 | 8.9 | 42 | 0.6 | 2.6 | 29 | 41.8 | 55.5 | 60 | 51 | 103 | 34
50TFF009 | 400 | 360 | 440 | 8.3 | 69 | 0.6 | 2.6 |  |  | 22.5 | 25 | 23 | 162 | 34
50TFF009 | 400 | 360 | 440 | 8.3 | 69 | 0.6 | 2.6 | 9.7 | 13.9 | 22.5 | 25 | 23 | 162 | 34
50TFF009 | 400 | 360 | 440 | 8.3 | 69 | 0.6 | 2.6 | 11.5 | 16.5 | 23.9 | 25 | 23 | 162 | 34
50TFF009 | 400 | 360 | 440 | 8.3 | 69 | 0.6 | 2.6 | 19.3 | 27.8 | 38.1 | 40 | 35 | 162 | 34
50TFF009 | 400 | 360 | 440 | 8.3 | 69 | 0.6 | 2.6 | 22.9 | 33.1 | 44.6 | 45 | 41 | 162 | 34
50TFF009 | 400 | 360 | 440 | 8.3 | 69 | 0.6 | 2.6 | 29 | 41.8 | 55.5 | 60 | 51 | 162 | 34
50TFF012 | 400 | 360 | 440 | 8.9 | 64 | 0.6 | 2.6 |  |  | 23.8 | 30 | 25 | 152 | 34
50TFF012 | 400 | 360 | 440 | 8.9 | 64 | 0.6 | 2.6 | 9.7 | 16.5 | 23.9 | 30 | 25 | 152 | 34
50TFF012 | 400 | 360 | 440 | 8.9 | 64 | 0.6 | 2.6 | 19.3 | 27.8 | 38.1 | 40 | 35 | 152 | 34
50TFF012 | 400 | 360 | 440 | 8.9 | 64 | 0.6 | 2.6 | 22.9 | 33.1 | 44.6 | 45 | 41 | 152 | 34
50TFF012 | 400 | 360 | 440 | 8.9 | 64 | 0.6 | 2.6 | 29 | 41.8 | 55.5 | 60 | 51 | 152 | 34
50TFF012 | 400 | 360 | 440 | 8.9 | 64 | 0.6 | 2.6 | 34.7 | 50.1 | 65.9 | 70†† | 61 | 152 | 34
50TFF014 | 400 | 360 | 440 | 10.4 | 73 | 0.6 | 4.8 |  |  | 29.4 | 35 | 31 | 192 | 34
50TFF014 | 400 | 360 | 440 | 10.4 | 73 | 0.6 | 4.8 | 11.5 | 16.5 | 29.4 | 35 | 31 | 192 | 34
50TFF014 | 400 | 360 | 440 | 10.4 | 73 | 0.6 | 4.8 | 19.3 | 27.8 | 40.8 | 45 | 38 | 192 | 34
50TFF014 | 400 | 360 | 440 | 10.4 | 73 | 0.6 | 4.8 | 22.9 | 33.1 | 47.3 | 50 | 44 | 192 | 34
50TFF014 | 400 | 360 | 440 | 10.4 | 73 | 0.6 | 4.8 | 29 | 41.8 | 58.2 | 60 | 54 | 192 | 34
50TFF014 | 400 | 360 | 440 | 10.4 | 73 | 0.6 | 4.8 | 34.7 | 50.1 | 68.6 | 70†† | 63 | 192 | 34

## PDF_Text
source_page | page_text
1 | Product 50TFF007-014 Single-Package Rooftop Units Data Electric Cooling with Electric Heat Option 50 Hz Nominal Capacity: 17.6 kW to 35.9 kW (5 to 10.2 Tons) Single-Package Rooftop Units with: • Galvanized pre-painted steel cabinet • Fifty-one mm (2-in.) return-air filters • Commercial strength base rails • Exclusive tool-less filter access panel • Corrosion-resistant sloped condensate pan • Single power entry to unit • Commercial duty motors with permanently lubricated bearings • Standard cooling operation at outdoor ambient temperatures as low as –4 C (25 F) • Meets ASHRAE Standard 62 (Indoor Air Quality) Features/Benefits 50TFF007 Compact, vertical discharge units convert to horizontal discharge, combining installation flexibility with efficient performance and easy maintenance. Easy installation and conversion All units are shipped in the vertical dis- charge configuration for fit-up to standard roof curbs. (Two different curb sizes fit unit sizes 007 and 008-014.) The contractor can order and install the roof curb early in the construction stage, before decisions on size require- ments are made. All units feature roll-formed baserail design with forklift slots on 3 sides and rigging holes for easier maneuvering. Durable packaging protects all units during shipment and storage. 50TFF008-014 The units can be easily converted from a vertical to a horizontal discharge configuration by interchang- ing the panels supplied with the unit. Copyright 2000 Carrier Corporation Form 50TFF-C1PD
2 | All units feature a non-corrosive finish is non-chalking, and is capable of up to 100% barometric relief capability sloped condensate drain pan in accor- withstanding Federal (U.S.A.) Test for high outdoor airflow applications. dance with ASHRAE (American Soci- Method Standard ASTM B117 In addition, the EconoMi$er baro- ety of Heating, Refrigeration and Air 500-hour salt spray test. All internal metric relief damper or integrated pow- Conditioning Engineers) Standard 62. cabinet panels are primed, permitting er exhaust accessory can be utilized to Also, the sloped condensate pan on longer life and a more attractive ap- help maintain proper building pressure. units permits either an external side pearance for the entire unit. In addi- condensate drain (outside the roof curb) tion, the 50TFF units are designed with Quiet, efficient operation and or an internal bottom drain (inside the a single, continuous top piece to elimi- dependable performance roof curb). Both options require field- nate any possible leaks. Totally en- Compressors have vibration isolators supplied P-trap. closed condenser-fan motors and per- for extremely quiet operation. Efficient In addition, the 50TFF units have a manently lubricated bearings provide fan and motor design permits opera- standard filter access door, which per- additional unit dependability. tion at very low sound levels, and all mits tool-less filter changes. Integrated economizers and 008-014 units are mounted on a spe- Field-installed electric heaters are outdoor air cial polycore plate. available in a wide range of capacities. The 50TFF008-014 units offer high During a first stage call for cooling, if Single point wiring kit makes installa- energy efficiency and lower utility costs the outdoor-air temperature is below tion simple. through part load operation using the control set point, the supply-air 2 stages of cooling. Simple electrical connections sensor modulates the economizer out- door-air damper open to achieve the Quiet and efficient operation is Terminal boards, located in the base set point. When second-stage cooling is provided by belt-driven evaporator fans unit control box, facilitate connections called for, the compressor is energized (standard). The belt-driven evaporator- to room thermostat, outdoor thermo- in addition to the economizer. If the fan motor allows adjustment to avail- stat(s), economizer, and electric heat. outdoor-air temperature is above the able static pressure to meet the job re- Service panels are quickly removed, set point, the first stage of compression quirements of even the most demand- permitting easy servicing. is activated and the economizer stays at ing applications. Thru-the-bottom service connection minimum vent position. Economizer Increased operating efficiency is capability and thru-the-curb service operation is controlled by Accusensor™ achieved through computer-designed connections accessory allows power I dry-bulb thermostat that senses coils featuring staggered copper tubes. and control wiring to be routed through outdoor-air temperature. Accessory up- Fins are ripple-edged for strength, the unit basepan or curb, minimizing grade kits include solid-state enthalpy lanced, and double waved for higher roof penetrations. Both power and control and differential enthalpy sensor. heat transfer. control connections are made on the The Durablade economizer has a re- same side of the unit to simplify instal- Carrier Apollo controls add liable sliding plate damper which is eas- lation. In addition, color-coded wires reliability, efficiency, and ily adjusted for 100% outdoor air, permit easy tracing and diagnostics. 100% return air, or any proportions of simplification Proven compressor reliability mixed air. The direct digital controls are ordered Design techniques feature computer- The 50TFF units also utilize the op- as a factory-installed option. Designed programmed balance between com- tional field or factory-installed and manufactured exclusively by pressor, condenser, and evaporator. EconoMi$er. This newly designed Carrier, the controls can be used to ac- Carrier-specified hermetic compres- EconoMi$er incorporates a tively monitor and control all modes of sors are equipped with compressor parallel-opposed blade design. In operation, as well as to monitor overcurrent and overtemperature pro- addition, the EconoMi$er has a spring evaporator-fan status, filter status tection to ensure dependability. return built into the damper motor to indoor-air quality (humidity and carbon provide reliable close-on-power-loss. dioxide), supply-air temperature, and The 50TFF units have Carrier’s ex- The EconoMi$er comes equipped with outdoor-air temperature. clusive Acutrol™ metering device which precisely controls refrigerant flow, Table of contents preventing slugging and flood-back, while maintaining optimum unit performance. Page Carrier’s exclusive Acutrol metering Features/Benefits . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 1-3 device precisely controls refrigerant Model Number Nomenclature . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 3 flow, preventing slugging and flood- Physical Data . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 4,5 back, while maintaining optimum unit Options and Accessories. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 6-8 performance. Base Unit Dimensions . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 9,10 Durable, dependable Accessory Dimensions . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 11,12 construction Selection Procedure . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 13,14 Designed for durability in any climate, Performance Data . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 15-33 the weather-resistant cabinets are Electrical Data . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .34 manufactured using pre-painted steel. Typical Piping and Wiring . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .35 The cabinet is constructed of galva- Typical Wiring Schematic . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 36,37 nized steel and bonderized, and all exte- Controls . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 38-40 rior panels are coated with a prepaint- Application Data . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .41 ed baked enamel finish. The paint Guide Specifications . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 42-44 2
3 | Features/Benefits (cont) The Apollo communicating control is The standard rooftop control system return air. The face-split evaporator factory-installed into the rooftop unit is readily adaptable to all conventional coils improve the dehumidification ca- evaporator-fan section (007) or unit and programmable thermostats. In ad- pability of the standard units, and control box (008-014), and comes dition, units with Apollo controls are standard enthalpy controls provided equipped with built-in diagnostic capa- suitable for integration into building with the optional or accessory econo- bilities. Light-emitting diodes (LEDs) monitor control systems if required. mizers maximize building humidity simplify troubleshooting by indicating This system gives the 50TFF units the control. The 50TFF units also have an thermostat commands for both stages flexibility to communicate with almost accessory, 100% open, two-position of heating and cooling, evaporator-fan any thermostat or building control damper to meet all your fresh outdoor operation, and economizer operation. system. air requirements. The Apollo communicating control is Indoor-air quality begins with For units without economizer, year- designed to work specifically with the round ventilation is enhanced by a Carrier rooftops Carrier TEMP and VVT® (variable vol- manual outdoor-air damper (ordered as ume and temperature) thermostats. Sloped condensate pans minimize bio- an accessory or an option on 50TFF The Apollo control combined with logical growth in rooftop units in accor- units). The damper can be preset to ad- Carrier thermostats incorporate a dance with ASHRAE Standard 62. mit up to 50% outdoor air. 5-minute recycle delay timer between Standard 51 mm (2-in.) filters with modes of operation to prevent short optional dirty filter indicator switch pro- cycling. vide for greater particle reduction in the Model number nomenclature LEGEND *Refer to 50TFF ordering data or contact your local Carrier representa- Al — Aluminum tive for 50TFF FIOP code table. †All coils have copper tubes. Cu — Copper FIOP — Factory-Installed Option 3
4 | Physical data (SI) 50TFF007-014 UNITS UNIT SIZE 50TFF 007 008 009 012 014 NOMINAL CAPACITY (kW) 17.6 21.5 24.3 29.2 35.9 OPERATING WEIGHT (kg) Unit Al/Al* 213 342 345 415 422 Al/Cu* 245 374 376 447 454 Durablade Economizer 15.4 20.0 20.0 20.0 20.0 EconoMi$er 21 28 28 28 28 Roof Curb† 52 65 65 65 65 COMPRESSOR Type Scroll Reciprocating Scroll Quantity 1 2 2 2 2 Oil (ml) 1597 1242 ea 1922 ea 1597 ea 1597 ea REFRIGERANT TYPE R-22 Operating Charge (kg) Circuit 1 3.40 2.18 3.12 3.26 3.91 Circuit 2 — 2.21 4.16 3.54 3.80 CONDENSER COIL 3/8-in., Enhanced Copper Tubes, Aluminum Lanced Fins Rows...Fins/m 2...669 1...669 2...669 2...669 2...669 Total Face Area (sq m) 0.97 1.90 1.67 1.90 2.30 CONDENSER FAN Propeller Type Nominal L/s 1415 2880 2880 3050 3050 Quantity...Diameter (mm) 1...559 2...559 2...559 2...559 2...559 Motor BkW...r/s .25...16.0 .19...15.5 .19...15.5 .19...15.5 .19...15.5 EVAPORATOR COIL 3/8-in., Enhanced Copper Tubes, Aluminum Double-Wavy Fins, Acutrol™ Feed Device Rows...Fins/m 4...590 3...590 3...590 3...590 4...590 Total Face Area (sq m) 0.51 0.74 0.74 0.93 1.03 EVAPORATOR FAN Centrifugal Type Quantity...Size (mm x mm) 1...254 x 254 1...381 x 381 1...381 x 381 1...381 x 381 1...381 x 381 Type Drive Belt Belt Belt Belt Belt Nominal L/s 1130 1230 1420 1700 1980 Motor kW 1.12 1.12 1.12 1.50 2.24 Maximum Continuous BkW 1.79 1.79 1.79 1.79 2.76 Motor Frame Size 56 56 56 56 56 Nominal r/s High/Low — — — — — Fan r/s Range 15.50-20.08 10.33-14.67 10.33-14.67 11.50-15.00 11.83-14.83 Motor Bearing Type Ball Ball Ball Ball Ball Maximum Allowable r/s 35.0 26.7 26.7 26.7 26.7 Motor Pulley Pitch Diameter Min/Max (mm) 71/97 61/86 71/97 71/97 102/127 Nominal Motor Shaft Diameter (mm) 16 16 16 16 22 Fan Pulley Pitch Diameter (mm) 114 178 178 178 203 Nominal Fan Shaft Diameter (mm) — 25 25 25 25 Belt, Quantity...Type...Length (mm) 1...A...1092 1...A...1245 1...A...1245 1...A...1245 1...A...1321 Pulley Center Line Distance (mm) 373-394 425-489 425-489 403-445 403-445 Speed Change per Full Turn of 1.33 .83 .83 .83 .73 Movable Pulley Flange (r/s) Movable Pulley Maximum Full Turns 5 5 5 5 5 From Closed Position Factory Setting 5 5 5 5 5 Factory Speed Setting (r/s) 15.50 10.33 10.33 11.50 11.83 Fan Shaft Diameter at Pulley (mm) 16 25 25 25 25 HIGH-PRESSURE SWITCH (kPa) Standard Compressor Internal Relief 3448 ± 345 3103 ± 345 3448 ± 345 (Differential) Cutout 2951 Reset (Auto.) 2206 LOW-PRESSURE SWITCH (kPa) Cutout 48 ± 21 Reset (auto.) 152 ± 48 FREEZE PROTECTION THERMOSTAT Opens (C) –1 Closes (C) 7 OUTDOOR-AIR INLET SCREENS Cleanable 1...508 x 635 x 25 Quantity...Size (mm) 1...508 x 610 x 25 1...406 x 635 x 25 RETURN-AIR FILTERS Throwaway Quantity...Size (mm) 2...406 x 635 x 51 4...406 x 508 x 51 4...406 x 508 x 51 4...508 x 508 x 51 4...508 x 508 x 51 LEGEND *Evaporator coil fins/condenser coil fins. †Weight of 356 mm roof curb. Al — Aluminum Bhp — Brake Horsepower NOTE: The 50TFF007-014 units have a loss-of-charge/low-pressure BkW — Fan Input Watts x Motor Efficiency switch (accessory) located in the liquid line. Cu — Copper 4
5 | Physical data (English) 50TFF007-014 UNITS UNIT SIZE 50TFF 007 008 009 012 014 NOMINAL CAPACITY (tons) 5 6.1 6.9 8.3 10.2 OPERATING WEIGHT (lb) Unit Al/Al* 470 755 760 915 930 Al/Cu* 540 825 830 985 1000 Durablade Economizer 34 44 44 44 44 EconoMi$er 47 62 62 62 62 Roof Curb† 115 143 143 143 143 COMPRESSOR Type Scroll Reciprocating Scroll Quantity 1 2 2 2 2 Oil (oz) 54 42 ea 65 ea 54 ea 54 ea REFRIGERANT TYPE R-22 Operating Charge (lb-oz) Circuit 1 7-8 4-13 6-14 7- 3 8-10 Circuit 2 — 4-14 9- 2 7-13 8- 6 CONDENSER COIL 3/8-in., Enhanced Copper Tubes, Aluminum Lanced Fins Rows...Fins/in. 2...17 1...17 2...17 2...17 2...17 Total Face Area (sq ft) 10.42 20.50 18.00 20.47 25.00 CONDENSER FAN Propeller Type Nominal Cfm 3000 6100 6100 6500 6500 Quantity...Diameter (in.) 1...22.0 2...22 2...22 2...22 2...22 Motor Hp...Rpm 1/3...960 1/4...930 1/4...930 1/4...930 1/4...930 EVAPORATOR COIL 3/8-in., Enhanced Copper Tubes, Aluminum Double-Wavy Fins, Acutrol™ Feed Device Rows...Fins/in. 4...15 3...15 3...15 3...15 4...15 Total Face Area (sq ft) 5.5 8.0 8.0 10.0 11.1 EVAPORATOR FAN Centrifugal Type Quantity...Size (in.) 1...10 x 10 1...15 x 15 1...15 x 15 1...15 x 15 1...15 x 15 Type Drive Belt Belt Belt Belt Belt Nominal Cfm 2000 2600 2600 3500 4200 Motor Hp 11/2 11/2 11/2 2 3 Maximum Continuous Bhp 2.40 2.40 2.40 2.40 3.70 Motor Frame Size 56 56 56 56 56 Fan Rpm Range 930-1205 620-880 620-880 690-900 710-890 Motor Bearing Type Ball Ball Ball Ball Ball Maximum Allowable Rpm 2100 1600 1600 1600 1600 Motor Pulley Pitch Diameter Min/Max (in.) 2.8/3.8 2.4/3.4 2.8/3.8 2.8/3.8 4.0/5.0 Nominal Motor Shaft Diameter (in.) 5/8 5/8 5/8 5/8 7/8 Fan Pulley Pitch Diameter (in.) 4.5 7.0 7.0 7.0 8.0 Nominal Fan Shaft Diameter (in.) — — — — — Belt, Quantity...Type...Length (in.) 1...A...40 1...A...49 1...A...49 1...A...49 1...A...52 Pulley Center Line Distance (in.) 14.7-15.5 16.75-19.25 16.75-19.25 15.85-17.50 15.85-17.50 Speed Change per Full Turn of 80 50 50 50 44 Movable Pulley Flange (rpm) Movable Pulley Maximum Full Turns 5 5 5 5 5 From Closed Position Factory Setting 5 5 5 5 5 Factory Speed Setting (rpm) 930 620 620 690 710 Fan Shaft Diameter at Pulley (in.) 5/8 1 1 1 1 HIGH-PRESSURE SWITCH (psig) Standard Compressor Internal Relief 500 ± 50 450 ± 50 500 ± 50 (Differential) Cutout 428 Reset (Auto.) 320 LOW-PRESSURE SWITCH (psig) Cutout 7 ± 3 Reset (Auto.) 22 ± 7 FREEZE PROTECTION THERMOSTAT Opens 30 ± 5 Closes 45 ± 5 OUTDOOR-AIR INLET SCREENS Cleanable Cleanable 1...20 x 25 x 1 Quantity...Size (in.) 1...20 x 24 x 1 1...16 x 25 x 1 RETURN-AIR FILTERS Throwaway Quantity...Size (in.) 2...16 x 25 x 2 4...16 x 20 x 2 4...16 x 20 x 2 4...20 x 20 x 2 4...20 x 20 x 2 LEGEND *Evaporator coil fins/condenser coil fins. †Requires the accessory/optional controls upgrade kit. Al — Aluminum Bhp — Brake Horsepower NOTE: The 50TFF007-014 units have a loss-of-charge/low-pressure BkW — Fan Input Watts x Motor Efficiency switch (accessory) located in the liquid line. Cu — Copper 5
6 | Options and accessories ITEM OPTION* ACCESSORY† Apollo Communicating Controls X Disconnect Switch X EconoMi$er X X EconoMi$er with Power Exhaust X Power Exhaust for EconoMi$er X Durablade Integrated Economizer (Includes Hood) X X Manual Outdoor-Air Damper X Condenser Coil Grille X Electric Heat X Electronic Programmable Thermostat X 25% Open Two-Position Damper X 100% Open Two-Position Damper X Roof Curbs (Vertical and Horizontal Discharge) X Thermostats and Subbases X Motormaster® I Head Pressure Control (Speed Control) X Motormaster II Head Pressure Control (Fan Cycling) X Time Guard® II Control Circuit X Thru-the-Bottom Service Connections X Thru-the-Curb Service Connections X Accusensor™ II Enthalpy Control X Accusensor III Enthalpy Sensor X Condenser Coil Hail Guard Assembly X Fan/Filter Status X Salt Spray Protection Grille (008-014) X Logo Kit X Outdoor-Air Enthalpy Sensor (EconoMi$er) X Return-Air Enthalpy Sensor (EconoMi$er) X Return-Air Temperature Sensor (EconoMi$er) X Indoor-Aair Quality (CO2) Sensor (EconoMi$er) X *Factory installed. †Field installed. HEAD PRESSURE CONTROL The 50TFF007-014 standard units are designed to operate in cooling at outdoor temperatures down to –3.8 C (25 F). With accessory Motormas- ter control (condenser fan speed modulation) or Motormaster II control (condenser fan cycling) units can operate at outdoor temperatures down to –17.8 C (0° F). The head pressure controls, which mount in the con- denser section, control the condenser-fan motor to maintain correct con- Motormaster I Control densing temperature. Refer to product ordering or contact your local (007-014) Carrier representative for appropriate accessory combinations for desired outdoor ambient temperature operation. Motormaster II Control (007-014) 6
7 | ELECTRONIC PROGRAMMABLE THERMOSTAT THERMOSTAT H C Zone thermostat (24 v) provides one- or 2-stage cooling for control of unit. Matching subbases are Carrier’s electronic programmable thermostat provides effi- available with or without tamperproof switches and cient temperature control by allowing you to program heating automatic changeover. and cooling setbacks and setups with provisions for weekends and holidays. Accessory remote sensing package is also avail- able to provide tamperproof control in high traffic spaces. Used in conjunction with factory-installed Apollo control, this thermo- TIME GUARD® II CONTROL stat provides a 5-minute recycle timer between modes of oper- Time Guard II control automatically prevents com- ation for short-cycle protection. pressor from restarting for at least 5 minutes after a shutdown. Accessory prevents short cycling of compressor if thermostat is changed rapidly. Time Guard II control mounts in the control compartment of unit. DURABLADE ECONOMIZER Exclusive Durablade economizer damper design saves energy while providing economical and reliable cooling. A sliding plate on the face of the economizer controls the amount of outdoor air entering the system. Closed, it pro- vides a leakproof seal which prevents ambient air from seep- ing in or conditioned air from seeping out. It can be adjusted easily for 100% outdoor air or any proportions of mixed air. Like the base unit, the economizer is converted easily for hor- izontal discharge applications. 7
8 | Options and accessories (cont) ACCUSENSOR™ II FACTORY-INSTALLED APOLLO CONTROL COMMUNICATING CONTROLS ACCUSENSOR III SENSOR P OPEN T POSITION MINIMUM 3 1 S DOS C B TR RE A8 V 188 . 91 B P1 T1 4 2 5 OUTDOOR TEM F P.(cid:176) 05 55 06 5 0 6 7 57 08 58 Y 10 T30 I RE OPEN D V. 6 DAMPER 0 IM 9 CLOSED 70 U 7- DA 3 MPER H 6 9 7 0 % 2 A C D B CW–SETPOINTS–CCW R T A U C 2 S 4V H A 3 AT M m 1 IN A . 1 VDC C A O CT N T RAT R IN U G N S , : 3 . 1 5 . A 5A IN OR UNPOWERE AT D E ST CONTACTS SHOWN IN HIGH ENTHALPY 2 3 1 TR 1RT 24VAC LORTNOC YPLAHTNE + The Apollo direct digital controls are designed exclusively by Carrier, and are used to actively monitor and control all modes of operation as well as to monitor evaporator-fan status, filter status, supply-air temperature, outdoor-air temperature, and indoor-air quality. They are designed to work in conjunction with Carrier Accusensor economizer controls help provide efficient, economical TEMP and VVT® system thermostats. economizer operation. Accusensor II solid-state enthalpy control includes the logic and one sensor to calculate both dry- and wet- bulb of the outdoor air to provide an accurate enthalpy reading on. It then decides when to energize the economizer based on this read- ELECTRIC HEATER ing. A second Accusensor III sensor compares outdoor temperature and humidity to return-air temperature and humidity and determines the most economical mixture of air (purchased in addition to first solid-state enthalpy sensor for differential enthalpy sensing). ECONOMI$ER ECONOMI$ER CONTROLLER GEAR-DRIVEN PLUG DAMPER ACTUATOR OUTDOOR AIR Electric heaters are available in a wide range TEMPERATURE of capacities for factory or field installation. SENSOR BAROMETRIC RELIEF DAMPERS Factory-installed EconoMi$er utilizes a microprocessor-based con- trol, gear drive damper system, low pressure drop characteristics, built-in spring return (for close upon power loss), and an integral barometric damper. NOTE: EconoMi$er is only available for vertical ductwork applica- tions and can be field or factory installed. 8
9 | Base unit dimensions — 50TFF007 STD UNIT DURABLADE ECONOMI$ER (A) (B) (C) (D) “A” UNIT WEIGHT ECONWEIGHT WEIGHT CORNER WEIGHT CORNER WEIGHT CORNER WEIGHT CORNER WEIGHT PANEL Lbs Kg Lbs Kg Lbs Kg Lbs Kg Lbs Kg Lbs Kg Lbs Kg LENGTH 50TFF007 470 213.2 34 15.4 47 21.3 148 67.1 103 46.7 155 70.3 64 29.0 1¢ -03/8 † [315.0] BOTTOM POWER CHART, THESE HOLES CONNECTION SIZES REQ’D FOR USE WITH ACCESSORY PACKAGES — A 13/8 † Dia. [35] Field Power Supply Hole CRBTMPWR001A00 (1/2 † , 3/4 † ) C B 2 2† 1 / D 2 † i a D . i [ a 5 . 1 [ ] 6 P 4 o ] w Po e w r S er u S pp u l p y p K ly n K oc n k o o c u k t out CO TH N R D E U A IT D S E I D ZE WIRE USE R S E IZ Q E ’ S D ( H M O a L x. E ) D E 7 3 / / 8 4 - † † D 1 ia 4 . N [2 P 2 T ] F C ie o l n d d C en o s n a tr t o e l D W r i a ri i n n g Hole 1 3 / / 2 4 † † P 2 o 4 w V er 1 7 1 / / 8 8 † † [ [ 2 2 2 8 . . 2 4 ] ] NOTES: 1. Dimensions in [ ] are in millimeters. 2. Center of gravity. 3. Direction of airflow. 4. On vertical discharge units, ductwork to be attached to accessory roof curb only. For horizontal dis- charge units field-supplied flanges should be attached to horizontal discharge openings, and all ductwork should be attached to the flanges. 5. Minimum clearance (local codes or jurisdiction may prevail): a. Between unit, flue side and combustible surfaces, 36 inches. b. Bottom of unit to combustible surfaces (when not using curb) 1 inch. Bottom of base rail to com- bustible surfaces (when not using curb) 0 inches. c. Condenser coil, for proper airflow, 36 in. one side, 12 in. the other. The side getting the greater clearance is optional. d. Overhead, 60 in. to assure proper condenser fan operation. e. Between units, control box side, 42 in. per NEC. f. Between unit and ungrounded surfaces, control box side, 36 in. per NEC. g. Between unit and block or concrete walls and other grounded surfaces, control box side, 42 in. per NEC. h. Horizontal supply and return end, 0 inches. 6. With the exception of the clearance for the condenser coil and combustion side as stated in Note 5a, b, and c, a removable fence or barricade requires no clearance. 7. Units may be installed on combustible floors made from wood or Class A, B, or C roof covering material if set on base rail. 8. The vertical center of gravity is 1¢ -6† [457] up from the bottom of the base rail. 9
10 | Base unit dimensions — 50TFF008-014 UNIT S W T E D I G U H N T IT E D C U O W R N E A O I B G M L H A IZ T D E E R EC W ON E O IG M H I T $ER C W O E ( R I A G N ) H E T R C W O E ( R I B G N ) H E T R C W O E ( R I C G N ) H E T R C W O E ( R I D G N ) H E T R “H” “J” “K” Lb Kg Lb Kg Lb Kg Lb Kg Lb Kg Lb Kg Lb Kg Ft-in. mm Ft-in. mm Ft-in. mm 50TFF008 755 342 44 20 62 28 164 74 140 64 208 94 243 110 1-27/8 378 3-55/16 1050 2-911/16 856 50TFF009 760 345 44 20 62 28 165 75 141 64 209 94 245 111 3-37/8 1013 3-55/16 1050 2-911/16 856 50TFF012 915 415 44 20 62 28 199 90 170 77 252 114 294 134 2-57/8 759 4-15/16 1253 3-03/8 924 50TFF014 930 422 44 20 62 28 202 92 172 78 256 116 300 136 1-27/8 378 4-15/16 1253 3-03/8 924 BOTTOM POWER CHART, THESE HOLES REQ’D CONNECTION SIZES FOR USE WITH ACCESSORY PACKAGES — B A 2 13 1 / / 8 2 † † D D i i a a . . [ [ 6 3 4 5 ] ] P Fi o e w ld e r P S ow up e p r l S y u K p n p o ly c k H o o u l t e C C R R B B T T M M P P W W R R 00 0 1 0 A 2A 00 0 0 ( 1 ( / 1 2 / † 2 , † 3 , / 1 4 † 1 ) /4 O † ) R C D E 1 7 3 / / 3 8 4 / † † 4 † D — D ia i 1 a . 4 . [ 2 [ N 4 2 P 4 ] ] F T C i e C h ld o a n r C g d o i e n n n g t s r o P a l t o e W r t D i H r r i a n o i g l n e Hole T C H O R S N E IZ D A E D U E IT D W U I S R E E REQ S (M ’ I D Z a E x H S . O ) LE F 2† Dia. [51] Power Supply Knockout 1/2 † 24 V 7/8 † [22.2] 3/4 † Power* 11/8 † [28.4] NOTES: 11/4 † FPT Power* 13/4 † [44.4] 1. Dimensions in [ ] are in millimeters. *Select either 3/4 † or 11/4 † for power, depending on wire 2. Center of gravity. size. 3. Direction of airflow. 4. Ductwork to be attached to accessory roof curb only. 5. Minimum clearance (local codes or jurisdiction may prevail): a. Bottom to combustible surfaces (when not using curb) 0 inches, on horizontal discharge units with electric heat 1 in. clearance to ductwork for 1 ft. b. Condenser coil, for proper airflow, 36 in. one side, 12 in. the other. The side getting the greater clearance is optional. c. Overhead, 60 in. to assure proper condenser fan operation. d. Between units, control box side, 42 in. per NEC (National Electrical Code). e. Between unit and ungrounded surfaces, control box side, 36 in. per NEC. f. Between unit and block or concrete walls and other grounded surfaces, control box side, 42 in. per NEC. g. Horizontal supply and return end, 0 inches. 6. With the exception of the clearance for the condenser coil as stated in Notes 5a, b, and c, a removable fence or barricade requires no clearance. 7. Units may be installed on combustible floors made from wood or Class A, B, or C roof covering material. 8. The vertical center of gravity is 1¢ -71/2 † [495] for 008 and 009, 2¢ -0† [610] for 012 and 014 up from the bottom of the base rail. 10
11 | Accessory dimensions A R C O C O E F S C S U O R R B Y “A” UN 5 I 0 T T S F I F ZE B C ALT DRA D IN HOLE G “E A ” S PO “ W F” ER CON “G TR ” OL C P O K N G N . E A C C T C O Y R . C C R R R R F F C C U U R R B B 0 0 0 0 1 2 A A 0 0 0 0 1 2 ¢ ¢ - - 2 0 † † [ [ 3 6 5 1 6 0 ] ] 007 [19 3 ] / 4 N † PT 3 1 /4 1 † / 4 [1 † 9 [3 ] 1 N . P 7] T [1 1 2 /2 . † 7] C C R R B B T T M M P P W W R R 0 0 0 0 2 1 A A 0 0 0 0 NPT 1¢ - [ 9 5 1 5 1 1 /1 ] 6 † [ 1 4 ¢ 0 -4 6 † ] [ 1 4 3 4 / . 4 5 † ] [12. 1 7 / ] 2 † NPT 3/4 † [19] NPT 1/2 † CRBTMPWR003A00 3/4 † 11/4 † [31.7] [12.7] CRBTMPWR004A00 [19] NPT NPT NOTES: 6. Service clearance 4 ft on each side. 1. Roof curb accessory is shipped disassembled. 7. Direction of airflow. 2. Insulated panels. 8. Connector packages CRBTMPWR001A00 3. Dimensions in [ ] are in millimeters. and 002A00 are for thru-the-curb connec- 4. Roof curb: galvanized steel. tions. Packages CRBTMP003A00 and 5. Attach ductwork to curb (flanges of duct 004A00 are for thru-the-bottom connections. rest on curb). 11
12 | Accessory dimensions (cont) A R C O C O E F S C S U O R R B Y “A” UN 5 I 0 T T S F I F ZE “B” “C” “ D D R ” A A I L N T G “E A ” S PO “ W F” ER CON “G TR ” OL CO PA N C N K E A C G TO E R CRRFCURB003A00 1¢ -2† [356] HOLE ACCESSORY CRRFCURB004A00 2¢ -0† [610] 008-014 3/4 † 3/4 † [19] NPT 1/2 † [12.7] CRBTMPWR001A00 2 [8 1 ¢ - 2 6 8 † 7 7 ] / 1¢ [ - 5 1 1 8 6 0 † 3 1 ] 5/ [ 1 4 3 4 / . 4 5 † ] [1 [1 2 9 . 1 7 ] / ] 2 N † N P P T T 11 3 / / 4 4 † † [ [ 3 1 1 9 . ] 7 N ] N PT PT 1/2 N † [ P 1 T 2.7] C C R RB B T T M M P P W W R R 0 0 0 0 2 3 A A 0 0 0 0 [19 3 ] / 4 N † PT 11/4 † [31.7] NPT NPT CRBTMPWR004A00 NOTES: 6. Service clearance 4 ft on each side. 1. Roof curb accessory is shipped disassembled. 7. Direction of airflow. 2. Insulated panels, 1† thick polyurethane 3. f D o i a m m e , n 1 s 3 io /4 n s lb i n d e [ n s ] it a y r . e in millimeters. 8. C 00 o 2 n A ne 00 ct or a r p e a ck fo a r g e t s h r C u R -t B he T - M cu P r W b R c 0 o 0 n 1 n A e 0 c 0 ti o a n n s d . 4. Roof curb: 16 gage steel. Packages CRBTMP003A00 and 004A00 are 5. Attach ductwork to curb (flanges of duct for thru-the-bottom connections. rest on curb). 12
13 | Selection procedure (with 50TFF012 example) — SI I. Determine cooling and heating requirements IV. Determine fan speed and power require- at design conditions. ments at design conditions. Given: Before entering the Fan Performance tables, calcu- late the total static pressure required based on unit Required Cooling Capacity (TC) . . . . . . . . . 28 kW components. From the given and the Pressure Drop Sensible Heat Capacity (SHC) . . . . . . . . . . 19 kW tables (page 33), find: Required Heating Capacity . . . . . . . . . . . . 18 kW Condenser Entering-Air Temp . . . . . . . . . . . 36 C External static pressure 300 Pa Evaporator Entering-Air Temp . . . . . . 26.7 C edb, Economizer 9 Pa 20 C ewb Electric Heat 14 Pa Evaporator Air Quantity. . . . . . . . . . . . . 1520 L/s Total static pressure 323 Pa External Static Pressure (ESP). . . . . . . . . . .300 Pa Enter the Fan Performance table for the 50TFF012 Electrical Characteristics (V-Ph-Hz) . . . . . 400-3-50 vertical discharge unit on page 23. Find the fan r/s Edb — Entering dry bulb and kilowatts at 323 Pa and 1520 L/s. Note that Ewb — Entering wet bulb the fan speed is 14.5 r/s and power required is Durablade economizer required. 1.56 kW (interpolation required). The standard II. Select unit based on required cooling motor will adequately handle the job requirements. capacity. V. Determine net capacities. Enter the 50TFF012 Cooling Capacities table on Capacities are gross and do not include the effect of page 18 at condenser entering temperature of evaporator-fan motor heat. Use IFM kW from Fan 36 C, evaporator-air entering at 1520 L/s, 26.7 C Performance table on page 23. db and 20 C wb. The 50TFF012 unit will provide Determine net cooling capacity as follows: cooling capacity of 30.1 kW and a sensible heat capacity of 21.2 kW. For evaporator-air tempera- Net capacity = gross capacity – IFM kW ture other than 26.7 C edb, calculate sensible heat = 30.1 kW – 1.56 kW capacity correction, as required, using the formula = 28.5 kW found in the notes following the Cooling Capacities Net sensible capacity = 21.2 kW – 1.56 kW table on page 19. = 19.6 kW NOTE: Unit ratings are gross capacities and do not Determine net heating capacity as follows: include the effect of evaporator-fan motor (IFM) Net capacity = gross capacity + IFM heat heat. To calculate net capacities, see Step V. = 19.3 kW + 1.56 kW III. Select electric heat: = 24.9 kW Heating load required is 18 kW. Enter the Electric Heating Capacities table (page 33) for the 50TFF012 at 400-3-50. The 19.3 kW heater at 400 v most closely satisfies the heating required. 13
14 | Selection procedure (with 50TFF012 example) — English I. Determine cooling and heating requirements IV. Determine fan speed and power require- at design conditions. ments at design conditions. Given: Before entering the Fan Performance tables, calcu- late the total static pressure required based on unit Required Cooling Capacity (TC) . . . . 96,000 Btuh components. From the given and the Pressure Drop Sensible Heat Capacity (SHC) . . . . . .70,000 Btuh tables (page 33) find: Required Heating Capacity . . . . . . . 62,000 Btuh Condenser Entering-Air Temp . . . . . . . . . . . 95 F External static pressure 1.10 in. wg Evaporator Entering-Air Temp . . . . . . . . 80 F edb, Economizer 0.04 in. wg 67 F ewb Electric Heat 0.06 in. wg Evaporator Air Quantity. . . . . . . . . . . . . 3200 cfm Total static pressure 1.20 in. wg External Static Pressure (ESP). . . . . . . .1.10 in. wg Enter the Fan Performance table for the 50TFF012 Electrical Characteristics (V-Ph-Hz) . . . . . 400-3-50 vertical discharge unit on page 27. Find the fan rpm Edb — Entering dry bulb and watts at 1.20 in. wg and 3200 cfm. Note that Ewb — Entering wet bulb the fan speed is 844 rpm and power required is Durablade economizer required. 1430 watts. The standard motor will adequately II. Select unit based on required cooling handle the job requirements. capacity. V. Determine net capacities. Enter the 50TFF012 Cooling Capacities table on Capacities are gross and do not include the effect of page 21 condenser entering temperature of 95 F, evaporator-fan motor heat. Use IFM Watts from Fan evaporator-air entering at 3200 cfm, 80 F db and Performance table on page 27. 67 F wb. The 50TFF012 unit will provide cooling Determine net cooling capacity as follows: capacity of 102,500 Btuh and a sensible heat capacity of 76,000 Btuh. For evaporator-air tem- Net capacity = gross capacity – IFM Watts perature other than 80 F edb, calculate sensible Btuh heat capacity correction, as required, using the for- = 102,500 Btuh – 1430 Watts x 3.413 mula found in the notes following the Cooling Watts Capacities table on page 21. = 102,500 Btuh – 4881 Btuh NOTE: Unit ratings are gross capacities and do not = 97,619 Btuh include the effect of evaporator-fan motor (IFM) Net sensible capacity = 76,000 Btuh – 4881 Btuh heat. To calculate net capacities, see Step V. = 71,119 Btuh III. Select electric heat: Determine net heating capacity as follows: Heating load required is 62,000 Btuh. Net Capacity= gross capacity + IFM heat = 65,871 + 4881 62,000 Btuh = 18.2 kW of heat required = 70,752 Btuh 3413 Btuh/kW Enter the Electric Heating Capacities table (page 33) for the 50TFF012 at 400-3-50. The 19.3 kW heater at 400 v most closely satisfies the heating required. 19.3 x 3413 = 65,871 Btuh gross capacity 14
15 | Performance data COOLING CAPACITIES — SI 50TFF007 (17.6 kW) Air Entering Evaporator — L/s/BF Temp (C) Air Entering 700/0.05 950/0.07 1200/0.09 Condenser Air Entering Evaporator — Ewb (C) (Edb) 13 16 19 22 13 16 19 22 13 16 19 22 TC 15.8 17.7 19.6 21.5 16.8 18.7 20.7 22.6 17.4 19.3 21.3 23.3 20 SHC 15.8 15.5 13.1 10.4 16.8 18.1 14.9 11.6 17.4 19.3 16.6 12.6 kW 3.98 4.11 4.25 4.39 4.08 4.21 4.35 4.49 4.12 4.27 4.41 4.55 TC 15.2 17.1 19.0 20.6 16.2 18.1 20.1 22.0 17.0 18.8 20.7 22.6 24 SHC 15.2 15.3 12.8 10.2 16.2 17.9 14.7 11.4 17.0 18.8 16.4 12.4 kW 4.26 4.41 4.56 4.71 4.38 4.51 4.66 4.82 4.43 4.58 4.73 4.88 TC 14.7 16.5 18.4 20.3 15.6 17.5 19.4 21.3 16.6 18.2 20.0 21.9 28 SHC 14.7 15.0 12.6 10.0 15.6 17.5 14.5 11.2 16.6 18.2 16.1 12.2 kW 4.54 4.70 4.87 5.04 4.66 4.82 4.98 5.15 4.74 4.89 5.05 5.21 TC 14.1 15.9 17.8 19.7 15.0 16.9 18.8 20.7 16.2 17.7 19.4 21.2 32 SHC 14.1 14.7 12.3 9.8 15.0 16.9 14.3 11.0 16.2 17.7 15.8 12.0 kW 4.81 4.99 5.17 5.36 4.92 5.10 5.29 5.48 5.05 5.20 5.37 5.55 TC 13.7 15.5 17.3 19.3 14.5 16.4 18.2 20.2 15.8 17.3 18.8 20.7 35 SHC 13.7 14.5 12.2 9.6 14.5 16.4 14.1 10.9 15.8 17.3 15.6 11.9 kW 5.01 5.20 5.39 5.60 5.12 5.31 5.52 5.73 5.28 5.61 5.61 5.80 TC 12.7 14.6 16.5 18.3 14.0 15.6 17.3 19.2 15.4 16.6 17.9 19.7 40 SHC 12.7 14.1 11.8 9.3 14.0 15.6 13.7 10.6 15.4 16.6 15.2 11.6 kW 5.33 5.54 5.76 5.99 5.46 5.68 5.90 6.13 5.68 5.83 5.99 6.20 TC 12.0 13.8 15.8 17.6 13.5 15.1 16.7 18.5 15.1 16.1 17.2 18.9 44 SHC 12.0 13.8 11.5 9.1 13.5 15.1 13.4 10.3 15.1 16.1 14.8 11.4 kW 5.60 5.82 6.05 6.29 5.75 5.97 6.20 6.45 5.99 6.14 6.31 6.52 TC 11.2 13.1 15.1 16.9 13.0 14.5 15.9 17.7 14.8 15.5 16.5 18.1 48 SHC 11.2 13.1 11.2 8.8 13.0 14.5 13.1 10.0 14.8 15.5 14.4 11.1 kW 5.85 6.09 6.34 6.60 6.04 6.26 6.50 6.76 6.31 6.46 6.61 6.84 TC 10.5 12.4 14.4 16.2 12.7 13.9 15.3 16.9 14.4 15.0 15.7 17.3 52 SHC 10.5 12.4 11.0 8.6 12.7 13.9 12.8 9.8 14.4 15.0 14.1 10.9 kW 6.11 6.36 6.63 6.91 6.31 6.56 6.81 7.08 6.62 6.77 6.92 7.16 LEGEND AND NOTES FOR COOLING CAPACITY TABLES — SI LEGEND 4. Formulas: BF — Bypass Factor SHCkW x 1000 Edb — Entering Dry Bulb Temperature (C) Cldb = Cedb – Ewb — Entering Wet Bulb Temperature (C) 1.23 x L/s kW — Compressor Input (kW) Leaving wet bulb = wet bulb temperature corresponding to enthalpy SHC — Sensible Heat Capacity (kW) TC — Total Capacity (kW) of air leaving coil (hlwb). NOTES: hlwb = hewb – TCkW x 1000 1. Ratings are gross, and do not account for the effects of the 1.20 x L/s evaporator-fan motor power and heat. 2. Direct interpolation is permissible. Do not extrapolate. Where hewb is enthalpy of air entering evaporator coil (kJ/kg). 3. SHC is based on 26.7 C db temperature of air entering the unit. At any other temperature, correct the SHC read from the table of cool- ing capacities as follows: Corrected SHCkW = SHC + [1.23 x 10–3 x (1 – BF) x (Cdb – 26.7) x L/s] Observe the rule of sign. Above 26.7 C, SHC correction will be posi- tive; add it to SHC. Below 26.7 C, SHC correction will be negative; subtract it from SHC. 15
16 | Performance data (cont) COOLING CAPACITIES — SI (cont) 50TFF008 (21.5 kW) Air Entering Evaporator — L/s BF Temp (C) Air Entering 850/0.05 1130/0.075 Condenser Air Entering Evaporator — Ewb (C) (Edb) 14 16 18 20 22 14 16 18 20 22 TC 19.5 20.9 22.5 24.3 26.0 21.6 22.3 23.7 25.3 27.0 20 SHC 19.4 18.0 16.2 14.3 12.3 21.4 20.5 18.5 16.1 13.4 kW 5.02 5.16 5.34 5.54 5.72 5.28 5.37 5.52 5.70 5.88 TC 19.1 20.4 21.9 23.7 25.4 21.0 21.7 23.1 24.7 26.4 24 SHC 18.9 17.7 16.0 14.1 12.1 21.0 20.2 18.3 15.9 13.3 kW 5.25 5.38 5.56 5.76 5.96 5.51 5.58 5.74 5.92 6.12 TC 18.6 19.8 21.3 23.0 24.8 20.5 21.1 22.4 24.1 25.9 28 SHC 18.4 17.3 15.7 13.9 11.9 20.5 19.8 18.0 15.7 13.1 kW 5.49 5.61 5.78 5.98 6.19 5.74 5.8 5.96 6.15 6.36 TC 18.0 19.1 20.6 22.2 23.9 19.9 20.3 21.5 23.2 25.0 32 SHC 17.8 16.9 15.4 13.6 11.6 19.8 19.4 17.7 15.4 12.9 kW 5.77 5.88 6.04 6.25 6.47 6.03 6.07 6.22 6.43 6.64 TC 17.3 18.2 19.63 21.3 23.0 18.2 19.4 20.6 22.3 24.0 36 SHC 17.2 16.4 15.0 13.2 11.3 19.1 18.9 17.3 15.0 12.5 kW 6.09 6.18 6.34 6.55 6.77 6.33 6.37 6.61 6.73 6.94 TC 16.6 18.3 18.7 20.3 22.0 18.4 18.6 19.6 21.3 23.0 40 SHC 16.6 15.9 14.6 12.8 10.9 18.4 18.3 16.9 14.7 12.3 kW 6.40 6.48 6.63 6.84 7.07 6.65 6.67 6.81 7.02 7.24 TC 15.9 16.4 17.7 19.4 21.0 17.7 17.7 18.7 20.2 21.9 44 SHC 15.9 15.4 14.2 12.5 10.6 17.7 17.6 16.4 14.3 11.9 kW 6.71 6.77 6.92 7.13 7.36 6.97 6.97 7.10 7.30 7.53 TC 15.2 15.5 16.7 18.3 19.9 16.9 16.9 17.7 19.1 20.7 48 SHC 15.2 14.9 13.8 12.1 10.2 16.9 16.9 15.8 13.9 11.5 kW 7.02 7.05 7.20 7.41 7.64 7.27 7.27 7.39 7.57 7.81 TC 14.4 14.5 15.6 17.3 18.8 16.1 16.1 16.8 18.0 19.6 52 SHC 14.4 14.3 13.3 11.7 9.9 16.1 16.1 15.2 13.5 11.2 kW 7.33 7.33 7.47 7.67 7.91 7.56 7.57 7.67 7.85 8.08 50TFF008 (21.5 kW) (cont) Air Entering Evaporator — L/s BF Temp (C) Air Entering 1180/0.075 1400/0.095 Condenser Air Entering Evaporator — Ewb (C) (Edb) 14 16 18 20 22 14 16 18 20 22 TC 21.8 22.5 23.9 25.5 27.1 22.9 23.1 24.3 26.1 27.7 20 SHC 21.8 20.9 18.9 16.4 13.6 22.8 22.4 20.5 17.7 14.5 kW 5.33 5.41 5.55 5.73 5.91 5.49 5.51 5.65 5.83 5.99 TC 21.3 21.9 23.3 24.9 26.5 22.4 22.5 23.7 25.4 27.0 24 SHC 21.2 20.6 18.7 16.2 13.5 22.3 22.0 20.2 17.5 14.3 kW 5.55 5.62 5.77 5.96 6.14 5.72 5.73 5.86 6.05 6.22 TC 20.8 21.2 22.5 24.2 25.9 21.8 21.9 23.1 24.7 26.4 28 SHC 20.7 20.2 18.4 16.0 13.3 21.8 21.7 20.0 17.3 14.1 kW 5.78 5.84 5.98 6.17 6.38 5.94 5.96 6.08 6.28 6.46 TC 20.2 20.5 21.7 23.4 25.2 21.2 21.2 22.2 23.8 25.6 32 SHC 20.2 19.8 18.1 15.7 13.0 21.2 21.0 19.5 17.0 13.9 kW 6.07 6.11 6.25 6.45 6.66 6.23 6.23 6.36 6.54 6.74 TC 19.5 19.6 20.7 22.4 24.1 20.4 20.4 20.7 22.8 24.6 36 SHC 19.4 19.2 17.7 15.3 12.7 20.4 20.4 19.0 16.6 13.6 kW 6.39 6.41 6.55 6.75 6.96 6.54 6.54 6.66 6.84 7.05 TC 18.7 18.7 19.8 21.3 23.1 19.6 19.6 20.4 21.7 23.4 40 SHC 18.7 18.6 17.2 15.0 12.4 19.6 19.6 18.4 16.3 13.3 kW 6.69 6.70 6.83 7.04 7.26 6.86 6.86 6.95 7.12 7.34 TC 17.9 17.9 18.8 20.3 22.0 18.8 18.8 19.4 20.6 22.3 44 SHC 17.9 17.9 16.7 14.6 12.1 18.8 18.8 17.8 15.9 13.0 kW 7.01 7.01 7.13 7.33 7.55 7.16 7.16 7.25 7.41 7.64 TC 17.1 17.1 17.9 19.2 20.8 17.9 17.9 18.5 19.5 21.2 48 SHC 17.1 17.1 16.1 14.2 11.7 17.9 17.9 17.2 15.5 12.7 kW 7.31 7.31 7.42 7.59 7.83 7.46 7.47 7.54 7.69 7.92 TC 16.3 16.3 16.9 18.0 19.6 17.1 17.1 17.4 18.3 19.9 52 SHC 16.3 16.3 15.4 13.9 11.4 17.1 17.1 16.5 15.1 12.3 kW 7.61 7.61 7.70 7.87 8.1 7.76 7.77 7.82 7.95 8.18 16
17 | COOLING CAPACITIES — SI (cont) 50TFF009 (24.3 kW) Air Entering Evaporator — L/s/BF Temp (C) Air Entering 1200/0.07 1400/.08 1700/0.11 Condenser Air Entering Evaporator — Ewb (C) (Edb) 13 16 19 22 13 16 19 22 13 16 19 22 TC 24.7 25.2 28.4 30.8 26.0 26.2 29.1 31.5 27.9 27.9 29.9 32.2 20 SHC 24.1 23.2 19.3 15.0 25.2 24.6 20.5 15.5 26.5 26.5 22.0 16.0 kW 6.25 6.38 6.60 6.70 6.60 6.68 6.97 7.06 7.25 7.25 7.66 7.73 TC 24.0 24.3 27.5 30.3 25.5 25.5 28.4 30.9 27.1 27.1 29.3 31.6 24 SHC 23.4 22.8 19.0 14.8 24.6 24.3 20.4 15.4 25.7 25.8 22.0 16.0 kW 6.61 6.69 6.96 7.09 6.97 7.02 7.35 7.46 7.61 7.60 8.04 8.14 TC 23.0 23.2 26.5 29.6 24.7 24.7 27.5 30.3 26.4 26.4 28.4 31.0 28 SHC 22.5 22.0 18.7 14.6 23.9 23.9 20.1 15.2 25.0 25.0 21.8 15.9 kW 7.00 7.06 7.33 7.48 7.34 7.34 7.71 7.86 7.98 7.97 8.42 8.55 TC 22.3 22.4 25.5 28.7 23.7 23.7 26.3 29.4 25.6 25.6 27.3 30.2 32 SHC 21.7 21.4 18.4 14.3 22.8 22.8 19.7 15.0 24.2 24.2 21.5 15.7 kW 7.32 7.36 7.71 7.87 7.72 7.72 8.09 8.25 8.37 8.36 8.77 8.96 TC 21.7 21.7 24.6 28.0 23.1 23.0 25.6 28.7 25.0 25.0 26.4 29.4 35 SHC 21.1 20.9 17.9 14.1 22.2 22.2 19.5 14.8 23.6 23.6 21.2 15.4 kW 7.56 7.59 8.01 8.17 8.00 7.99 8.37 8.57 8.66 8.65 9.03 9.27 TC 20.7 20.7 23.1 26.7 22.0 22.0 23.9 27.4 23.6 23.6 25.0 28.2 40 SHC 20.1 20.1 17.4 13.6 21.2 21.2 18.8 14.3 22.2 22.2 20.7 15.1 kW 7.96 7.96 8.44 8.66 8.42 8.41 8.82 9.06 9.15 9.14 9.47 9.78 TC 19.9 19.9 22.0 25.5 21.2 21.2 22.7 26.3 22.7 22.7 23.7 27.0 44 SHC 19.3 19.3 16.9 13.2 20.3 20.3 18.3 14.0 21.3 21.3 20.2 14.8 kW 8.29 8.29 8.78 9.04 8.75 8.75 9.15 9.44 9.52 9.51 9.80 10.17 TC 19.1 19.1 20.8 24.3 20.3 20.3 21.5 25.0 21.8 21.8 22.3 25.8 48 SHC 18.5 18.5 16.4 12.8 19.4 19.4 17.8 13.5 20.4 20.4 19.5 14.4 kW 8.62 8.62 9.05 9.42 9.08 9.08 9.48 9.83 9.88 9.87 10.10 10.56 LEGEND AND NOTES FOR COOLING CAPACITY TABLES — SI LEGEND 4. Formulas: BF — Bypass Factor SHCkW x 1000 Edb — Entering Dry Bulb Temperature (C) Cldb = Cedb – Ewb — Entering Wet Bulb Temperature (C) 1.23 x L/s kW — Compressor Input (kW) Leaving wet bulb = wet bulb temperature corresponding to enthalpy SHC — Sensible Heat Capacity (kW) TC — Total Capacity (kW) of air leaving coil (hlwb). NOTES: hlwb = hewb – TCkW x 1000 1. Ratings are gross, and do not account for the effects of the 1.20 x L/s evaporator-fan motor power and heat. 2. Direct interpolation is permissible. Do not extrapolate. Where hewb is enthalpy of air entering evaporator coil (kJ/kg). 3. SHC is based on 26.7 C db temperature of air entering the unit. At any other temperature, correct the SHC read from the table of cool- ing capacities as follows: Corrected SHCkW = SHC + [1.23 x 10–3 x (1 – BF) x (Cdb – 26.7) x L/s] Observe the rule of sign. Above 26.7 C, SHC correction will be posi- tive; add it to SHC. Below 26.7 C, SHC correction will be negative; subtract it from SHC. 17
18 | Performance data (cont) COOLING CAPACITIES — SI (cont) 50TFF012 (29.2 kW) Air Entering Evaporator — L/s BF Temp (C) Air Entering 1140/0.08 1520/0.105 Condenser Air Entering Evaporator — Ewb (C) (Edb) 14 16 18 20 22 14 16 18 20 22 TC 26.6 28.2 30.5 33.1 34.7 30.5 31.4 32.7 34.3 36.3 20 SHC 26.4 24.8 22.8 20.3 17.3 30.4 29.3 26.2 22.2 18.7 kW 6.82 6.98 7.17 7.35 7.42 7.09 7.17 7.27 7.39 7.60 TC 25.8 27.0 29.4 32.1 33.8 29.6 30.4 31.8 33.5 35.3 24 SHC 25.6 24.2 22.3 19.9 16.8 29.5 28.7 25.9 22.2 18.4 kW 7.20 7.34 7.54 7.73 7.82 7.47 7.53 7.65 7.80 7.99 TC 24.7 25.8 28.2 30.8 32.8 28.5 29.1 30.7 32.6 34.4 28 SHC 24.6 23.5 21.7 19.4 16.4 28.5 27.9 25.4 21.9 18.2 kW 7.61 7.93 8.11 8.32 8.45 8.09 8.12 8.26 8.46 8.64 TC 23.6 24.5 26.6 29.4 31.8 27.3 27.7 29.4 31.5 33.3 32 SHC 23.5 22.7 21.1 18.8 16.1 27.3 27.0 24.8 21.6 17.8 kW 8.03 8.13 8.31 8.53 8.67 8.30 8.32 8.47 8.67 8.85 TC 22.4 23.0 25.0 27.9 30.7 26.1 26.3 27.9 30.1 32.0 36 SHC 22.3 21.8 20.3 18.2 17.8 26.0 26.0 24.1 21.2 17.4 kW 8.47 8.53 8.73 8.96 9.15 8.74 8.74 8.89 9.11 9.30 TC 21.1 21.5 23.4 26.2 29.5 24.7 24.7 26.4 28.7 30.8 40 SHC 21.1 20.9 19.6 17.5 15.3 24.7 24.7 23.3 20.7 17.2 kW 8.95 8.97 9.15 9.40 9.64 9.20 9.20 9.34 9.56 9.80 TC 20.0 20.1 21.7 24.4 27.9 23.1 23.1 24.4 26.6 29.4 44 SHC 20.0 19.9 18.7 16.8 14.8 23.1 23.1 22.0 20.0 16.7 kW 9.40 9.40 9.60 9.86 10.11 9.70 9.71 9.82 10.03 10.29 TC 19.1 19.1 20.3 22.6 26.0 21.5 21.5 22.4 24.3 27.6 48 SHC 10.1 19.1 17.9 16.2 14.2 21.5 21.5 20.7 19.1 16.2 kW 9.89 9.89 10.06 10.32 10.59 10.22 10.22 10.31 10.50 10.79 TC 18.3 18.3 19.1 20.9 24.0 20.0 20.0 20.4 21.9 25.5 52 SHC 18.3 18.3 17.2 15.5 13.5 20.0 20.0 18.4 18.1 15.5 kW 10.37 10.37 10.52 10.77 11.07 10.74 10.74 10.81 10.98 11.28 50TFF012 (29.2 kW) (cont) Air Entering Evaporator — L/s BF Temp (C) Air Entering 1800/0.125 1880/0.13 Condenser Air Entering Evaporator — Ewb (C) (Edb) 14 16 18 20 22 14 16 18 20 22 TC 31.5 31.9 33.3 35.3 37.2 31.7 23.1 33.5 35.3 37.3 20 SHC 31.4 30.6 27.8 24.0 19.9 31.7 31.1 28.3 24.4 20.2 kW 7.12 7.16 7.30 7.50 7.70 7.15 7.18 7.32 7.51 7.71 TC 30.8 31.0 32.4 34.2 36.2 31.0 31.2 32.5 34.4 36.2 24 SHC 30.8 30.1 27.4 23.6 19.6 31.0 30.5 27.9 24.0 19.7 kW 7.53 7.54 7.68 7.88 8.10 7.54 7.57 7.71 7.90 8.09 TC 30.0 30.1 31.4 33.2 35.2 30.3 30.4 31.6 33.3 35.0 28 SHC 30.0 29.6 27.2 23.4 19.3 30.2 30.1 27.6 23.7 19.5 kW 7.95 7.97 8.11 8.30 8.51 7.99 7.99 8.13 8.31 8.51 TC 29.1 29.1 30.3 32.1 34.0 29.4 29.4 30.5 32.2 34.0 32 SHC 29.1 29.0 26.7 23.1 18.9 29.4 29.4 27.1 23.5 19.2 kW 8.40 8.41 8.54 8.73 8.95 8.44 8.44 8.56 8.75 8.95 TC 28.1 28.0 29.1 30.8 32.8 28.3 28.3 29.3 31.0 32.9 36 SHC 27.9 28.0 26.1 22.8 18.5 28.3 28.3 26.5 23.3 18.9 kW 8.87 8.87 8.89 9.17 9.40 8.91 8.91 9.01 9.19 9.42 TC 26.5 26.5 27.7 29.5 31.5 27.0 27.0 28.0 29.7 31.6 40 SHC 14.7 26.5 25.1 22.5 18.3 26.9 27.0 25.6 23.0 18.6 kW 9.37 9.36 9.46 9.64 9.88 9.41 9.40 9.50 9.66 9.89 TC 24.8 24.8 25.7 27.5 30.0 25.2 25.2 26.1 27.7 30.1 44 SHC 24.8 24.8 23.8 21.8 18.0 25.2 25.2 24.4 22.3 18.2 kW 9.87 9.87 9.96 10.12 10.36 9.92 9.92 9.99 10.13 10.38 TC 23.0 23.0 23.7 25.3 28.3 23.4 23.4 24.0 25.5 28.4 48 SHC 23.0 23.0 22.4 20.9 17.5 23.4 23.4 23.0 21.4 17.8 kW 10.39 10.39 10.45 10.59 10.86 10.43 10.43 10.49 10.61 10.90 TC 21.3 21.3 21.6 22.8 26.5 21.6 21.6 21.8 23.0 26.7 52 SHC 21.3 21.3 21.0 19.9 17.0 21.6 21.6 21.4 20.4 17.4 kW 10.93 10.93 10.95 11.07 11.38 10.97 10.97 10.99 11.10 11.41 18
19 | COOLING CAPACITIES — SI (cont) 50TFF014 (35.9 kW) Air Entering Evaporator — L/s/BF Temp (C) Air Entering 1500/0.13 2000/0.17 2350/0.21 Condenser Air Entering Evaporator — Ewb (C) (Edb) 13 16 19 22 13 16 19 22 13 16 19 22 TC 34.7 38.0 41.4 44.4 37.0 40.0 43.2 46.3 36.6 40.1 43.6 46.7 20 SHC 34.7 33.8 28.1 22.0 37.0 39.9 31.7 24.0 36.6 40.1 33.5 25.0 kW 8.92 8.99 9.08 9.13 9.00 9.06 9.13 9.22 9.05 9.10 9.15 9.25 TC 32.1 35.8 39.6 43.0 34.8 38.2 41.6 44.9 35.5 38.7 42.1 45.5 24 SHC 32.1 32.8 27.4 21.6 34.8 38.2 31.1 23.7 35.5 38.7 32.4 24.8 kW 9.34 9.46 9.60 9.70 9.47 9.57 9.68 9.80 9.60 9.63 9.74 9.84 TC 29.4 33.6 37.9 41.6 32.9 36.3 40.0 43.4 34.4 37.4 40.6 44.0 28 SHC 29.4 31.9 26.7 21.1 32.9 36.3 30.5 23.3 34.4 37.4 32.5 24.6 kW 9.78 9.94 10.12 10.27 9.95 10.08 10.22 10.39 10.15 10.10 10.25 10.42 TC 26.7 31.5 36.2 40.2 30.8 34.5 38.3 42.0 33.0 36.0 39.1 42.7 32 SHC 26.7 30.9 26.0 20.7 30.8 34.5 29.9 22.9 33.0 36.0 31.9 24.3 kW 10.20 10.42 10.64 10.85 10.40 10.59 10.76 10.96 10.49 10.65 10.82 11.01 TC 24.7 29.9 34.9 39.1 29.2 33.1 37.0 40.9 31.4 35.0 38.0 41.6 35 SHC 24.7 29.7 25.5 20.3 29.2 33.1 29.4 22.7 31.4 35.0 31.5 24.2 kW 10.52 10.80 11.03 11.30 10.77 11.00 11.18 11.40 10.40 11.07 11.25 11.47 TC 21.1 26.8 32.3 37.1 26.9 30.8 34.7 38.8 30.5 53.1 35.8 39.5 40 SHC 21.1 26.8 24.4 19.7 26.9 30.8 28.3 22.1 30.5 33.1 30.6 23.7 kW 11.10 11.40 11.71 12.00 11.42 11.64 11.88 12.13 11.64 11.79 11.96 12.20 TC 20.5 25.3 30.2 35.2 25.7 28.8 32.2 36.9 29.1 31.0 33.4 37.6 44 SHC 20.5 25.3 23.5 19.1 25.7 28.8 27.1 21.5 29.1 31.0 29.4 23.2 kW 11.62 11.93 12.25 12.58 12.05 12.24 12.44 12.73 12.26 12.38 12.52 12.79 TC 20.4 24.1 27.9 33.2 24.5 26.9 29.6 34.9 27.7 29.0 30.8 35.5 48 SHC 20.4 24.1 27.9 33.2 24.5 26.9 25.8 21.0 27.7 29.0 28.1 22.6 kW 12.15 12.45 12.78 13.17 12.68 12.84 13.00 13.33 12.88 12.97 13.10 13.39 TC 20.1 22.8 25.8 31.3 23.3 24.9 27.0 33.1 26.2 26.9 28.2 33.5 52 SHC 20.1 22.8 21.4 17.8 23.3 24.9 24.5 20.3 26.0 26.8 26.7 22.1 kW 12.67 12.98 13.31 13.75 13.34 13.43 13.56 13.93 13.49 13.57 13.67 13.97 LEGEND AND NOTES FOR COOLING CAPACITY TABLES — SI LEGEND 4. Formulas: BF — Bypass Factor SHCkW x 1000 Edb — Entering Dry Bulb Temperature (C) Cldb = Cedb – Ewb — Entering Wet Bulb Temperature (C) 1.23 x L/s kW — Compressor Input (kW) Leaving wet bulb = wet bulb temperature corresponding to enthalpy SHC — Sensible Heat Capacity (kW) TC — Total Capacity (kW) of air leaving coil (hlwb). NOTES: hlwb = hewb – TCkW x 1000 1. Ratings are gross, and do not account for the effects of the 1.20 x L/s evaporator-fan motor power and heat. 2. Direct interpolation is permissible. Do not extrapolate. Where hewb is enthalpy of air entering evaporator coil (kJ/kg). 3. SHC is based on 26.7 C db temperature of air entering the unit. At any other temperature, correct the SHC read from the table of cool- ing capacities as follows: Corrected SHCkW = SHC + [1.23 x 10–3 x (1 – BF) x (Cdb – 26.7) x L/s] Observe the rule of sign. Above 26.7 C, SHC correction will be posi- tive; add it to SHC. Below 26.7 C, SHC correction will be negative; subtract it from SHC. 19
20 | Performance data (cont) COOLING CAPACITIES — ENGLISH 50TFF007 (5 TONS) Air Entering Evaporator — Cfm/BF Temp (F) Air Entering 1500/0.05 2000/0.07 2500/0.09 Condenser Air Entering Evaporator — Ewb (F) (Edb) 62 67 72 62 67 72 62 67 72 TC 60.0 66.0 72.1 63.0 69.2 76.1 65.2 71.5 78.1 75 SHC 50.5 42.6 34.5 58.2 48.5 38.3 64.3 54.0 41.3 kW 4.44 4.57 4.71 4.52 4.66 4.84 4.58 4.74 4.90 TC 57.2 63.2 69.4 60.3 66.3 72.4 62.6 68.0 74.3 85 SHC 49.4 41.6 33.5 57.3 47.5 37.1 62.6 52.8 39.9 kW 4.85 5.00 5.17 4.96 5.11 5.28 5.03 5.18 5.34 TC 54.4 60.2 66.3 57.1 62.9 69.4 60.0 64.7 70.9 95 SHC 48.1 40.4 32.4 55.6 46.4 36.2 60.0 52.0 39.3 kW 5.25 5.43 5.62 5.35 5.54 5.75 5.47 5.62 5.81 TC 51.0 56.9 62.9 54.2 59.5 65.7 57.2 61.1 67.1 105 SHC 46.5 39.1 31.2 53.5 45.2 35.0 57.2 50.7 38.2 kW 5.64 5.83 6.05 5.76 5.97 6.19 5.90 6.05 6.26 TC 47.6 53.7 59.5 51.4 56.0 62.0 54.4 57.4 63.3 115 SHC 45.0 37.8 30.0 51.3 44.0 33.8 54.4 49.4 37.0 kW 6.02 6.24 6.48 6.17 6.39 6.63 6.33 6.48 6.70 TC 44.7 50.3 55.8 48.7 52.3 58.0 51.6 53.5 59.2 125 SHC 43.5 36.6 28.8 48.7 42.5 32.4 51.6 47.7 35.9 kW 6.39 6.65 6.90 6.61 6.77 7.03 6.79 6.87 7.12 50TFF008 (6.1 TONS) Air Entering Evaporator — Cfm/BF Temp (F) Air Entering 1950/0.06 2400/0.075 2500/0.075 3000/0.095 Condenser Air Entering Evaporator — Ewb (F) (Edb) 62 67 72 62 67 72 62 67 72 62 67 72 TC 71.9 80.1 88.3 74.9 83.0 90.9 75.3 83.6 91.3 77.4 85.2 92.9 75 SHC 56.3 46.6 55.1 62.3 50.5 57.0 63.6 51.2 60.4 69.1 55.3 23.7 kW 5.47 5.73 6.02 5.60 5.86 6.14 5.64 5.90 6.14 5.74 6.00 6.24 TC 69.0 77.1 85.4 71.7 79.8 88.2 72.2 80.2 88.5 74.3 82.0 90.0 85 SHC 59.7 50.5 40.6 66.6 55.6 43.6 68.0 56.6 44.1 73.8 62.0 47.0 kW 5.77 6.04 6.34 5.90 6.17 6.47 5.93 6.19 6.49 6.05 6.31 6.57 TC 64.9 72.7 80.8 67.4 75.2 83.5 67.8 75.6 83.8 70.7 77.1 85.5 95 SHC 57.9 48.8 39.1 64.6 54.0 42.1 65.8 55.1 42.7 70.5 60.2 45.9 kW 6.32 6.61 6.54 6.45 6.75 6.60 6.48 6.76 6.69 6.60 6.86 3.46 TC 60.4 68.1 76.2 63.0 70.4 78.6 63.5 70.8 78.8 66.7 72.0 80.1 105 SHC 55.7 47.2 37.5 62.2 52.4 40.8 63.2 53.4 41.3 66.7 58.6 44.1 kW 6.59 6.86 7.19 6.71 7.00 7.32 6.74 7.02 7.34 6.90 7.11 7.40 TC 55.9 63.4 71.1 59.0 65.4 73.2 59.7 65.6 73.5 62.5 66.8 75.0 115 SHC 53.2 45.4 35.9 59.0 50.6 39.0 59.7 51.6 39.6 62.7 56.8 43.0 kW 6.99 7.26 7.58 7.13 7.39 7.71 7.17 7.41 7.72 7.34 7.49 7.83 TC 51.1 58.4 65.8 55.1 60.0 67.7 55.8 60.3 57.9 58.7 61.3 69.0 125 SHC 50.4 43.5 34.1 55.0 48.6 37.3 55.8 49.8 37.9 58.6 54.8 41.3 kW 7.37 7.63 7.95 7.54 7.75 8.08 7.58 6.77 8.10 7.75 7.87 8.20 50TFF009 (6.9 TONS) Air Entering Evaporator — Cfm/BF Temp (F) Air Entering 2000/0.07 2500/.08 3000/0.10 3500/0.11 Condenser Air Entering Evaporator — Ewb (F) (Edb) 62 67 72 62 67 72 62 67 72 62 67 72 TC 79.2 90.1 99.5 85.0 95.2 103.7 88.9 98.5 106.4 92.3 100.9 108.4 75 SHC 65.7 56.4 46.2 74.9 62.5 49.2 81.9 67.3 51.4 86.0 71.2 52.8 kW 6.44 6.56 6.68 6.76 6.93 7.06 7.12 7.39 7.49 7.56 7.93 8.03 TC 74.6 85.8 96.0 79.4 90.6 100.2 84.4 94.3 103.0 88.3 96.7 105.0 85 SHC 63.7 54.8 44.9 72.2 60.8 48.1 78.9 66.0 50.5 83.9 70.3 52.2 kW 6.85 7.06 7.21 7.25 7.46 7.59 7.59 7.90 8.04 8.01 8.45 8.59 TC 70.2 80.4 91.4 74.7 82.9 96.1 79.1 84.1 98.9 84.5 91.5 100.7 95 SHC 61.6 52.5 43.2 69.6 59.2 46.8 75.3 64.4 49.3 80.1 68.7 51.0 kW 7.26 7.58 7.75 7.62 7.98 8.15 8.08 8.43 8.60 8.53 8.99 9.15 TC 65.5 75.6 86.8 70.4 79.9 91.0 75.1 83.0 93.9 79.3 85.9 95.9 105 SHC 59.3 50.5 41.6 55.4 56.7 45.0 72.2 61.8 47.7 75.0 67.0 49.7 kW 7.64 8.05 8.28 8.03 8.50 8.69 8.50 8.98 9.16 9.07 9.48 9.71 TC 60.7 70.5 81.7 66.0 74.4 85.6 70.9 77.3 88.4 75.0 79.5 90.5 115 SHC 56.5 48.5 39.8 63.5 54.5 43.2 68.0 59.8 45.9 70.6 64.3 48.0 kW 8.01 8.47 8.81 8.45 8.96 9.21 8.96 9.44 9.69 9.57 10.00 10.27 TC 45.4 65.1 75.7 61.8 68.7 79.9 66.6 71.3 82.6 70.6 73.3 84.5 125 SHC 53.6 46.3 37.5 60.0 52.4 41.3 63.7 57.6 44.0 66.2 61.9 46.1 kW 8.43 8.90 9.35 8.88 9.39 9.77 9.43 9.88 10.26 10.06 10.41 10.81 20
21 | COOLING CAPACITIES — ENGLISH (cont) 50TFF012 (8.3 TONS) Air Entering Evaporator — Cfm/BF Temp (F) Air Entering 2500/0.09 3200/0.105 3800/0.12 4000/0.13 Condenser Air Entering Evaporator — Ewb (F) (Edb) 62 67 72 62 67 72 62 67 72 62 67 72 TC 95.1 108.3 116.7 104.5 112.8 121.4 106.2 114.9 124.4 107.0 115.8 124.2 75 SHC 77.4 64.2 77.2 87.6 70.1 82.0 101.9 74.6 84.7 95.0 75.9 32.4 kW 7.39 7.69 7.83 7.55 7.74 8.00 7.5 7.81 8.10 7.56 7.84 8.10 TC 88.9 102.3 112.0 98.5 108.3 116.9 101.8 110.3 119.2 102.7 110.8 119.0 85 SHC 79.9 69.3 55.1 93.5 77.7 60.0 100.3 83.4 63.7 102.2 85.1 64.4 kW 7.91 8.24 8.42 8.08 8.34 8.60 8.10 8.39 8.69 8.15 8.41 8.67 TC 81.8 94.7 107.2 91.2 102.5 110.9 96.8 104.4 113.7 98.0 105.0 114.2 95 SHC 76.4 66.2 53.8 89.5 76.0 58.1 96.7 82.1 61.4 98.0 83.9 63.2 kW 8.64 8.94 8.85 8.77 9.08 8.96 8.8 9.15 9.03 8.91 9.17 4.60 TC 74.2 86.4 101.8 83.4 95.2 105.3 89.7 98.2 107.6 91.3 98.7 108.0 105 SHC 72.1 62.8 51.8 83.4 73.4 56.9 89.7 80.5 60.8 91.3 82.6 61.7 kW 9.06 9.42 9.74 9.26 9.56 9.88 9.4 9.65 9.96 9.48 9.66 9.98 TC 67.4 77.2 94.2 75.6 83.8 99.0 81.3 87.4 100.6 82.8 88.4 101.0 115 SHC 67.3 59.1 49.5 75.6 68.9 55.1 81.2 76.3 59.0 82.7 78.7 60.1 kW 9.71 10.04 10.42 9.97 10.19 10.59 10.1 10.28 10.66 10.19 10.31 10.68 TC 63.2 69.2 84.4 68.5 71.8 88.8 73.1 75.0 92.3 74.2 76.0 93.0 125 SHC 63.2 56.0 46.0 68.5 64.3 51.9 73.0 70.9 56.9 74.2 73.0 58.4 kW 10.37 10.68 11.09 10.69 10.85 11.27 10.9 10.95 11.37 10.93 10.97 11.41 50TFF014 (10.2 TONS) Air Entering Evaporator — Cfm/BF Temp (F) Air Entering 3150/0.13 4200/0.17 5100/0.21 Condenser Air Entering Evaporator — Ewb (F) (Edb) 62 67 72 62 67 72 62 67 72 TC 125.1 137.3 147.5 133.0 143.5 154.1 135.1 145.6 156.1 75 SHC 107.5 90.6 71.7 125.8 101.9 78.7 134.0 109.7 83.1 kW 9.48 9.60 9.69 9.58 9.67 9.79 9.59 9.69 9.83 TC 115.4 129.6 140.9 124.4 135.9 147.3 128.9 138.6 149.9 85 SHC 103.1 87.7 69.8 120.8 99.8 77.0 128.3 108.6 82.1 kW 10.15 10.33 10.49 10.29 10.43 10.61 10.34 10.48 10.66 TC 105.5 122.0 134.4 115.8 128.2 140.4 122.7 131.5 143.6 95 SHC 98.9 84.8 67.8 115.7 97.8 75.3 122.7 107.6 81.2 kW 10.83 11.06 11.30 11.01 11.20 11.41 11.11 11.27 11.47 TC 94.1 112.2 126.9 106.5 118.9 132.4 115.2 122.6 135.8 105 SHC 92.7 81.2 65.3 106.5 94.8 73.2 115.2 105.6 79.4 kW 11.54 11.83 12.10 11.76 11.98 12.22 11.92 12.06 12.31 TC 86.9 100.4 117.9 96.5 105.3 123.7 104.6 109.2 126.2 115 SHC 86.8 76.4 62.5 96.5 89.8 70.5 104.6 100.4 77.2 kW 12.26 12.55 12.91 12.58 12.74 13.07 12.73 12.83 13.14 TC 79.9 88.5 108.8 86.4 91.7 115.0 94.1 96.0 116.5 125 SHC 79.9 71.7 59.6 86.3 84.8 67.8 99.1 94.6 74.8 kW 13.00 13.29 13.72 13.40 13.49 13.91 13.55 13.62 13.96 LEGEND AND NOTES FOR COOLING CAPACITY TABLES — ENGLISH LEGEND 4. Formulas: E B d F b — — B E y n p te a r s in s g F D ac ry to B r ulb Temperature (F) Fldb = Fedb – SHCBtuh Ewb — Entering Wet Bulb Temperature (F) 1.09 x cfm kW — Compressor Motor Power Input Leaving wet bulb = wet bulb temperature corresponding to enthalpy of air SHC — Sensible Heat Capacity (1000 Btuh) TC — Total Capacity (1000 Btuh) leaving coil (hlwb). NOTES: hlwb = hewb – TCBtuh 1. Ratings are gross, and do not account for the effects of the evaporator-fan 4.50 x cfm motor power and heat. 2. Direct interpolation is permissible. Do not extrapolate. Where hewb is enthalpy of air entering evaporator coil (kJ/kg). 3. SHC is based on 80 F db temperature of air entering the unit. At any other temperature, correct the SHC read from the table of cooling capaci- ties as follows: Corrected SHCBtuh = SHC + [1.10 x (1 – BF) x (Fdb – 80) x cfm] Observe the rule of sign. Above 80 F, SHC correction will be positive; add it to SHC. Below 80 F, SHC correction will be negative; subtract it from SHC. 21
22 | Performance data (cont) FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS 50TFF007 (17.6 kW) — STANDARD MOTOR (BELT DRIVE) External Static Pressure (Pa) Airflow 25 50 100 150 200 250 300 350 400 (L/s) R/s kW R/s kW R/s kW R/s kW R/s kW R/s kW R/s kW R/s kW R/s kW 700 12.1 0.30 13.1 0.36 14.8 0.48 16.4 0.61 17.8 0.75 18.7 0.85 18.7 0.83 17.8 0.67 16.0 0.44 750 12.8 0.36 13.7 0.42 15.5 0.56 17.0 0.68 18.4 0.84 19.5 0.98 20.1 1.05 20.0 1.23 19.1 0.85 800 13.5 0.42 14.4 0.49 16.1 0.63 17.5 0.77 18.9 0.93 20.1 1.09 21.1 1.22 21.5 1.28 21.3 1.22 850 14.2 0.56 15.1 0.61 16.7 0.74 18.1 0.85 19.4 1.00 20.6 1.15 21.7 1.31 22.9 1.50 23.9 1.69 900 14.9 0.63 15.8 0.70 17.3 0.82 18.7 0.95 19.9 1.10 21.1 1.26 22.2 1.42 23.3 1.62 24.4 1.80 950 15.7 0.72 16.5 0.78 17.9 0.91 19.3 1.06 20.5 1.21 21.7 1.37 22.8 1.55 23.8 1.73 24.8 1.93 1000 16.4 0.81 17.2 0.88 18.6 1.02 19.9 1.18 21.1 1.34 22.2 1.50 23.3 1.69 24.3 1.86 25.2 2.06 1050 17.2 0.92 17.9 0.99 19.2 1.13 20.6 1.30 21.7 1.48 22.8 1.64 23.8 1.83 24.9 2.01 25.7 2.21 1100 18.0 1.03 18.6 1.10 19.9 1.26 21.2 1.44 22.3 1.63 23.4 1.79 24.4 1.98 25.4 2.18 26.3 2.38 1150 18.7 1.17 19.2 1.23 20.6 1.41 21.8 1.58 23.0 1.78 24.0 1.97 24.9 2.14 25.9 2.34 — — 1200 19.4 1.23 19.8 1.36 21.3 1.55 22.4 1.72 23.6 1.92 24.6 2.12 25.5 2.29 — — — — LEGEND nuisance tripping or premature motor failure. Unit warranty will not be affected. See Evaporator-Fan Motor Performance table on BkW — Fan Input kW x Motor Efficiency page 30 or additional information. kW — Kilowatt Input to Motor 6. Use of a field-supplied motor may affect wire sizing. Contact your NOTES: Carrier representative to verify. 1. Boldface indicates field-supplied drive required (see Note 3). 7. To convert kW to bkW: BkW = kW x Motor Efficiency 2. indicates field-supplied motor and drive required. Motor Efficiency: .81 Maximum Continuous kW: 2.12 3. Factory-shipped drive range is 15.50 to 20.08 r/s. Other r/s’s may 8. Interpolation is permissible. Do not extrapolate. require a field-supplied drive. 9. Static pressure losses (i.e., economizer, electric heater) must be 4. Values include losses for filters, unit casing, and wet coils. added to external static pressure before entering Fan Performance 5. Extensive motor and electrical testing on these units ensures that table. the full range of the motor can be utilized with confidence. Using your fan motors up to the kW ratings shown will not result in 50TFF008,009 (21.5 AND 24.3 kW) — STANDARD MOTOR (BELT DRIVE) External Static Pressure (Pa) Airflow 50 100 150 200 250 300 350 400 450 500 (L/s) R/s kW R/s kW R/s kW R/s kW R/s kW R/s kW R/s kW R/s kW R/s kW R/s kW 800 7.0 0.27 9.0 0.45 9.6 0.53 11.0 0.70 12.0 1.86 13.1 1.03 13.9 1.25 15.0 1.74 15.5 1.96 16.6 2.45 900 7.5 0.37 9.3 0.55 10.1 0.66 11.4 0.84 12.3 1.02 13.4 1.19 14.2 1.43 15.3 1.86 15.8 2.10 16.8 2.55 1000 8.1 0.47 9.7 0.65 10.6 0.79 11.8 0.98 12.7 1.18 13.7 1.37 14.5 1.61 15.5 1.98 16.1 2.24 17.0 2.65 1100 8.7 0.57 10.1 0.75 11.1 0.92 12.2 1.12 13.1 1.34 14.0 1.55 14.8 1.79 15.7 2.10 16.4 2.38 17.2 2.75 1200 9.3 0.67 10.5 0.85 11.6 1.05 12.6 1.26 13.5 1.50 14.3 1.73 15.1 1.97 15.9 2.22 16.7 2.52 17.4 2.85 1300 9.8 0.80 11.0 0.99 12.1 1.21 13.0 1.43 13.9 1.67 14.7 1.93 15.5 2.18 16.2 2.34 16.9 2.69 17.6 2.97 1400 10.4 0.94 11.5 1.13 12.6 1.38 13.5 1.63 14.3 1.87 15.1 2.13 15.9 2.41 16.6 2.66 17.3 2.92 — — 1500 11.0 1.11 12.0 1.31 13.0 1.58 13.9 1.85 14.7 2.11 15.5 2.36 16.3 2.64 17.0 2.91 — — — — LEGEND nuisance tripping or premature motor failure. Unit warranty will not be affected. See Evaporator-Fan Motor Performance table on BkW — Fan Input kW x Motor Efficiency page 30 or additional information. kW — Kilowatt Input to Motor 6. Use of a field-supplied motor may affect wire sizing. Contact your NOTES: Carrier representative to verify. 1. Boldface indicates field-supplied drive required (see Note 3). 7. To convert kW to bkW: BkW = kW x Motor Efficiency 2. indicates field-supplied motor and drive required. Motor Efficiency: .81 Maximum Continuous kW: 2.12 3. Factory-shipped drive range is 10.33 to 14.67 r/s. Other r/s’s may 8. Interpolation is permissible. Do not extrapolate. require a field-supplied drive. 9. Static pressure losses (i.e., economizer, electric heater) must be 4. Values include losses for filters, unit casing, and wet coils. added to external static pressure before entering Fan Performance 5. Extensive motor and electrical testing on these units ensures that table. the full range of the motor can be utilized with confidence. Using your fan motors up to the kW ratings shown will not result in 22
23 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) 50TFF012 (29.2 kW) — STANDARD MOTOR (BELT DRIVE) External Static Pressure (Pa) Airflow 50 100 150 200 250 300 350 400 450 500 (L/s) R/s kW R/s kW R/s kW R/s kW R/s kW R/s kW R/s kW R/s kW R/s kW R/s kW 1100 7.6 0.36 9.2 0.46 10.2 0.56 11.3 0.70 12.7 0.74 12.9 0.80 13.6 0.90 14.4 1.09 15.2 1.20 16.2 1.37 1200 7.9 0.39 9.3 0.51 10.4 0.63 11.4 0.75 12.8 0.86 13.0 0.90 13.9 1.02 14.6 1.13 15.4 1.38 16.3 1.60 1250 8.2 0.42 9.5 0.55 10.6 0.69 11.5 0.80 12.9 1.92 13.1 1.02 14.2 1.14 14.8 1.38 15.6 1.65 16.5 1.83 1300 8.4 0.56 9.6 0.78 10.8 0.88 11.7 0.96 12.6 1.09 13.3 1.18 14.3 1.34 15.1 1.58 15.9 1.81 16.7 2.03 1400 8.8 0.66 10.0 0.86 11.1 0.98 12.0 1.10 12.9 1.22 13.7 1.33 14.5 1.47 15.4 1.67 16.2 1.90 16.8 2.12 1500 9.2 0.74 10.4 0.95 11.5 1.09 12.4 1.23 13.2 1.35 14.0 1.49 14.8 1.57 15.6 1.77 16.4 1.97 17.1 2.21 1600 9.7 0.85 10.8 1.07 11.8 1.22 12.8 1.37 13.6 1.49 14.4 1.65 15.1 1.79 15.8 1.94 16.5 2.09 17.3 2.31 1700 10.2 0.96 11.2 1.19 12.2 1.35 13.1 1.51 13.9 1.66 14.7 1.81 15.4 1.98 16.1 2.13 16.7 2.29 17.4 2.46 1800 10.6 1.09 11.7 1.34 12.6 1.51 13.5 1.67 14.3 1.85 15.0 2.01 15.7 2.18 16.4 2.36 17.1 2.54 17.7 2.71 1900 11.1 1.24 12.1 1.49 13.0 1.67 13.9 1.86 14.7 2.04 15.4 2.23 16.1 2.40 16.8 2.59 17.4 2.80 18.0 2.99 LEGEND nuisance tripping or premature motor failure. Unit warranty will not be affected. See Evaporator-Fan Motor Performance table on BkW — Fan Input kW x Motor Efficiency page 30 or additional information. kW — Kilowatt Input to Motor 6. Use of a field-supplied motor may affect wire sizing. Contact your NOTES: Carrier representative to verify. 1. Boldface indicates field-supplied drive required (see Note 3). 7. To convert kW to bkW: BkW = kW x Motor Efficiency 2. indicates field-supplied motor and drive required. Motor Efficiency: .83 Maximum Continuous kW: 2.12 3. Factory-shipped drive range is 11.50 to 15.00 r/s. Other r/s’s may 8. Interpolation is permissible. Do not extrapolate. require a field-supplied drive. 9. Static pressure losses (i.e., economizer, electric heater) must be 4. Values include losses for filters, unit casing, and wet coils. added to external static pressure before entering Fan Performance 5. Extensive motor and electrical testing on these units ensures that table. the full range of the motor can be utilized with confidence. Using your fan motors up to the kW ratings shown will not result in 50TFF014 (35.9 kW) — STANDARD MOTOR (BELT DRIVE) External Static Pressure (Pa) Airflow 50 100 150 200 250 300 350 400 450 500 (L/s) R/s kW R/s kW R/s kW R/s kW R/s kW R/s kW R/s kW R/s kW R/s kW R/s kW 1500 9.7 0.66 10.8 0.84 11.7 0.91 12.6 1.09 13.5 1.27 14.3 1.32 15.1 1.44 16.0 1.55 16.9 1.66 17.5 1.88 1550 9.9 0.72 11.0 0.89 11.9 1.01 12.8 1.15 13.7 1.34 14.5 1.46 15.2 1.38 16.1 1.71 17.0 1.79 17.5 2.02 1600 10.2 0.78 11.2 0.95 12.1 1.10 13.0 1.22 13.8 1.41 14.6 1.58 15.4 1.71 16.2 1.79 17.0 1.92 17.6 2.15 1650 10.4 0.85 11.5 1.01 12.4 1.20 13.2 1.29 14.0 1.48 14.8 1.67 15.5 1.76 16.3 1.89 17.1 2.06 17.6 2.28 1700 10.7 0.91 11.7 1.08 12.6 1.29 13.4 1.38 14.2 1.55 15.0 1.76 15.7 1.92 16.4 2.01 17.1 2.18 17.7 2.36 1750 10.9 1.07 11.9 1.22 12.8 1.37 13.6 1.52 14.4 1.67 15.1 1.86 15.8 2.02 16.5 2.20 17.2 2.36 17.7 2.51 1800 11.1 1.12 12.1 1.29 13.0 1.45 13.8 1.60 14.6 1.75 15.3 1.95 16.0 2.12 16.7 2.29 17.3 2.47 17.9 2.64 1850 11.4 1.19 12.4 1.36 13.2 1.54 14.0 1.69 14.7 1.84 15.5 2.03 16.2 2.22 16.8 2.40 17.5 2.59 18.1 2.77 1900 11.6 1.26 12.6 1.45 13.4 1.62 14.2 1.78 14.9 1.93 15.6 2.12 16.3 2.33 17.0 2.52 17.7 2.71 18.3 2.90 1950 11.9 1.34 12.8 1.53 13.7 1.71 14.4 1.88 15.1 2.03 15.8 2.22 16.5 2.44 17.2 2.64 17.8 2.83 18.4 3.03 2000 12.1 1.42 13.0 1.62 13.9 1.80 14.6 1.99 15.3 2.15 16.0 2.32 16.7 2.54 17.3 2.76 18.0 2.96 18.6 3.16 2050 12.4 1.51 13.2 1.71 14.1 1.89 14.8 2.09 15.5 2.26 16.2 2.42 16.9 2.64 17.5 2.88 18.1 3.09 17.7 3.30 2100 12.6 1.60 13.5 1.81 14.3 2.00 15.0 2.21 15.7 2.39 16.4 2.54 17.0 2.76 17.7 3.01 18.3 3.23 18.9 3.44 2150 12.8 1.70 13.7 1.92 14.5 2.12 15.3 2.33 15.9 2.51 16.6 2.68 17.2 2.88 17.8 3.14 18.5 3.36 19.1 3.59 2200 13.1 1.79 13.9 2.02 14.7 2.22 15.5 2.45 16.1 2.64 16.8 2.82 17.4 3.01 18.0 3.25 18.6 3.51 19.2 3.75 2250 13.3 1.91 14.2 2.14 15.0 2.34 15.7 2.57 16.4 2.77 17.0 2.97 17.6 3.14 18.2 3.39 18.8 3.65 19.4 3.90 2300 13.6 2.01 14.4 2.26 15.2 2.47 15.9 2.69 16.6 2.92 17.2 3.12 17.8 3.30 18.4 3.52 19.0 3.80 19.5 4.06 2350 13.8 2.13 14.6 2.38 15.4 2.60 16.1 2.82 16.8 3.07 17.4 3.26 18.0 3.47 18.6 3.67 19.2 3.93 19.7 4.22 LEGEND nuisance tripping or premature motor failure. Unit warranty will not be affected. See Evaporator-Fan Motor Performance table on BkW — Fan Input kW x Motor Efficiency page 30 or additional information. kW — Kilowatt Input to Motor 6. Use of a field-supplied motor may affect wire sizing. Contact your NOTES: Carrier representative to verify. 1. Boldface indicates field-supplied drive required (see Note 3). 7. To convert kW to bkW: BkW = kW x Motor Efficiency 2. indicates field-supplied motor and drive required. Motor Efficiency: .85 Maximum Continuous kW: 3.31 3. Factory-shipped drive range is 11.83 to 14.83 r/s. Other r/s’s may 8. Interpolation is permissible. Do not extrapolate. require a field-supplied drive. 9. Static pressure losses (i.e., economizer, electric heater) must be 4. Values include losses for filters, unit casing, and wet coils. added to external static pressure before entering Fan Performance 5. Extensive motor and electrical testing on these units ensures that table. the full range of the motor can be utilized with confidence. Using your fan motors up to the kW ratings shown will not result in 23
24 | Performance data (cont) FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS 50TFF007 (17.6 kW) — STANDARD MOTOR (BELT DRIVE) External Static Pressure (Pa) Airflow 25 50 100 150 200 250 300 350 400 (L/s) R/s kW R/s kW R/s kW R/s kW R/s kW R/s kW R/s kW R/s kW R/s kW 700 10.8 0.25 12.0 0.30 13.9 0.41 15.6 0.53 17.0 0.67 18.4 0.83 19.8 1.04 21.2 1.27 21.9 1.38 750 11.5 0.30 12.5 0.35 14.4 0.47 16.1 0.60 17.5 0.74 18.8 0.88 20.1 1.09 21.5 1.31 22.3 1.42 800 12.1 0.35 13.1 0.41 14.9 0.53 16.5 0.67 17.9 0.81 19.2 0.96 20.4 1.12 21.7 1.36 22.6 1.50 850 12.8 0.49 13.7 0.53 15.4 0.64 17.0 0.76 18.3 0.89 19.6 1.03 20.8 1.19 21.9 1.35 23.0 1.52 900 13.4 0.54 14.3 0.59 15.9 0.71 17.5 0.84 18.8 0.97 20.0 1.11 21.3 1.28 22.3 1.44 23.4 1.63 950 14.1 0.61 14.9 0.65 16.5 0.78 17.9 0.92 19.3 1.06 20.5 1.20 21.7 1.37 22.8 1.55 23.8 1.73 1000 14.7 0.67 15.5 0.73 17.0 0.85 18.4 1.00 19.8 1.15 21.0 1.31 22.1 1.48 23.2 1.66 24.2 1.85 1050 15.4 0.75 16.1 0.82 17.6 0.95 18.9 1.10 20.3 1.27 21.5 1.43 22.5 1.60 23.6 1.78 24.6 1.98 1100 16.1 0.85 16.7 0.91 18.2 1.05 19.5 1.21 20.8 1.37 22.0 1.56 23.0 1.73 24.0 1.91 25.1 2.10 1150 16.8 0.95 17.4 1.01 18.7 1.17 20.0 1.31 21.2 1.49 22.4 1.69 23.5 1.87 24.5 2.05 25.5 2.23 1200 17.5 1.05 18.1 1.10 19.6 1.25 20.5 1.41 21.8 1.61 22.8 1.77 24.1 2.01 25.0 2.20 26.0 2.39 LEGEND nuisance tripping or premature motor failure. Unit warranty will not be affected. See Evaporator-Fan Motor Performance table on BkW — Fan Input kW x Motor Efficiency page 30 or additional information. kW — Kilowatt Input to Motor 6. Use of a field-supplied motor may affect wire sizing. Contact your NOTES: Carrier representative to verify. 1. Boldface indicates field-supplied drive required (see Note 3). 7. To convert kW to bkW: BkW = kW x Motor Efficiency 2. indicates field-supplied motor and drive required. Motor Efficiency: .81 Maximum Continuous kW: 2.12 3. Factory-shipped drive range is 15.50 to 20.08 r/s. Other r/s’s may 8. Interpolation is permissible. Do not extrapolate. require a field-supplied drive. 9. Static pressure losses (i.e., economizer, electric heater) must be 4. Values include losses for filters, unit casing, and wet coils. added to external static pressure before entering Fan Performance 5. Extensive motor and electrical testing on these units ensures that table. the full range of the motor can be utilized with confidence. Using your fan motors up to the kW ratings shown will not result in 50TFF008,009 (21.5 AND 24.3 kW) — STANDARD MOTOR (BELT DRIVE) External Static Pressure (Pa) Airflow 50 100 150 200 250 300 350 400 450 500 (L/s) R/s kW R/s kW R/s kW R/s kW R/s kW R/s kW R/s kW R/s kW R/s kW R/s kW 800 6.5 0.29 8.2 0.35 9.4 0.53 10.8 0.71 11.9 0.86 12.7 1.10 13.3 1.31 13.3 1.55 13.5 1.80 13.8 2.08 900 7.1 0.36 8.6 0.45 9.8 0.62 11.1 0.81 12.1 0.95 13.0 1.23 13.6 1.45 13.7 1.70 13.9 1.95 14.2 2.19 1000 7.5 0.43 9.0 0.55 10.2 0.73 11.4 0.92 12.4 1.09 13.3 1.36 13.9 1.59 14.1 1.85 14.3 2.11 14.6 2.35 1100 7.9 0.50 9.4 0.65 10.6 0.84 11.7 1.03 12.7 1.23 13.6 1.49 14.4 1.73 14.9 2.00 15.1 2.27 15.0 2.53 1200 8.3 0.57 9.8 0.75 11.0 0.95 12.0 1.14 13.0 1.37 13.9 1.62 14.8 1.87 15.5 2.15 16.0 2.43 16.4 2.71 1300 8.8 0.66 10.2 0.85 11.3 1.06 12.4 1.29 13.3 1.52 14.2 1.77 15.0 2.04 15.8 2.32 16.5 2.60 17.1 2.88 1400 9.2 0.76 10.6 0.97 11.7 1.19 12.7 1.45 13.7 1.69 14.5 1.93 15.3 2.21 16.1 2.50 16.9 2.78 — — 1500 9.7 0.88 11.0 1.10 12.1 1.34 13.0 1.60 14.0 1.88 14.8 2.14 15.6 2.41 16.4 2.70 — — — — LEGEND nuisance tripping or premature motor failure. Unit warranty will not be affected. See Evaporator-Fan Motor Performance table on BkW — Fan Input kW x Motor Efficiency page 30 or additional information. kW — Kilowatt Input to Motor 6. Use of a field-supplied motor may affect wire sizing. Contact your NOTES: Carrier representative to verify. 1. Boldface indicates field-supplied drive required (see Note 3). 7. To convert kW to bkW: BkW = kW x Motor Efficiency 2. indicates field-supplied motor and drive required. Motor Efficiency: .81 Maximum Continuous kW: 2.12 3. Factory-shipped drive range is 10.33 to 14.67 r/s. Other r/s’s may 8. Interpolation is permissible. Do not extrapolate. require a field-supplied drive. 9. Static pressure losses (i.e., economizer, electric heater) must be 4. Values include losses for filters, unit casing, and wet coils. added to external static pressure before entering Fan Performance 5. Extensive motor and electrical testing on these units ensures that table. the full range of the motor can be utilized with confidence. Using your fan motors up to the kW ratings shown will not result in 24
25 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) 50TFF012 (29.2 kW) — STANDARD MOTOR (BELT DRIVE) External Static Pressure (Pa) Airflow 50 100 150 200 250 300 350 400 450 500 (L/s) R/s kW R/s kW R/s kW R/s kW R/s kW R/s kW R/s kW R/s kW R/s kW R/s kW 1100 7.3 0.30 8.6 0.43 9.8 0.47 10.8 0.60 11.8 0.72 12.8 0.85 13.6 0.90 13.6 0.95 14.2 0.98 14.4 1.04 1200 7.4 0.35 8.7 0.46 9.9 0.58 11.0 0.72 11.9 0.80 12.9 0.86 13.7 0.96 13.8 1.02 14.4 1.08 14.7 1.23 1250 7.6 0.39 8.8 0.49 10.0 0.69 11.1 0.77 12.0 0.88 13.0 0.87 13.8 1.02 13.9 1.08 14.6 1.20 15.0 1.45 1300 7.6 0.56 8.9 0.67 10.2 0.83 11.1 0.91 12.1 1.05 13.1 1.21 13.9 1.22 14.0 0.79 15.0 1.43 15.6 1.64 1400 8.0 0.66 9.3 0.78 10.5 0.91 11.4 1.03 12.4 1.16 13.3 1.30 14.1 1.41 14.6 1.25 15.4 1.64 16.0 1.75 1500 8.4 0.74 9.6 0.87 10.7 0.99 11.8 1.14 12.7 1.28 13.5 1.42 14.3 1.57 15.1 1.67 15.7 1.83 16.4 1.88 1600 8.8 0.85 10.0 0.96 11.1 1.10 12.1 1.25 12.9 1.40 13.8 1.55 14.5 1.70 15.3 1.88 16.0 2.00 16.7 2.09 1700 9.1 0.96 10.3 1.06 11.3 1.22 12.3 1.37 13.2 1.53 14.0 1.69 14.8 1.86 15.5 2.02 16.3 2.23 17.0 2.36 1800 9.5 1.09 10.7 1.18 11.7 1.34 12.6 1.51 13.5 1.68 14.3 1.86 15.0 2.03 15.8 2.21 16.4 2.40 17.2 2.62 1900 9.9 1.24 11.0 1.31 12.0 1.48 12.9 1.66 13.8 1.84 14.6 2.04 15.3 2.21 16.0 2.42 16.7 2.61 17.3 2.82 LEGEND nuisance tripping or premature motor failure. Unit warranty will not be affected. See Evaporator-Fan Motor Performance table on BkW — Fan Input kW x Motor Efficiency page 30 or additional information. kW — Kilowatt Input to Motor 6. Use of a field-supplied motor may affect wire sizing. Contact your NOTES: Carrier representative to verify. 1. Boldface indicates field-supplied drive required (see Note 3). 7. To convert kW to bkW: BkW = kW x Motor Efficiency 2. indicates field-supplied motor and drive required. Motor Efficiency: .83 Maximum Continuous kW: 2.12 3. Factory-shipped drive range is 11.50 to 15.00 r/s. Other r/s’s may 8. Interpolation is permissible. Do not extrapolate. require a field-supplied drive. 9. Static pressure losses (i.e., economizer, electric heater) must be 4. Values include losses for filters, unit casing, and wet coils. added to external static pressure before entering Fan Performance 5. Extensive motor and electrical testing on these units ensures that table. the full range of the motor can be utilized with confidence. Using your fan motors up to the kW ratings shown will not result in 50TFF014 (35.9 kW) — STANDARD MOTOR (BELT DRIVE) External Static Pressure (Pa) Airflow 50 100 150 200 250 300 350 400 450 500 (L/s) R/s kW R/s kW R/s kW R/s kW R/s kW R/s kW R/s kW R/s kW R/s kW R/s kW 1500 9.0 0.58 10.2 0.73 11.3 0.88 12.1 1.00 13.2 1.21 14.2 1.24 15.1 1.28 16.0 1.44 16.5 1.68 17.3 1.80 1550 9.2 0.62 10.4 0.79 11.5 0.94 12.3 1.06 13.2 1.24 14.3 1.29 15.1 1.41 16.0 1.59 16.6 1.81 17.3 1.93 1600 9.4 0.67 10.6 0.84 11.7 1.01 12.5 1.14 13.3 1.28 14.4 1.38 15.2 1.54 16.1 1.73 16.6 1.94 17.4 2.06 1650 9.7 0.73 10.8 0.89 11.9 1.08 12.7 1.21 13.5 1.35 14.5 1.48 15.3 1.67 16.1 1.86 16.7 2.02 17.4 2.15 1700 9.9 0.79 11.0 0.96 12.1 1.14 12.9 1.29 13.6 1.44 14.6 1.64 15.4 1.82 16.2 1.94 16.8 2.13 17.5 2.29 1750 10.1 0.94 11.2 1.11 12.2 1.26 13.0 1.42 13.9 1.56 14.7 1.75 15.5 1.94 16.2 2.12 16.9 2.29 17.4 2.44 1800 10.4 1.01 11.4 1.17 12.4 1.33 13.3 1.51 14.0 1.64 14.8 1.81 15.6 2.02 16.3 2.21 17.0 2.40 17.6 2.56 1850 10.6 1.07 11.6 1.22 12.5 1.40 13.5 1.59 14.2 1.72 15.0 1.89 15.7 2.10 16.5 2.32 17.2 2.51 17.8 2.68 1900 10.8 1.13 11.8 1.29 12.7 1.46 13.7 1.68 14.4 1.81 15.1 1.98 15.8 2.19 16.6 2.40 17.3 2.60 18.0 2.80 1950 11.1 1.21 12.0 1.35 12.9 1.55 13.8 1.76 14.5 1.91 15.3 2.07 16.0 2.27 16.7 2.51 17.4 2.71 18.1 2.92 2000 11.3 1.29 12.1 1.43 13.1 1.63 14.0 1.84 14.7 2.01 15.4 2.17 16.2 2.36 16.8 2.60 17.5 2.82 18.2 3.04 2050 11.6 1.36 12.3 1.51 13.2 1.71 14.1 1.92 14.9 2.12 15.6 2.28 16.3 2.47 17.0 2.70 17.6 2.93 18.3 3.15 2100 11.9 1.45 12.5 1.58 13.4 1.81 14.3 2.00 15.1 2.23 15.8 2.39 16.5 2.58 17.1 2.80 17.8 3.04 18.4 3.29 2150 12.0 1.54 12.7 1.67 13.6 1.89 14.5 2.09 15.3 2.34 15.9 2.51 16.6 2.69 17.3 2.90 17.9 3.16 18.6 3.41 2200 12.4 1.64 12.9 1.76 13.8 1.99 14.6 2.19 15.5 2.45 16.1 2.64 16.8 2.82 17.4 3.02 18.1 3.28 18.7 3.55 2250 12.6 1.75 13.1 1.85 14.0 2.08 14.8 2.30 15.6 2.56 16.3 2.77 16.9 2.94 17.6 3.14 18.2 3.40 18.8 3.67 2300 12.9 1.85 13.3 1.95 14.2 2.19 15.0 2.42 15.8 2.65 16.5 2.91 17.1 3.08 17.7 3.29 18.4 3.51 19.0 3.80 2350 13.2 1.95 13.5 2.06 14.4 2.29 15.2 2.54 16.0 2.77 16.7 3.04 17.3 3.23 17.9 3.44 18.5 3.65 19.1 3.92 LEGEND nuisance tripping or premature motor failure. Unit warranty will not be affected. See Evaporator-Fan Motor Performance table on BkW — Fan Input kW x Motor Efficiency page 30 or additional information. kW — Kilowatt Input to Motor 6. Use of a field-supplied motor may affect wire sizing. Contact your NOTES: Carrier representative to verify. 1. Boldface indicates field-supplied drive required (see Note 3). 7. To convert kW to bkW: BkW = kW x Motor Efficiency 2. indicates field-supplied motor and drive required. Motor Efficiency: .85 Maximum Continuous kW: 3.31 3. Factory-shipped drive range is 11.83 to 14.83 r/s. Other r/s’s may 8. Interpolation is permissible. Do not extrapolate. require a field-supplied drive. 9. Static pressure losses (i.e., economizer, electric heater) must be 4. Values include losses for filters, unit casing, and wet coils. added to external static pressure before entering Fan Performance 5. Extensive motor and electrical testing on these units ensures that table. the full range of the motor can be utilized with confidence. Using your fan motors up to the kW ratings shown will not result in 25
26 | Performance data (cont) FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS 50TFF007 (5 TONS) — STANDARD MOTOR (BELT DRIVE) External Static Pressure (in. wg) Airflow 0.1 0.2 0.4 0.6 0.8 1.0 1.2 1.4 1.6 (Cfm) Rpm Watts Rpm Watts Rpm Watts Rpm Watts Rpm Watts Rpm Watts Rpm Watts Rpm Watts Rpm Watts 1500 731 304 789 368 895 488 990 617 1074 764 1130 875 1168 921 1250 1059 1345 1216 1600 772 359 826 424 930 562 1019 691 1105 847 1174 985 1213 1078 1315 1197 1401 1335 1700 814 424 865 497 964 636 1050 774 1134 930 1208 1096 1265 1234 1348 1455 1421 1639 1800 852 562 905 615 1002 739 1084 859 1163 998 1235 1156 1303 1318 1371 1499 1433 1638 1900 894 630 945 692 1037 818 1119 948 1194 1089 1266 1250 1330 1413 1396 1604 1460 1796 2000 936 708 984 771 1072 899 1154 1047 1226 1190 1297 1361 1362 1534 1422 1718 1485 1910 2100 978 795 1024 859 1108 998 1190 1156 1259 1310 1327 1473 1393 1656 1452 1840 1510 2041 2200 1021 891 1064 956 1145 1097 1225 1275 1294 1439 1359 1604 1423 1779 1483 1980 1538 2171 2300 1064 998 1104 1064 1183 1216 1260 1396 1330 1578 1392 1744 1454 1927 1515 2128 1569 2326 2400 1107 1114 1145 1182 1222 1353 1296 1534 1365 1718 1426 1901 1485 2084 1544 2283 1601 2459 2500 1150 1241 1186 1318 1262 1491 1331 1674 1400 1875 1461 2067 1518 2249 1575 2445 — — LEGEND Evaporator-Fan Motor Performance table on page 30 for additional information. Bhp — Brake Horsepower 6. Use of a field-supplied motor may affect wire sizing. Contact your Carrier Watts — Input Watts to Motor representative to verify. NOTES: 7. To convert Watts to Bhp: 1. Boldface indicates field-supplied drive required (see Note 3). Watts x Motor Efficiency 2. indicates field-supplied motor and drive required. Bhp = 746 3. Factory-shipped drive range is 930 to 1205 rpm. Other rpms may require a field-supplied drive. Motor Efficiency: .81 Maximum Continuous Watts: 2120 4. Values include losses for filters, unit casing, and wet coils. 8. Interpolation is permissible. Do not extrapolate. 5. Extensive motor and electrical testing on these units ensures that the full 9. Static pressure losses (i.e., economizer, electric heater) must be added to range of the motor can be utilized with confidence. Using your fan motors external static pressure before entering Fan Performance table. up to the wattage ratings shown will not result in nuisance tripping or premature motor failure. Unit warranty will not be affected. See 50TFF008,009 (6.1 AND 6.9 TONS) — STANDARD MOTOR (BELT DRIVE) External Static Pressure (in. wg) Airflow 0.2 0.4 0.6 0.8 1.0 1.2 1.4 1.6 1.8 2.0 (Cfm) Rpm Watts Rpm Watts Rpm Watts Rpm Watts Rpm Watts Rpm Watts Rpm Watts Rpm Watts Rpm Watts Rpm Watts 1950 466 429 564 567 623 731 689 894 745 1041 799 1250 861 1616 922 1902 759 2219 1004 2640 2000 473 448 571 590 571 755 694 923 750 1079 804 1289 864 1638 924 1928 790 2246 1007 2652 2100 488 486 585 637 641 803 705 981 761 1156 814 1368 871 1682 929 1980 853 2283 1013 2677 2200 503 524 585 684 653 851 716 1039 772 1233 824 1447 878 1727 934 2032 916 2326 1019 2702 2250 511 539 592 708 659 875 722 1072 778 1275 829 1491 884 1744 937 2058 947 2343 1022 2710 2300 518 562 599 731 665 899 727 1097 783 1310 834 1526 885 1770 939 2084 979 2369 1025 2727 2400 534 607 613 787 677 965 738 1165 794 1378 844 1604 892 1840 944 2119 987 2428 1039 2791 2500 549 653 627 835 690 1031 750 1233 805 1456 855 1691 902 1927 949 2188 1002 2495 1041 2831 2550 557 684 633 867 697 1064 756 1267 811 1499 861 1735 908 1980 953 2232 1003 2521 1045 2854 2600 565 708 639 891 703 1097 761 1301 816 1543 866 1779 913 2023 957 2275 1004 2554 1050 2878 2700 581 763 652 948 717 1173 773 1378 827 1621 878 1875 924 2128 967 2377 1010 2637 1056 2925 2800 597 827 665 1014 713 1250 786 1473 839 1709 889 1971 935 2223 978 2479 1019 2735 1061 3002 2900 613 891 679 1081 745 1335 799 1560 850 1805 900 2067 946 2335 989 2595 1030 2847 — — 3000 629 965 694 1156 759 1413 812 1665 862 1901 911 2171 957 2445 1000 2702 1040 2956 — — 3100 646 1039 709 1241 772 1508 825 1761 875 2015 923 2275 968 2554 1011 2832 — — — — 3200 662 1123 724 1335 785 1595 840 1866 887 2128 934 2386 980 2661 1022 2933 — — — — 3300 679 1207 740 1430 798 1691 854 1980 900 2240 946 2504 991 2775 — — — — — — 3400 696 1301 756 1534 811 1788 868 2093 914 2369 959 2629 1003 2886 — — — — — — 3500 712 1396 771 1639 824 1892 881 2206 928 2495 971 2759 1014 3009 — — — — — — LEGEND Evaporator-Fan Motor Performance table on page 30 for additional Bhp — Brake Horsepower information. 6. Use of a field-supplied motor may affect wire sizing. Contact your Carrier Watts — Input Watts to Motor representative to verify. NOTES: 7. To convert Watts to Bhp: 1. Boldface indicates field-supplied drive required (see Note 3). Watts x Motor Efficiency 2. indicates field-supplied motor and drive required. Bhp = 746 3. Factory-shipped drive range is 620 to 880 rpm. Other rpms may require a field-supplied drive. Motor Efficiency: .81 Maximum Continuous Watts: 2120 4. Values include losses for filters, unit casing, and wet coils. 8. Interpolation is permissible. Do not extrapolate. 5. Extensive motor and electrical testing on these units ensures that the full 9. Static pressure losses (i.e., economizer, electric heater) must be added to range of the motor can be utilized with confidence. Using your fan motors external static pressure before entering Fan Performance table. up to the wattage ratings shown will not result in nuisance tripping or premature motor failure. Unit warranty will not be affected. See 26
27 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) 50TFF012 (8.3 TONS) — STANDARD MOTOR (BELT DRIVE) External Static Pressure (in. wg) Airflow 0.2 0.4 0.6 0.8 1.0 1.2 1.4 1.6 1.8 2.0 (Cfm) Rpm Watts Rpm Watts Rpm Watts Rpm Watts Rpm Watts Rpm Watts Rpm Watts Rpm Watts Rpm Watts Rpm Watts 2500 471 369 552 494 617 611 679 719 740 818 757 881 765 944 811 1034 889 1321 946 1645 2600 483 404 562 530 627 656 685 773 754 881 765 944 775 1025 825 1097 907 1429 959 1771 2700 495 449 573 575 638 710 694 827 757 944 775 1007 793 1088 848 1240 929 1528 975 1878 2800 508 485 583 620 648 755 704 881 759 1007 791 1070 808 1186 887 1357 954 1690 987 1959 2900 521 530 594 665 659 809 714 944 766 1070 807 1150 823 1339 918 1519 963 1834 999 2040 3000 532 630 605 763 670 891 725 1014 778 1148 825 1275 874 1422 926 1613 974 1920 1012 2134 3100 544 677 616 803 680 940 735 1081 787 1216 835 1353 880 1491 933 1656 983 1963 1017 2177 3200 557 716 628 859 690 998 746 1148 796 1284 844 1430 888 1569 934 1718 988 1980 1025 2230 3300 570 763 639 907 700 1064 757 1216 805 1353 854 1508 897 1648 940 1853 989 2031 1032 2282 3400 583 818 651 965 711 1123 767 1284 815 1430 863 1587 907 1744 947 1946 991 2099 1038 2318 3500 596 867 663 1031 721 1190 777 1353 826 1517 871 1665 916 1831 956 2039 997 2195 1043 2380 3600 609 924 674 1097 732 1267 787 1430 836 1595 880 1753 926 1927 966 2134 1004 2291 1045 2478 3700 622 989 686 1165 744 1335 797 1508 847 1691 890 1849 934 2015 976 2238 1013 2397 1051 2569 3800 635 1047 698 1241 755 1413 808 1595 857 1779 901 1945 943 2160 985 2344 1023 2514 1059 2688 3900 649 1123 713 1318 767 1491 818 1683 867 1866 912 2050 952 2265 994 2451 1032 2633 1068 2819 4000 662 1190 722 1396 778 1578 829 1779 878 1962 922 2203 962 2371 1003 2560 1042 2763 1078 2952 4100 675 1267 734 1482 790 1674 839 1875 888 2058 933 2309 973 2496 1011 2679 1051 2895 1087 3097 4200 689 1353 746 1569 801 1761 851 1971 898 2212 943 2424 983 2624 1021 2810 1060 3029 1090 3276 LEGEND Evaporator-Fan Motor Performance table on page 30 for additional information. Bhp — Brake Horsepower 6. Use of a field-supplied motor may affect wire sizing. Contact your Carrier Watts — Input Watts to Motor representative to verify. NOTES: 7. To convert Watts to Bhp: 1. Boldface indicates field-supplied drive required (see Note 3). Watts x Motor Efficiency 2. indicates field-supplied motor and drive required. Bhp = 746 3. Factory-shipped drive range is 690 to 900 rpm. Other rpms may require a field-supplied drive. Motor Efficiency: .83 Maximum Continuous Watts: 2120 4. Values include losses for filters, unit casing, and wet coils. 8. Interpolation is permissible. Do not extrapolate. 5. Extensive motor and electrical testing on these units ensures that the full 9. Static pressure losses (i.e., economizer, electric heater) must be added to range of the motor can be utilized with confidence. Using your fan motors external static pressure before entering Fan Performance table. up to the wattage ratings shown will not result in nuisance tripping or premature motor failure. Unit warranty will not be affected. See 50TFF014 (10.2 TONS) — STANDARD MOTOR (BELT DRIVE) External Static Pressure (in. wg) Airflow 0.2 0.4 0.6 0.8 1.0 1.2 1.4 1.6 1.8 2.0 (Cfm) Rpm Watts Rpm Watts Rpm Watts Rpm Watts Rpm Watts Rpm Watts Rpm Watts Rpm Watts Rpm Watts Rpm Watts 3100 570 623 636 799 693 886 748 1044 800 1202 850 1281 901 1360 950 1474 989 1597 1000 1755 3200 584 676 649 842 705 948 759 1097 809 1281 858 1352 907 1457 960 1571 1001 1703 1006 1834 3300 598 728 662 904 717 1027 769 1158 819 1342 867 1483 914 1536 963 1668 1010 1799 1018 1940 3400 612 781 675 957 729 1115 780 1229 829 1414 876 1589 922 1606 968 1764 1018 1940 1022 2045 3500 626 873 688 1018 741 1202 792 1299 840 1483 886 1676 930 1773 975 1826 1021 2062 1039 2203 3600 640 913 702 1080 754 1290 803 1378 851 1553 896 1755 940 1913 983 1887 1026 2212 1051 2370 3700 654 1065 714 1218 767 1373 815 1514 861 1666 906 1862 950 2027 991 2202 1030 2361 1064 2512 3800 668 1129 727 1291 780 1456 827 1598 873 1751 916 1948 959 2123 1001 2299 1040 2476 1075 2638 3900 683 1194 741 1365 793 1540 839 1691 884 1836 927 2035 969 2228 1010 2405 1049 2593 1085 2773 4000 697 1267 754 1448 806 1624 851 1785 895 1931 938 2123 979 2334 1020 2521 1059 2710 1095 2901 4100 711 1340 767 1531 819 1708 864 1879 907 2035 949 2219 989 2441 1029 2638 1068 2837 1105 3028 4200 726 1423 780 1624 832 1802 877 1983 919 2149 960 2316 1000 2548 1039 2764 1077 2955 1114 3166 4300 741 1506 794 1717 845 1897 889 2096 931 2263 971 2423 1011 2647 1049 2882 1087 3092 1124 3304 4400 755 1598 808 1819 858 2000 902 2210 943 2387 983 2548 1022 2764 1059 3010 1097 3230 1133 3442 4500 770 1700 821 1923 871 2114 915 2325 955 2512 995 2683 1033 2882 1070 3138 1107 3368 1143 3590 4600 784 1794 835 2027 884 2219 928 2450 968 2638 1006 2828 1044 3010 1081 3258 1117 3516 1152 3748 4700 799 1905 849 2140 897 2343 941 2566 981 2773 1018 2964 1056 3147 1092 3387 1127 3655 1162 3897 4800 814 2009 863 2254 910 2468 954 2692 993 2919 1030 3111 1067 3304 1103 3525 1138 3804 1172 4055 4900 829 2131 877 2378 923 2602 967 2828 1006 3065 1043 3267 1079 3470 1114 3674 1149 3934 1182 4223 5000 843 2246 892 2503 937 2746 980 2964 1019 3221 1055 3424 1091 3637 1126 3822 1160 4083 1193 4382 5100 858 2378 906 2629 950 2891 993 3111 1032 3388 1068 3590 1103 3804 1137 4009 1171 4242 1204 4531 LEGEND premature motor failure. Unit warranty will not be affected. See Evaporator-Fan Motor Performance table on page 30 for additional Bhp — Brake Horsepower information. Watts — Input Watts to Motor 6. Use of a field-supplied motor may affect wire sizing. Contact your Carrier NOTES: representative to verify. 1. Boldface indicates field-supplied drive required (see Note 3). 7. To convert Watts to Bhp: 2. indicates field-supplied motor and drive required. Watts x Motor Efficiency Bhp = 3. Factory-shipped drive range is 710 to 890 rpm. Other rpms may require a 746 field-supplied drive. 4. Values include losses for filters, unit casing, and wet coils. Motor Efficiency: .85 Maximum Continuous Watts: 3313 5. Extensive motor and electrical testing on these units ensures that the full 8. Interpolation is permissible. Do not extrapolate. range of the motor can be utilized with confidence. Using your fan motors 9. Static pressure losses (i.e., economizer, electric heater) must be added to up to the wattage ratings shown will not result in nuisance tripping or external static pressure before entering Fan Performance table. 27
28 | Performance data (cont) FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHRGE UNITS 50TFF007 (5 TONS) — STANDARD MOTOR (BELT DRIVE) External Static Pressure (in. wg) Airflow 0.1 0.2 0.4 0.6 0.8 1.0 1.2 1.4 1.6 (Cfm) Rpm Watts Rpm Watts Rpm Watts Rpm Watts Rpm Watts Rpm Watts Rpm Watts Rpm Watts Rpm Watts 1500 656 258 722 304 840 424 939 543 1024 672 1106 829 1195 995 1269 1179 1347 1354 1600 691 304 753 350 867 470 965 608 1050 737 1127 884 1207 1078 1285 1262 1360 1464 1700 727 350 785 405 895 534 991 672 1076 811 1151 958 1222 1123 1301 1354 1370 1566 1800 765 487 821 532 923 638 1019 843 1099 883 1178 1031 1249 1182 1316 1353 1382 1526 1900 802 539 854 585 953 700 1046 835 1126 965 1201 1106 1274 1275 1338 1439 1402 1621 2000 840 600 888 646 984 771 1073 907 1154 1047 1226 1190 1297 1361 1363 1534 1424 1718 2100 878 669 923 716 1015 843 1101 981 1182 1140 1252 1292 1320 1456 1388 1639 1448 1831 2200 916 739 958 795 1046 924 1129 1072 1209 1241 1280 1404 1345 1569 1410 1744 1473 1945 2300 954 827 993 883 1079 1022 1160 1173 1237 1344 1309 1517 1372 1691 1434 1866 1496 2067 2400 993 916 1029 973 1112 1123 1190 1275 1264 1447 1336 1639 1400 1823 1459 1997 1519 2188 2500 1031 1022 1066 1081 1145 1241 1220 1396 1292 1569 1363 1770 1428 1962 1486 2145 1543 2335 LEGEND Evaporator-Fan Motor Performance table on page 30 for additional information. Bhp — Brake Horsepower 6. Use of a field-supplied motor may affect wire sizing. Contact your Carrier Watts — Input Watts to Motor representative to verify. NOTES: 7. To convert Watts to Bhp: 1. Boldface indicates field-supplied drive required (see Note 3). Watts x Motor Efficiency 2. indicates field-supplied motor and drive required. Bhp = 746 3. Factory-shipped drive range is 930 to 1205 rpm. Other rpms may require a field-supplied drive. Motor Efficiency: .81 Maximum Continuous Watts: 2120 4. Values include losses for filters, unit casing, and wet coils. 8. Interpolation is permissible. Do not extrapolate. 5. Extensive motor and electrical testing on these units ensures that the full 9. Static pressure losses (i.e., economizer, electric heater) must be added to range of the motor can be utilized with confidence. Using your fan motors external static pressure before entering Fan Performance table. up to the wattage ratings shown will not result in nuisance tripping or premature motor failure. Unit warranty will not be affected. See 50TFF008,009 (6.1 AND 6.9 TONS) — STANDARD MOTOR (BELT DRIVE) External Static Pressure (in. wg) Airflow 0.2 0.4 0.6 0.8 1.0 1.2 1.4 1.6 1.8 2.0 (Cfm) Rpm Watts Rpm Watts Rpm Watts Rpm Watts Rpm Watts Rpm Watts Rpm Watts Rpm Watts Rpm Watts Rpm Watts 1950 429 410 424 538 600 659 671 843 736 1046 778 1252 800 1501 765 1735 736 1945 666 2060 2000 435 421 429 553 605 683 675 867 739 1071 783 1282 808 1532 795 1770 759 1988 697 2123 2100 447 443 439 584 615 731 683 916 746 1122 794 1343 825 1594 826 1840 805 2075 760 2250 2200 459 465 549 615 625 779 691 965 753 1173 805 1404 842 1656 857 1910 851 2162 823 2377 2250 465 473 554 630 630 803 695 989 757 1199 810 1439 850 1691 873 1945 863 2206 855 2445 2300 471 487 559 646 635 827 699 1014 760 1224 816 1465 859 1718 888 1980 897 2249 887 2504 2400 482 524 569 684 645 875 708 1064 768 1284 824 1526 872 1779 909 2050 931 2326 935 2595 2500 494 554 581 723 654 924 717 1123 776 1344 832 1587 882 1849 925 2119 955 2394 972 2678 2550 501 577 587 747 659 956 722 1156 780 1378 836 1621 887 1884 931 2162 964 2436 986 2718 2600 507 592 592 771 663 981 727 1182 784 1404 839 1656 891 1919 936 2197 973 2479 999 2759 2700 520 638 604 827 672 1031 737 1250 793 1473 846 1726 898 1997 946 2275 987 2554 1019 2839 2800 533 684 615 875 683 1081 747 1327 802 1552 855 1805 906 2076 954 2352 997 2637 1034 2917 2900 546 731 626 932 693 1140 756 1396 813 1630 863 1884 913 2154 961 2436 1006 2727 — — 3000 559 779 637 989 704 1207 765 1473 823 1718 872 1962 921 2240 969 2529 1014 2807 — — 3100 572 835 648 1056 715 1275 775 1543 832 1814 882 2058 930 2335 976 2620 1021 2902 — — 3200 585 883 660 1114 727 1353 785 1321 841 1901 892 2162 939 2428 984 2710 — — — — 3300 598 940 671 1182 739 1439 795 1691 851 1997 902 2266 948 2529 993 2799 — — — — 3400 610 998 682 1258 750 1526 806 1779 860 2084 912 2369 958 2637 1002 2902 — — — — 3500 623 1056 694 1335 761 1613 817 1866 870 2180 921 2479 968 2751 — — — — — — LEGEND Evaporator-Fan Motor Performance table on page 30 for additional information. Bhp — Brake Horsepower 6. Use of a field-supplied motor may affect wire sizing. Contact your Carrier Watts — Input Watts to Motor representative to verify. NOTES: 7. To convert Watts to Bhp: 1. Boldface indicates field-supplied drive required (see Note 3). Watts x Motor Efficiency 2. indicates field-supplied motor and drive required. Bhp = 746 3. Factory-shipped drive range is 620 to 880 rpm. Other rpms may require a field-supplied drive. Motor Efficiency: .81 Maximum Continuous Watts: 2120 4. Values include losses for filters, unit casing, and wet coils. 8. Interpolation is permissible. Do not extrapolate. 5. Extensive motor and electrical testing on these units ensures that the full 9. Static pressure losses (i.e., economizer, electric heater) must be added to range of the motor can be utilized with confidence. Using your fan motors external static pressure before entering Fan Performance table. up to the wattage ratings shown will not result in nuisance tripping or premature motor failure. Unit warranty will not be affected. See 28
29 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) 50TFF012 (8.3 TONS) — STANDARD MOTOR (BELT DRIVE) External Static Pressure (in. wg) Airflow 0.2 0.4 0.6 0.8 1.0 1.2 1.4 1.6 1.8 2.0 (Cfm) Rpm Watts Rpm Watts Rpm Watts Rpm Watts Rpm Watts Rpm Watts Rpm Watts Rpm Watts Rpm Watts Rpm Watts 2500 437 333 517 440 590 566 653 692 712 755 770 827 805 881 811 944 830 998 883 1240 2600 448 369 526 476 597 602 660 746 717 836 778 881 815 926 822 989 843 1079 898 1357 2700 460 404 534 512 605 638 668 791 723 908 779 944 825 980 835 1052 855 1186 910 1474 2800 471 449 544 557 613 683 675 361 730 971 783 1052 830 1070 843 1150 868 1303 924 1546 2900 483 494 553 593 620 728 682 881 738 1034 789 1150 840 1159 860 1195 880 1429 942 1681 3000 484 562 560 677 631 810 690 940 747 1081 800 1233 850 1353 879 1233 925 1604 964 1761 3100 495 607 570 723 638 851 699 998 755 1140 805 1284 857 1447 896 1473 935 1709 975 1811 3200 505 646 579 763 646 899 708 1047 761 1199 812 1344 862 1517 908 1639 944 1836 984 1903 3300 516 692 589 810 655 956 717 1106 767 1250 819 1413 867 1578 915 1753 952 1920 993 2014 3400 527 739 599 859 664 1006 724 1165 775 1318 827 1482 873 1639 920 1831 963 2005 1001 2091 3500 537 795 609 907 672 1064 731 1216 784 1387 833 1552 880 1718 926 1901 970 2134 1007 2221 3600 548 851 619 956 680 1114 738 1275 794 1456 840 1621 888 1805 931 1971 976 2230 1017 2362 3700 560 916 629 1014 688 1173 747 1344 802 1534 847 1700 895 1884 938 2108 981 2309 1024 2496 3800 571 981 639 1072 698 1241 756 1422 810 1604 856 1788 901 1971 945 2203 986 2389 1029 2605 3900 582 1047 649 1140 708 1310 764 1499 816 1674 865 1875 908 2050 953 2300 993 2478 1034 2707 4000 593 1123 659 1207 717 1387 773 1578 823 1753 875 1962 915 2186 960 2389 1000 2587 1039 2800 4100 605 1207 670 1284 727 1465 781 1648 832 1840 883 2050 924 2291 966 2487 1008 2698 1046 2904 4200 616 1292 680 1361 737 1543 789 1726 841 1927 889 2177 934 2389 972 2587 1015 2819 1053 3029 LEGEND Evaporator-Fan Motor Performance table on page 30 for additional information. Bhp — Brake Horsepower 6. Use of a field-supplied motor may affect wire sizing. Contact your Carrier Watts — Input Watts to Motor representative to verify. NOTES: 7. To convert Watts to Bhp: 1. Boldface indicates field-supplied drive required (see Note 3). Watts x Motor Efficiency 2. indicates field-supplied motor and drive required. Bhp = 746 3. Factory-shipped drive range is 690 to 900 rpm. Other rpms may require a field-supplied drive. Motor Efficiency: .83 Maximum Continuous Watts: 2120 4. Values include losses for filters, unit casing, and wet coils. 8. Interpolation is permissible. Do not extrapolate. 5. Extensive motor and electrical testing on these units ensures that the full 9. Static pressure losses (i.e., economizer, electric heater) must be added to range of the motor can be utilized with confidence. Using your fan motors external static pressure before entering Fan Performance table. up to the wattage ratings shown will not result in nuisance tripping or premature motor failure. Unit warranty will not be affected. See 50TFF014 (10.2 TONS) — STANDARD MOTOR (BELT DRIVE) External Static Pressure (in. wg) Airflow 0.2 0.4 0.6 0.8 1.0 1.2 1.4 1.6 1.8 2.0 (Cfm) Rpm Watts Rpm Watts Rpm Watts Rpm Watts Rpm Watts Rpm Watts Rpm Watts Rpm Watts Rpm Watts Rpm Watts 3100 529 535 605 693 669 834 719 948 775 1158 815 1308 880 1352 911 1606 940 1685 971 1826 3200 541 579 615 746 680 886 729 1009 791 1211 827 1369 889 1448 920 1676 951 1747 985 1922 3300 553 632 626 790 692 948 740 1071 792 1237 832 1413 895 1571 929 1755 965 1843 999 2027 3400 566 685 636 843 702 1018 751 1141 798 1290 845 1510 903 1668 940 1826 980 1940 1010 2133 3500 579 737 647 904 713 1080 763 1220 807 1352 856 1589 911 1747 952 1887 989 2054 1021 2229 3600 593 790 659 957 722 1141 775 1290 817 1431 867 1624 920 1799 965 2010 1000 2150 1035 2308 3700 607 947 670 1113 732 1267 782 1423 833 1565 879 1751 927 1940 973 2123 1013 2290 1046 2432 3800 621 1010 681 1170 742 1332 795 1506 842 1641 889 1819 934 2018 980 2210 1022 2396 1058 2557 3900 636 1073 693 1226 751 1398 808 1590 851 1725 898 1897 942 2105 987 2307 1030 2503 1068 2683 4000 650 1137 705 1291 761 1464 819 1674 861 1811 908 1974 950 2193 994 2405 1037 2602 1077 2801 4100 665 1210 717 1357 772 1548 830 1759 871 1905 917 2070 960 2272 1001 2503 1045 2710 1085 2919 4200 680 1283 728 1431 783 1632 839 1836 883 2009 925 9175 969 2370 1009 2602 1051 2828 1092 3037 4300 696 1365 739 1506 794 1717 848 1914 896 2123 935 2281 979 2468 1018 2701 1058 2937 1100 3157 4400 711 1456 750 1582 805 1811 857 2000 908 2237 945 2387 988 2575 1028 2801 1066 3047 1106 3285 4500 727 1540 762 1666 817 1897 867 2096 919 2343 955 2512 996 2692 1037 2901 1074 3166 1113 3414 4600 742 1641 774 1759 828 1992 877 2193 929 2450 967 2638 1005 2819 1046 3019 1084 3276 1121 3544 4700 758 1742 786 1854 840 2088 888 2307 938 2557 980 2773 1015 2946 1056 3147 1093 3396 1129 3674 4800 773 1845 799 1948 852 2193 899 2423 947 2656 992 9910 1025 3083 1064 3285 1103 3516 1137 3795 4900 789 1958 812 2053 863 2290 910 2548 957 2773 1003 3047 1036 3230 1073 3433 1112 3655 1147 3925 5000 805 2070 826 2166 875 2405 921 2665 966 2891 1014 3184 1049 3396 1083 3590 1121 3804 1157 4055 5100 821 2202 840 2290 887 2521 932 2792 976 3019 1024 3322 1061 3553 1093 3748 1129 3962 1166 4204 LEGEND Evaporator-Fan Motor Performance table on page 30 for additional information. Bhp — Brake Horsepower 6. Use of a field-supplied motor may affect wire sizing. Contact your Carrier Watts — Input Watts to Motor representative to verify. NOTES: 7. To convert Watts to Bhp: 1. Boldface indicates field-supplied drive required (see Note 3). Watts x Motor Efficiency 2. indicates field-supplied motor and drive required. Bhp = 746 3. Factory-shipped drive range is 710 to 890 rpm. Other rpms may require a field-supplied drive. Motor Efficiency: .85 Maximum Continuous Watts: 3313 4. Values include losses for filters, unit casing, and wet coils. 8. Interpolation is permissible. Do not extrapolate. 5. Extensive motor and electrical testing on these units ensures that the full 9. Static pressure losses (i.e., economizer, electric heater) must be added to range of the motor can be utilized with confidence. Using your fan motors external static pressure before entering Fan Performance table. up to the wattage ratings shown will not result in nuisance tripping or premature motor failure. Unit warranty will not be affected. See 29
30 | Performance data (cont) EVAPORATOR-FAN MOTOR PERFORMANCE MAXIMUM MAXIMUM MAXIMUM UNIT UNIT RATED ACCEPTABLE ACCEPTABLE ACCEPTABLE MAXIMUM 50TFF VOLTAGE CONTINUOUS CONTINUOUS OPERATING AMP DRAW BkW* BHP* WATTS 007 400 1.79 2.40 2,120 3.0 008 400 1.79 2.40 2,120 3.0 009 400 1.79 2.40 2,120 3.0 012 400 1.79 2.40 2,120 3.0 014 400 2.76 3.70 3,313 5.5 LEGEND *Extensive motor and electrical testing on these units ensures that the full range of the motors can be utilized with confidence. Using your fan Bhp — Brake Horsepower motors up to the ratings shown in this table will not result in nuisance BkW — kW x Motor Efficiency tripping or premature motor failure. Unit warranty will not be affected. FAN R/s AT MOTOR PULLEY SETTINGS* (SI) MOTOR PULLEY TURNS OPEN UNIT 50TFF 0 1/2 1 11/2 2 21/2 3 31/2 4 41/2 5 007 20.08 19.67 19.17 18.75 18.25 17.83 17.33 16.92 16.42 16.00 15.50 008,009 14.67 14.25 13.83 13.33 12.92 12.50 12.08 11.67 11.25 10.83 10.33 012 15.00 14.58 14.25 13.92 13.58 13.25 12.92 12.58 12.25 11.92 11.50 014 14.83 14.58 14.25 13.72 13.67 13.33 13.08 12.75 12.50 12.17 11.83 *Approximate fan r/s shown. FAN RPM AT MOTOR PULLEY SETTINGS* (ENGLISH) UNIT MOTOR PULLEY TURNS OPEN 50TFF 0 1/2 1 11/2 2 21/2 3 31/2 4 41/2 5 007 1205 1180 1150 1125 1095 1070 1040 1015 985 960 930 008,009 880 855 830 800 775 750 725 700 675 650 620 012 900 875 855 835 815 795 775 755 735 715 690 014 890 875 855 835 820 800 785 765 750 730 710 *Approximate fan rpm shown. 30
31 | DURABLADE ECONOMIZER BAROMETRIC RELIEF DAMPER CHARACTERISTICS — 50TFF007 DURABLADE ECONOMIZER BAROMETRIC RELIEF DAMPER CHARACTERISTICS — 50TFF008-014 31
32 | Performance data (cont) 32 )mfc( WOLF ECONOMI$ER POWER EXHAUST PERFORMANCE (50TFF007) 2500 2000 2 FANS 1500 OPERATING 1000 1 FAN OPERATING 500 0 0 0.1 0.2 0.3 0.4 0.5 STATIC PRESSURE (in. wg) ECONOMI$ER POWER EXHAUST PERFORMANCE (50TFF008-014) 5000 4000 3000 2000 1000 0 0 0.1 0.2 0.3 0.4 0.5 STATIC PRESSURE (in. wg) )mfc( WOLF 2 FANS OPERATING 1 FAN OPERATING ECONOMI$ER OUTDOOR-AIR LEAKAGE 50 40 30 20 10 0 0 0.25 0.5 0.75 1 )MFC( WOLF 0.25 0.20 0.15 0.10 0.05 0.00 0 500 1000 1500 2000 FLOW (CFM) SIZE 007 STATIC PRESSURE (in. wg) SIZES 008-014 )gw .ni( ERUSSERP CITATS SIZE 007 SIZES 008-014 ECONOMI$ER RETURN-AIR PRESSURE DROP 0.25 0.20 0.15 0.10 0.05 0.00 1200 2000 2800 3600 4400 FLOW (CFM) )gw .ni( ERUSSERP CITATS ECONOMI$ER BAROMETRIC FLOW 0.35 0.30 SIZE 007 SIZES 008-014
33 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 L/s COMPONENT 700 800 900 1000 1100 1200 1 Heater Module 20 22 25 27 30 32 2 Heater Modules 41 42 42 43 44 45 Durablade Economizer 12 12 12 12 12 12 EconoMi$er 32 40 50 63 77 — ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF008-014 L/s COMPONENT 800 900 1000 1100 1200 1300 1400 1500 1600 1700 1800 1900 2000 2100 2200 2300 2400 1 Heater Module 1 2 4 6 8 10 12 14 16 18 19 21 23 25 27 29 31 2 Heater Modules 5 7 9 10 12 15 17 20 22 25 27 29 32 34 37 39 40 Durablade Economizer 2 3 4 5 6 7 8 9 10 11 12 13 14 15 16 17 18 EconoMi$er — — — — — — 31 35 41 50 59 67 75 84 90 97 105 ACCESSORY/FIOP STATIC PRESSURE DROP (in. wg) — 50TFF007 Cfm COMPONENT 1500 1600 1800 2000 2200 2400 2500 1 Heater Module 0.09 0.09 0.10 0.11 0.11 0.12 0.13 2 Heater Modules 0.16 0.16 0.17 0.17 0.17 0.18 0.18 Durablade Economizer 0.05 0.05 0.05 0.05 0.05 0.05 0.05 EconoMi$er 0.13 0.15 0.19 0.24 0.29 0.35 — ACCESSORY/FIOP STATIC PRESSURE DROP (in. wg) — 50TFF008-014 Cfm COMPONENT 1900 2200 2500 3000 3500 4000 4500 5000 5500 1 Heater Module 0.01 0.02 0.03 0.05 0.07 0.08 0.10 0.12 0.14 2 Heater Modules 0.02 0.03 0.05 0.07 0.09 0.12 0.14 0.16 0.19 Durablade Economizer 0.02 0.02 0.02 0.03 0.04 0.05 0.06 0.07 0.08 EconoMi$er — — — 0.125 0.18 0.27 0.34 0.40 — ELECTRIC HEATING CAPACITIES — 50TFF007-014 UNIT UNIT ELECTRICAL ACCESSORY PART NO. 50TFF CHARACTERISTICS kW 50DJ90– 4.2 0921 8.0 0941 007 400-3-50 9.7 0951 16.0* 0941 17.7* 0941, 0951 9.7 1681 11.5 1631 008 400-3-50 19.3 1641 22.9 1651 29.0* 1681, 1641 9.7 1681 11.5 1631 009 400-3-50 19.3 1641 22.9 1651 29.0* 1681, 1641 9.7† 1681 11.5** 1631 012, 19.3 1641 400-3-50 014 22.9 1651 29.0 1681, 1641 34.7* 1631, 1651 *Two heater packages are required to provide kW indicated. †Available on 012 size units only. **Available on 014 size units only. NOTE: The kW ratings shown above are at 400 v. 33
34 | Electrical data 50TFF007-014 VOLTAGE COMPR OFM MINIMUM UNIT UNIT NOMINAL RANGE (ea) (ea) IFM ELECTRIC HEAT* POWER SUPPLY DISCONNECT VOLTAGE 50TFF (50 Hz) Min Max RLA LRA FLA FLA Nominal FLA MCA MOCP** FLA LRA kW† — — 18.4 25 18 4.2 7.2 18.4 25 18 400 8.0 13.8 18.4 25 18 007 360 440 9.9 72.0 0.6 2.6 109 (3 phase) 9.7 16.8 20.8 25 19 16.0 27.8 32.1 35 30 17.7 30.7 34.6 35 32 — — 23.8 30 25 9.7 13.9 23.8 30 25 400 11.5 16.5 23.9 25 25 008 360 440 8.9 42.0 0.6 2.6 103 (3 phase) 19.3 27.8 38.1 40 35 22.9 33.1 44.6 45 41 29.0 41.8 55.5 60 51 — — 22.5 25 23 9.7 13.9 22.5 25 23 400 11.5 16.5 23.9 25 23 009 360 440 8.3 69.0 0.6 2.6 162 (3 phase) 19.3 27.8 38.1 40 35 22.9 33.1 44.6 45 41 29.0 41.8 55.5 60 51 — — 23.8 30 25 9.7 16.5 23.9 30 25 400 19.3 27.8 38.1 40 35 012 360 440 8.9 64.0 0.6 2.6 152 (3 phase) 22.9 33.1 44.6 45 41 29.0 41.8 55.5 60 51 34.7 50.1 65.9 70†† 61 — — 29.4 35 31 11.5 16.5 29.4 35 31 400 19.3 27.8 40.8 45 38 014 360 440 10.4 73.0 0.6 4.8 192 (3 phase) 22.9 33.1 47.3 50 44 29.0 41.8 58.2 60 54 34.7 50.1 68.6 70†† 63 LEGEND EXAMPLE: Supply voltage is 400-3-50. FLA — Full Load Amps AB = 393 v HACR — Heating, Air Conditioning and Refrigeration BC = 403 v IFM — Indoor (Evaporator) Fan Motor AC = 396 v LRA — Locked Rotor Amps MCA — Minimum Circuit Amps 393 + 403 + 396 MOCP — Maximum Overcurrent Protection Average Voltage = 3 NEC — National Electrical Code (U.S.A.) OFM — Outdoor (Condenser) Fan Motor RLA — Rated Load Amps 1192 = 3 *Heater capacity (kW) is based on heater voltage of 400 v. If power distribution voltage to unit varies from rated heater voltage, heater = 397 kW will vary accordingly. †Heaters are field installed only. Determine maximum deviation from average voltage: **Fuse or HACR circuit breaker. (AB) 397 – 393 = 4 v ††Fusing in single point box provides the required branch circuit (BC) 403 – 397 = 6 v protection. (AC) 397 – 396 = 1 v NOTES: Maximum deviation is 6 v. 1. In compliance with NEC requirements (U.S.A. Standard) for multimo- Determine percent voltage imbalance. tor and combination load equipment (refer to NEC Articles 430 and 440), the overcurrent protective device for the unit shall be fuse or 393 + 403 + 396 HACR breaker. Average Voltage = 2. Unbalanced 3-Phase Supply Voltage 3 Never operate a motor where a phase imbalance in supply voltage is This amount of phase imbalance is satisfactory as it is below the maxi- greater than 2%. Use the following formula to determine the percent mum allowable 2%. of voltage imbalance. % Voltage imbalance IMPORTANT: If the supply voltage phase imbalance is more than 2%, contact your local electric utility company immediately. max voltage deviation from average voltage = 100 x average voltage 34
35 | Typical piping and wiring — 50TFF007-014 (sizes 008-014 shown) VERTICAL DISCHARGE DUCTING TOOL-LESS FILTER ACCESS DOOR CONDENSER-FAN DISCHARGE AIR HORIZONTAL DISCHARGE DUCTING LEGEND NEC — National Electrical Code (U.S.A. Standard) 35
36 | Typical wiring schematic (50TFF008-014 shown) 36
37 | LEGEND AHA — Adjustable Heat Anticipator SEN — Sensor AWG — American Wire Gage SW1 — Switch Fully Open C — Contactor, Compressor SW2 — Switch Fully Closed CAP — Capacitor SW3 — Switch Min Vent Position CB — Circuit Breaker SW4 — Switch Max Vent Position CC — Cooling Compensator TB — Terminal Block COMP — Compressor Motor TC — Thermostat-Cooling D — Diode TH — Thermostat-Heating EC — Enthalpy Control TRAN — Transformer ECON — Economizer Field Splice EPS — Emergency Power Supply EQUIP — Equipment Marked Wire ER — Economizer Relay FPT — Freeze-Up Protection Thermostat Terminal (Marked) FU — Fuse GND — Ground Terminal (Unmarked) HC — Heater Contactor (Strip Heat) Terminal Block HPS — High-Pressure Switch IFC — Indoor-Fan Contactor Splice IFM — Indoor-Fan Motor IFMOVL — Indoor-Fan Motor Overload Splice (Marked) IFR — Indoor-Fan Relay LPS — Low-Pressure Switch Factory Wiring LSM — Limit Switch (Manual Reset) Field Control Wiring MTR — Motor OAT — Outdoor-Air Thermostat Field Power Wiring OFC — Outdoor-Fan Contactor OFM — Outdoor-Fan Motor Accessory or Optional Wiring P — Plug To indicate common potential only. PL — Plug Assembly Not to represent wiring. QT — Quadruple Terminal R — Relay SAT — Supply-Air Thermostat NOTES 1. If any of the original wire furnished must be replaced, it must be replaced with type 90 C wire or its equivalent. 2. Three-phase motors are protected under primary single-phasing conditions. 3. Thermostat: HH07AT170, 172, 174 and P272-2783 Subbase: HH93AZ176, 178 and P272-1882, 1883 4. Set heat anticipator at 1 amp. 5. Use copper conductors only. 6. Use copper, copper-clad aluminum or aluminum conductors. 37
38 | Controls Operating sequence the damper modulates to the fully closed position when the IFM is deenergized. Cooling, units without economizer — When thermo- stat calls for cooling, terminals G and Y1 are energized. When the OAT is below the ECON SP setting and the The indoor (evaporator) fan contactor (IFC), and compres- room thermostat calls for Stage 1 cooling (R to G + Y1), sor contactor no. 1 (C1) are energized and evaporator-fan the EconoMi$er modulates to the minimum position when motor, compressor no. 1 and condenser fans start. The the IFM is energized. The EconoMi$er provides Stage 1 of liquid line solenoid valve for compressor no. 1 is deener- cooling by modulating the return and outdoor-air dampers gized to open. The condenser-fan motor runs continuously to maintain a 12.8 C (55 F) supply air set point. If the while unit is cooling. On 50TFF008-014 units, if the ther- supply-air temperature (SAT) is greater than 13.9 C (57 F), mostat calls for a second stage of cooling by energizing Y2, the EconoMi$er modulates open, allowing a greater compressor contactor no. 2 (C2) is energized and com- amount of outdoor air to enter the unit. If the SAT drops pressor no. 2 starts. below 11.7 C (53 F), the outdoor air damper modulates closed to reduce the amount of outdoor air. When the SAT Heating, units without economizer (If Accessory is between 11.1 and 13.9 C (53 and 57 F), the Heater is Installed) — Upon a call for heating through EconoMi$er maintains its position. terminal W1, IFC and heater contactor no. 1 (HC1) are energized. On units equipped for 2 stages of heat, when If outdoor-air alone cannot satisfy the cooling require- additional heat is needed, HC2 is energized through W2. ments of the conditioned space, and the OAT is above the MECH CLG LOCKOUT set point, the EconoMi$er inte- Cooling, units with Durablade economizer — When grates free cooling with mechanical cooling. This is accom- the outdoor-air temperature is above the outdoor-air ther- plished by the strategies below. mostat (OAT) setting and the room thermostat calls for cooling, compressor contactor no. 1 is energized to start NOTE: Compressor has a 2-minute Minimum On, Mini- compressor no. 1 and the condenser-fan motor. The mum Off, and Interstage delay timer. evaporator-fan motor is energized and the economizer 1. If Y1 is energized, and the room thermostat calls for damper moves to the minimum position. Upon a further Y2 (2-stage thermostat), the compressor and OFM call for cooling, compressor contactor no. 2 will be ener- are energized. The EconoMi$er damper is main- gized (50TFF008-014), starting compressor no. 2. After tained at its current position. the thermostat is satisfied, the damper moves to the fully 2. If Y1 is energized for more than 20 minutes, and Y2 closed position. is not energized (whether or not a 2-stage thermostat When the outdoor-air temperature is below the OAT set- is used), the compressor and OFM are energized. ting and the thermostat calls for cooling, the economizer The EconoMi$er damper is maintained at its current dampers move to the minimum position. If the supply-air position. temperature is above 13.9 C (57 F), the damper continues 3. If Y1 is energized, and the compressor is already to open until it reaches the fully open position or until the energized (see Step 2) and the room thermostat calls supply-air temperature drops below 13.9 C (57 F). for Y2, the compressor continues to operate. When the supply-air temperature falls to between 4. If compressor is energized and the thermostat is satis- 13.9 C (57 F) and 11.1 C (52 F), the damper will remain at fied, the compressor, the OFM, and IFM are deener- an intermediate open position. If the supply-air tempera- gized and the EconoMi$er modulates closed. ture falls below 11.1 C (52 F), the damper will modulate closed until it reaches the minimum position or until the When the OAT is below the MECH CLG LOCKOUT set supply-air temperature is above 11.1 C (52 F). When the point, the compressors remain off. thermostat is satisfied, the damper will move to the fully Cooling, units with EconoMi$er (50TFF008-014) closed position. — When the outdoor-air temperature (OAT) is above the If the outdoor air alone cannot satisfy the cooling ECON SP set point and the room thermostat calls for requirements of the conditioned space, economizer cool- Stage 1 cooling (R to G + Y1), the indoor (evaporator) fan ing is integrated with mechanical cooling, providing motor (IFM) is energized and the EconoMi$er damper second-stage cooling. Compressor no. 1 and the modulates to minimum position. The compressor contac- condenser fan will be energized and the position of the tor is energized to start the compressor and outdoor (con- economizer damper will be determined by the supply-air denser) fan motor (OFM). After the thermostat is satisfied, temperature. Compressor no. 2 (50TFF008-014) is locked the damper modulates to the fully closed position when the out. IFM is deenergized. When the second stage of cooling is satisfied, the com- When the OAT is below the ECON SP setting and the pressor and condenser-fan motor will be deenergized. room thermostat calls for Stage 1 cooling (R to G + Y1), The damper position will be determined by the supply-air the EconoMi$er modulates to the minimum position when temperature. the IFM is energized. The EconoMi$er provides Stage 1 of cooling by modulating the return and outdoor-air dampers When the first stage of cooling is satisfied, the damper to maintain a (12.8 C) 55 F supply air set point. If the sup- will move to fully closed position. ply-air temperature (SAT) is greater than 13.9 C (57 F), the Cooling, units with EconoMi$er (50TFF007) — EconoMi$er modulates open, allowing a greater amount of When the outdoor-air temperature (OAT) is above the outdoor air to enter the unit. If the SAT drops below ECON SP set point and the room thermostat calls for 11.7 C (53 F), the outdoor air damper modulates closed to Stage 1 cooling (R to G + Y1), the indoor (evaporator) fan reduce the amount of outdoor air. When the SAT is be- motor (IFM) is energized and the EconoMi$er damper tween 11.7 and 13.9 C (53 and 57 F), the EconoMi$er modulates to minimum position. The compressor contac- maintains its position. tor is energized to start the compressor and outdoor (con- denser) fan motor (OFM). After the thermostat is satisfied, 38
39 | If outdoor-air alone cannot satisfy the cooling require- When the OAT is below the MECH CLG LOCKOUT set ments of the conditioned space, and the OAT is above the point, the compressors remain off. MECH CLG LOCKOUT set point, the EconoMi$er inte- Heating, units with economizer (If Accessory grates free cooling with mechanical cooling. This is accom- Heater is Installed) — When the room thermostat calls plished by the strategies below. for heat through terminal W1, the evaporator-fan contac- NOTE: Compressors have a 2-minute Minimum On, Mini- tor and heater contactor no. 1 are energized. On units mum Off, and Interstage delay timer. equipped for 2 stages of heat, when additional heat is needed, heater contactor no. 2 is energized through W2. 1. If Y1 is energized, and the room thermostat calls for The economizer damper moves to the minimum position Y2 (2-stage thermostat), compressor no. 1 and OFM during heating. When the thermostat is satisfied, the are energized. The EconoMi$er damper is main- damper moves to the fully closed position. tained at its current position. 2. If Y1 is energized for more than 20 minutes, and Y2 TEMP systems is not energized (whether or not a 2-stage thermostat A TEMP System is a network of communicating Carrier is used), compressor no. 1 and OFM are energized. TEMP System Thermostats and rooftop, factory-mounted The EconoMi$er damper is maintained at its current Apollo direct digital controls, each serving its own zone position. and heating/cooling unit. Networking allows your building 3. If Y1 is energized, and compressor no. 1 is already manager to easily access each of your systems from a sin- energized (see Step 2) and the room thermostat calls gle location...whether they are in the same building or for Y2, compressor no. 1 continues to operate. If Y2 located throughout town. remains energized for more than 20 minutes, com- The TEMP System’s inherently flexible, modular base pressor no. 2 is energized. design supports the exact number of independent, single NOTE: Compressor no. 2 cannot be energized unless zone systems you require...no more, no less, no compro- there is a signal for Y2 from the space thermostat. mises. 4. If compressor no. 2 is energized, and the Y2 signal Ideal for department stores, small office buildings, fast from the thermostat is satisfied, compressor no. 1 food chains, schools and hotels, a TEMP System is a and 2 are deenergized. Reasserting Y2 will start com- cost-effective way to maintain comfortable building pressor no. 1 and (after a 20-minute interstage delay) environments. compressor 2. 5. If compressor no. 1 is energized and the thermostat is satisfied, compressor no. 1, the OFM, and IFM are deenergized and the EconoMi$er modulates closed. TEMP SYSTEM THERMOSTAT (WITH TIMECLOCK) TEMP SYSTEM THERMOSTAT (WITHOUT TIMECLOCK) 39
40 | Controls (cont) Variable Volume/Variable Temperature Through the use of communicating electronic controls, (VVT®) Systems VVT Systems are able to provide the comfort of a multiple zone system while using the installation, operating and VVT Systems are dedicated to total building comfort. Car- maintenance economics of single zone equipment...virtu- rier thermostats, zone dampers, and HVAC equipment ally putting an end to the cost vs comfort compromise. with factory-mounted direct digital controls continually monitor and adjust their operation to ensure uninterrupted and personalized comfort for all occupants. 40
41 | Application data Outdoor installation — Units approved for outdoor Heating-to-cooling changeover — All units are auto- installation only. matic changeover from heating to cooling when automatic changeover thermostat and subbase are used. Ductwork — Secure vertical discharge ductwork to roof curb. For horizontal discharge applications, either attach Airflow — Units are draw-thru on cooling and blow-thru ductwork to unit, or use field-supplied flanges attached to on heating. the horizontal discharge openings and attach all ductwork Maximum airflow — To minimize the possibility of con- to flanges. densate blow-off from evaporator, airflow through units Horizontal discharge — To convert from vertical dis- should not exceed 67 L/s per kW (500 cfm/ton). charge to horizontal discharge: Minimum airflow — For cooling minimum airflow is 1. Remove economizer or two-position damper to gain 40 L/s per kW (300 cfm/ton). For 50TFF007-014 units access to return duct opening. with electric heating, required minimum L/s (cfm) is 849 (1800) for 50TFF007; 1062 (2250) for 50TFF008; 1203 2. Move the horizontal-discharge duct opening covers to (2550) for 50TFF009; and 1416 (3000) for 50TFF012 the vertical discharge openings. and 014. 3. Rotate economizer or two-position damper Minimum ambient cooling operating temperature 90 degrees. — The minimum temperature for standard units is –4 C 4. Rotate the barometric relief damper 90 degrees. (25 F). With accessory Motormaster® II control, units can operate at outdoor temperatures down to –17.8 C (0° F). 5. Install block-off plate over the opening on the access Internal unit design — Due to Carrier’s internal unit panel. design (draw-thru over the motor), air path, and specially Thru-the-curb service connections — Roof curb con- designed motors, the full kW horsepower (maximum con- nections allow field power wires and control wires to enter tinuous bkW and bhp) listed in the Physical Data tables and through the roof curb opening. the notes following each Fan Performance table can be uti- Thru-the-bottom service connections — Power con- lized with confidence. nections made through the bottom of the unit must utilize Using Carrier motors with the values listed in the Physi- an accessory Carrier roof curb and accessory thru-the-bot- cal and Fan Performance Data tables will not result in nui- tom power connection accessory kit. sance tripping or premature motor failure. The unit Thermostat — Use of 2-stage heating and cooling ther- warranty will not be affected. mostat is recommended for all units. A 2-stage cooling Apollo direct digital controls — The Apollo direct digi- thermostat is required on units with accessory economizer tal controls must be used with either a Carrier master or to provide integrated cooling. monitor thermostat. 41
42 | Guide specifications Packaged Rooftop Cooling Unit with material, providing a minimum 19 mm (3/ -in.) 4 Electric Heat Option — Constant Volume connection with both vertical and horizontal drains and shall comply with ASHRAE 62. Application 6. Unit shall have factory-installed filter access HVAC Guide Specifications panel to provide filter access with tool-less removal. Size Range: 17.6 to 35.9 kW (5.0 to 10.2 Tons) Nominal Cooling 7. Unit shall have standard thru-the-bottom power connection capability. Carrier Model Number: 50TFF C. Fans: Part 1 — General 1. Indoor blower (evaporator fan) shall be belt- 1.01 SYSTEM DESCRIPTION driven, double inlet, forward-curved centrifugal Outdoor rooftop- or slab-mounted, electrically con- type. Belt drive shall include an adjustable-pitch trolled cooling unit with optional heat utilizing a her- motor pulley. metic compressor for cooling duty and electric 2. Indoor blower (evaporator-fan) shall be made resistance coils for heating duty. Unit shall discharge from steel with a corrosion-resistant finish and supply air vertically or horizontally as shown on con- shall be dynamically balanced. tract drawings. 3. Bearings shall be of the sealed, permanently 1.02 QUALITY ASSURANCE lubricated, ball-bearing type for longer life and A. Unit shall be rated in accordance with ARI Standards lower maintenance. 210/240 or 360 and 270 (U.S.A.). 4. Condenser fan shall be of the direct-driven pro- B. Unit shall be designed to conform to ASHRAE 15, peller type and shall discharge air vertically. latest revision, and in accordance with UL 1995. 5. Condenser fan shall have aluminum blades riv- (U.S.A. Standards). eted to corrosion-resistant steel spiders and shall C. Roof curb shall be designed to conform to NRCA be dynamically balanced. Standards (U.S.A.). D. Compressor(s): D. Insulation and adhesive shall meet NFPA 90A 1. Reciprocating or scroll type fully hermetic type, requirements (U.S.A. Standard) for flame spread and internally protected. smoke generation. 2. Factory rubber-mounted and internally spring E. Unit casing shall be capable of withstanding Federal mounted for vibration isolation. test method (U.S.A. Standard) Standard ASTM B117 500-hour salt spray test. 3. On independent mounting circuits (008-014). F. Units shall be designed in accordance with ISO 9001, E. Coils: and shall be manufactured in a facility registered to 1. Condenser coils shall have aluminum plate fins ISO 9002/BS5750, Part 2. mechanically bonded to enhanced copper tubes 1.03 DELIVERY, STORAGE, AND HANDLING with all joints brazed. Unit(s) shall be stored and handled per manufacturer’s 2. Tube sheet openings shall be belled to prevent recommendations. tube wear. Part 2 — Products 3. Evaporator coil shall be of the full face active design. 2.01 EQUIPMENT (STANDARD) F. Refrigerant Components: A. General: Refrigerant circuit components shall include: Factory-assembled, single-piece cooling unit with optional heat. Contained within the unit enclosure 1. Refrigerant feed system. shall be all factory wiring, piping, controls, refrigerant 2. Refrigerant filter drier. charge (R-22), and special features required prior to 3. Service gage connections on suction, discharge, field start-up. and liquid line. B. Unit Cabinet: G. Filter Section: 1. Unit cabinet shall be constructed of galvanized 1. Standard filter section shall consist of factory- steel, bonderized and coated with a baked installed low-velocity, throwaway 51 mm (2-in.) enamel finish on all externally exposed surfaces. thick fiberglass filters of commercially available 2. Evaporator fan cabinet interior shall be insulated sizes. with a minimum 13 mm (1/ -in.) thick 1 lb den- 2 2. Filter face velocity shall not exceed 1.64 m/s sity neoprene coated, flexible fiberglass insula- (320 fpm) at nominal airflows. tion coated on the air side. 3. Filter section shall use only one size filter. 3. Cabinet panels shall be easily removable for 4. Filters shall be accessible through an access servicing. panel with ‘‘no-tool’’ removal. 4. Holes shall be provided in the base rails for rig- H. Controls and Safeties: ging shackles to facilitate overhead rigging, and forklift slots shall be provided to facilitate 1. Unit Controls: maneuvering. Unit shall be complete with self-contained low- 5. Unit shall have a factory-installed, sloped con- voltage control circuit. densate drain pan made of a non-corrosive 42
43 | 2. Standard Safeties: * 3. Integrated Economizer: a. Unit shall incorporate compressor over- a. Integrated integral-modulating type capable temperature and overcurrent safety devices to of simultaneous economizer and compressor shut off compressor. operation. b. Heating section shall be provided with the fol- b. Includes all hardware and controls to provide lowing minimum protections: cooling with outdoor air. 1) High-temperature limit switches. c. Equipped with low-leakage dampers not to 2) Overcurrent protection. exceed 3% leakage, at 249 Pa (1 in. wg) pres- sure differential (Durablade economizer). 3. Refrigerant Controls: d. Capable of introducing up to 100% outdoor Shall contain high-pressure, loss-of-charge/ air in both minimum and fully open positions. low-pressure, and freeze protection switches. e. Equipped with a gravity relief sliding plate damper (Durablade economizer). Damper I. Operating Characteristics: shall close upon unit shutoff. 1. Unit shall be capable of starting and running at f. EconoMi$er shall be equipped with a baro- 46.1 C (115 F) ambient outdoor temperature, metric relief damper with up to 100% of meeting maximum load criteria of ARI Standard return air (007) or 90% of return air (008- 210/240 or 360 (U.S.A. Standard) at ± 10% 014) relief. Durablade economizer is voltage. equipped with 30% of return-air relief. 2. Compressor with standard controls shall be g. Designed to close damper during loss-of- capable of operation down to –4 C (25 F) ambi- power situations with emergency power sup- ent outdoor temperature. ply (Durablade economizer) or spring return J. Electrical Requirements: built into motor (EconoMi$er). All unit power wiring shall enter unit cabinet at a sin- h. Dry bulb outdoor-air thermostat (Durablade gle factory-predrilled location. economizer) shall be provided as standard. K. Motors: Enthalpy control shall be provided as an option. 1. Compressor motors shall be cooled by refriger- ant passing through motor windings and shall i. Durablade economizer is a guillotine-style have line break thermal and current overload damper and EconoMi$er is a parallel-blade protection. design. 2. Indoor blower (evaporator-fan) motor shall have NOTE: EconoMi$er shall also be available permanently lubricated bearings and inherent with field-installed power exhaust accessory. automatic-reset thermal overload protection. * 4. Manual Outdoor-Air Damper: 3. Totally enclosed condenser-fan motor shall have Manual damper package shall consist of permanently lubricated bearings, and inherent damper, birdscreen, and rainhood which can be automatic-reset thermal overload protection. preset to admit up to 50% outdoor air for year- L. Special Features: round ventilation. Certain features are not applicable when the features * 5. 100% Open Two-Position Damper: designated by * are specified. For assistance in a. Two-position damper package shall include amending the specifications, your local Carrier Sales single blade damper and motor. Admits up to Office should be contacted. 100% outdoor air. * 1. Direct Digital Controls: b. Damper shall close upon indoor (evaporator) a. Shall be available as a factory-installed option. fan shutoff. b. Shall actively monitor all modes of operation, c. Designed to close damper during loss of as well as evaporator-fan status, filter status, power situations. indoor-air quality, supply-air temperature, and d. Equipped with barometric relief damper. outdoor-air temperature. * 6. 25% Open Two-Position Damper: c. Shall work with Carrier TEMP and VVT® systems. a. Two-position damper package shall include single blade damper and motor. Admits up to d. Shall have built-in diagnostics for thermostat 25% open outdoor air. commands for both staged heating and cool- ing, evaporator-fan operation, and econo- b. Damper shall close upon indoor (evaporator) mizer operation. fan shutoff. e. Shall be equipped with a 5-minute time delay c. Designed to close damper during loss of between modes of operation. power situations. 2. Roof Curbs: (Horizontal and Vertical) d. Equipped with barometric relief damper. a. Formed galvanized steel with wood nailer * 7. Solid-State Enthalpy Control: strip and capable of supporting entire unit a. For use with Durablade economizer weight. package. b. Allows for installing and securing ductwork to b. Capable of sensing outdoor-air enthalpy curb prior to mounting unit on the curb. content (temperature and humidity) and 43
44 | Guide specifications (cont) controlling economizer cut-in point to have with direct digital controls or with an indica- minimum heat content air passing over the tor light at the thermostat. evaporator coil for most efficient system 19. Unit-Mounted Disconnect Switch: operation. Shall be factory-installed. Internally mounted, * 8. Differential Enthalpy Sensor: non-fused switch provides unit power shutoff. a. For use with economizer only. Shall be accessible from outside the unit. b. Capable of comparing enthalpy content 20. Logo Kit: (temperature and humidity) of outdoor and Shall provide logo for field installation onto indoor air and controlling economizer cut- outdoor coil grille. in point at the most economical level. 21. EconoMi$er and Power Exhaust: * 9. Electric Resistance Heaters: Package shall provide control of internal a. Open wire nichrome elements with all nec- building pressure. The system shall exhaust essary safety operating controls. up to 100% of return air. b. UL (U.S.A. Standard) listed and indicated on basic unit informative plate. 22. Power Exhaust for Accessory EconoMi$er: c. Available in multiples to match heating Power exhaust shall be used in conjunction requirements. with EconoMi$er to provide the system with the capability to exhaust up to 100% of *10. Low-Ambient Operation (Head Pressure return air. The power exhaust is field- Control) Package: installed accessory. Consists of solid-state control and condenser- 23. Outdoor-Air Enthalpy Sensor: coil temperature sensor to operate at outdoor ambient temperatures down to –17.8 C (0° F) The outdoor-air enthlapy sensor shall be used with the EconoMi$er device to provide by condenser-fan cycling. single enthalpy control. When used in con- *11. Thermostat and Subbase: junction with a return air enthalpy sensor, Provides staged cooling and heating auto- the EconoMi$er device will provide different matic (or manual) changeover, fan control, enthalpy control. The sensor allows the and indicator light. EconoMi$er controller to determine if out- side air is suitable for free cooling. 12. Thru-The-Bottom Service Connectors: 24. Return-Air Enthalpy Sensor: Kit shall provide connectors to permit electri- cal connections to be brought to the unit The return-air enthalpy sensor shall be used through the basepan. with the EconoMi$er device. When used in conjunction with an outdoor air enthalpy *13. Electronic Programmable Thermostat: sensor, the EconoMi$er device will provide Capable of using deluxe full-featured elec- differential enthalpy control. tronic thermostat. Shall use built-in compres- 25. Return-Air Temperature Sensor: sor cycle delay control for both heating and The return-air temperature sensor shall be cooling duty. Capable of working with used with the EconoMi$er device. When Carrier direct digital controls. used in conjunction with the standard 14. Condenser Coil Hail Guard Assembly: outdoor air temperature sensor, the Hail guard shall protect against damage from EconoMi$er device will provide differential hail and flying debris. temperature control. 15. Condenser Coil Grille: 26. Indoor-Air Quality (CO 2 ) Sensor: The grille protects the condenser coil from a. Shall have the ability to provide demand damage by large objects without increasing ventilation indoor-air quality (IAQ) con- unit clearances. trol through the economizer with an IAQ sensor. 16. Compressor Cycle Delay: b. The IAQ sensor shall be available in duct Unit shall be prevented from restarting for a mount, wall mount, and wall mount with minimum of 5 minutes after shutdown. LED display. The set point shall have 17. Salt Spray Protection Package (008-014): adjustment capability. Coil guard protects coil from corrosion in coastal areas and in areas with high sulfur emissions. 18. Fan/Filter Status Switch: Provides status of indoor fan (ON/OFF) or filter (CLEAN/DIRTY). Status shall be dis- played over communication bus when used Carrier Corporation • Syracuse, New York 13221 9-00 Manufacturer reserves the right to discontinue, or change at any time, specifications or designs without notice and without incurring obligations. Book 1 4 New Book 1 Page 44 Catalog No. 005-003 Printed in U.S.A. F orm 5 0TFF-C1PD Tab 1b 6b Tab OP2b Replaces: New

## Extracted_Tables
source_page | table_no | page_title | row_no | column_no | cell_value
4 | 1 | Physical data (SI) | 1 | 1 | 7
4 | 1 | Physical data (SI) | 1 | 2 | 8
4 | 1 | Physical data (SI) | 1 | 3 | 9
4 | 1 | Physical data (SI) | 1 | 4 | 12
4 | 1 | Physical data (SI) | 2 | 1 | 17.6
4 | 1 | Physical data (SI) | 2 | 2 | 21.5
4 | 1 | Physical data (SI) | 2 | 3 | 24.3
4 | 1 | Physical data (SI) | 2 | 4 | 29.2
4 | 1 | Physical data (SI) | 3 | 1 | 213 245 15.4 21 52
4 | 1 | Physical data (SI) | 3 | 2 | 342 374 20.0 28 65
4 | 1 | Physical data (SI) | 3 | 3 | 345 376 20.0 28 65
4 | 1 | Physical data (SI) | 3 | 4 | 415 447 20.0 28 65
4 | 1 | Physical data (SI) | 4 | 1 | Scroll 1 1597
4 | 1 | Physical data (SI) | 4 | 2 | Reciprocating 2 2 2 1242 ea 1922 ea 1597 ea
4 | 1 | Physical data (SI) | 5 | 1 | 3.40 —
4 | 1 | Physical data (SI) | 5 | 2 | 2.18 2.21
4 | 1 | Physical data (SI) | 5 | 3 | R-22 3.12 4.16
4 | 1 | Physical data (SI) | 5 | 4 | 3.26 3.54
5 | 1 | Physical data (English) | 1 | 1 | 7
5 | 1 | Physical data (English) | 1 | 2 | 8
5 | 1 | Physical data (English) | 1 | 3 | 9
5 | 1 | Physical data (English) | 1 | 4 | 12
5 | 1 | Physical data (English) | 2 | 1 | 5
5 | 1 | Physical data (English) | 2 | 2 | 6.1
5 | 1 | Physical data (English) | 2 | 3 | 6.9
5 | 1 | Physical data (English) | 2 | 4 | 8.3
5 | 1 | Physical data (English) | 3 | 1 | 470 540 34 47 115
5 | 1 | Physical data (English) | 3 | 2 | 755 825 44 62 143
5 | 1 | Physical data (English) | 3 | 3 | 760 830 44 62 143
5 | 1 | Physical data (English) | 3 | 4 | 915 985 44 62 143
5 | 1 | Physical data (English) | 4 | 1 | Scroll 1 54
6 | 1 | Options and accessories | 1 | 1 | OPTION*
6 | 1 | Options and accessories | 2 | 1 | X
6 | 1 | Options and accessories | 3 | 1 | X
6 | 1 | Options and accessories | 4 | 1 | X
6 | 1 | Options and accessories | 7 | 1 | X
6 | 2 | Options and accessories | 1 | 1 | HEAD PRESSURE CONTROL The 50TFF007-014 standard units are designed to operate in cooling at outdoor temperatures down to –3.8 C (25 F). With accessory Motormas- ter control (condenser fan speed modulation) or Motormaster II control (condenser fan cycling) units can operate at outdoor temperatures down to –17.8 C (0° F). The head pressure controls, which mount in the con- denser section, control the condenser-fan motor to maintain correct con- Motormaster I Control densing temperature. Refer to product ordering or contact your local (007-014) Carrier representative for appropriate accessory combinations for desired outdoor ambient temperature operation. Motormaster II Control (007-014)
7 | 1 | ELECTRONIC PROGRAMMABLE THERMOSTAT THERMOSTAT | 1 | 1 | ELECTRONIC PROGRAMMABLE THERMOSTAT THERMOSTAT H C Zone thermostat (24 v) provides one- or 2-stage cooling for control of unit. Matching subbases are Carrier’s electronic programmable thermostat provides effi- available with or without tamperproof switches and cient temperature control by allowing you to program heating automatic changeover. and cooling setbacks and setups with provisions for weekends and holidays. Accessory remote sensing package is also avail- able to provide tamperproof control in high traffic spaces. Used in conjunction with factory-installed Apollo control, this thermo- TIME GUARD® II CONTROL stat provides a 5-minute recycle timer between modes of oper- Time Guard II control automatically prevents com- ation for short-cycle protection. pressor from restarting for at least 5 minutes after a shutdown. Accessory prevents short cycling of compressor if thermostat is changed rapidly. Time Guard II control mounts in the control compartment of unit. DURABLADE ECONOMIZER Exclusive Durablade economizer damper design saves energy while providing economical and reliable cooling. A sliding plate on the face of the economizer controls the amount of outdoor air entering the system. Closed, it pro- vides a leakproof seal which prevents ambient air from seep- ing in or conditioned air from seeping out. It can be adjusted easily for 100% outdoor air or any proportions of mixed air. Like the base unit, the economizer is converted easily for hor- izontal discharge applications.
8 | 1 | Options and accessories (cont) | 1 | 1 | ACCUSENSOR™ II FACTORY-INSTALLED APOLLO CONTROL COMMUNICATING CONTROLS ACCUSENSOR III SENSOR P OPEN T POSITION MINIMUM 3 1 S DOS C B TR RE A8 V 188 . 91 B P1 T1 4 2 5 OUTDOOR TEM F P.(cid:176) 05 55 06 5 0 6 7 57 08 Y 10 T30 I OPEN D 6 DAMPER 0 IM CLOSED 70 U DA MPER H 9 0 % A C D B CW–SETPOINTS–CCW R T A U C 2 S 4V H A 3 AT M m 1 IN A . 1 VDC C A O CT N T RAT R IN U G N S , : 3 . 1 5 . A 5A IN OR UNPOWERE AT D E ST CONTACTS SHOWN IN HIGH ENTHALPY 2 3 1 TR 1RT 24VAC LORTNOC YPLAHTNE + 58 RE V. 9 7- 3 6 7 2 The Apollo direct digital controls are designed exclusively by Carrier, and are used to actively monitor and control all modes of operation as well as to monitor evaporator-fan status, filter status, supply-air temperature, outdoor-air temperature, and indoor-air quality. They are designed to work in conjunction with Carrier Accusensor economizer controls help provide efficient, economical TEMP and VVT® system thermostats. economizer operation. Accusensor II solid-state enthalpy control includes the logic and one sensor to calculate both dry- and wet- bulb of the outdoor air to provide an accurate enthalpy reading on. It then decides when to energize the economizer based on this read- ELECTRIC HEATER ing. A second Accusensor III sensor compares outdoor temperature and humidity to return-air temperature and humidity and determines the most economical mixture of air (purchased in addition to first solid-state enthalpy sensor for differential enthalpy sensing). ECONOMI$ER ECONOMI$ER CONTROLLER GEAR-DRIVEN PLUG DAMPER ACTUATOR OUTDOOR AIR Electric heaters are available in a wide range TEMPERATURE of capacities for factory or field installation. SENSOR BAROMETRIC RELIEF DAMPERS Factory-installed EconoMi$er utilizes a microprocessor-based con- trol, gear drive damper system, low pressure drop characteristics, built-in spring return (for close upon power loss), and an integral barometric damper. NOTE: EconoMi$er is only available for vertical ductwork applica- tions and can be field or factory installed.
8 | 2 | Options and accessories (cont) | 1 | 1 | +
9 | 1 | Base unit dimensions — 50TFF007 | 1 | 1 | STD UNIT DURABLADE ECONOMI$ER (A) (B) WEIGHT ECONWEIGHT WEIGHT CORNER WEIGHT CORNER WEIGHT Lbs Kg Lbs Kg Lbs Kg Lbs Kg Lbs Kg
9 | 1 | Base unit dimensions — 50TFF007 | 2 | 1 | 7 470 213.2 34 15.4 47 21.3 148 67.1 103 46.7
9 | 2 | Base unit dimensions — 50TFF007 | 1 | 1 | 2. Center of gravity. 3. Direction of airflow. 4. On vertical discharge units, ductwork to be attached to accessory roof curb only. For horizontal dis- charge units field-supplied flanges should be attached to horizontal discharge openings, and all ductwork should be attached to the flanges. 5. Minimum clearance (local codes or jurisdiction may prevail): a. Between unit, flue side and combustible surfaces, 36 inches. b. Bottom of unit to combustible surfaces (when not using curb) 1 inch. Bottom of base rail to com- bustible surfaces (when not using curb) 0 inches. c. Condenser coil, for proper airflow, 36 in. one side, 12 in. the other. The side getting the greater clearance is optional. d. Overhead, 60 in. to assure proper condenser fan operation. e. Between units, control box side, 42 in. per NEC. f. Between unit and ungrounded surfaces, control box side, 36 in. per NEC. g. Between unit and block or concrete walls and other grounded surfaces, control box side, 42 in. per NEC. h. Horizontal supply and return end, 0 inches. 6. With the exception of the clearance for the condenser coil and combustion side as stated in Note 5a, b, and c, a removable fence or barricade requires no clearance. 7. Units may be installed on combustible floors made from wood or Class A, B, or C roof covering material if set on base rail. 8. The vertical center of gravity is 1¢-6† [457] up from the bottom of the base rail.
10 | 1 | Base unit dimensions — 50TFF008-014 | 1 | 2 | 1. Dimensions in [ ] are in millimeters. *Select either 3/4 † or 11/4 † for power, depending on wir 2. Center of gravity. size. 3. Direction of airflow. 4. Ductwork to be attached to accessory roof curb only. 5. Minimum clearance (local codes or jurisdiction may prevail): a. Bottom to combustible surfaces (when not using curb) 0 inches, on horizontal discharge units w electric heat 1 in. clearance to ductwork for 1 ft. b. Condenser coil, for proper airflow, 36 in. one side, 12 in. the other. The side getting the grea clearance is optional. c. Overhead, 60 in. to assure proper condenser fan operation. d. Between units, control box side, 42 in. per NEC (National Electrical Code). e. Between unit and ungrounded surfaces, control box side, 36 in. per NEC. f. Between unit and block or concrete walls and other grounded surfaces, control box side, 42 in. NEC. g. Horizontal supply and return end, 0 inches. 6. With the exception of the clearance for the condenser coil as stated in Notes 5a, b, and c, a remova fence or barricade requires no clearance. 7. Units may be installed on combustible floors made from wood or Class A, B, or C roof covering materi 8. The vertical center of gravity is 1¢-71/2 † [495] for 008 and 009, 2¢-0† [610] for 012 and 014 up from bottom of the base rail.
11 | 1 | Accessory dimensions | 1 | 1 | [19] NPT NPT NOTES: 6. Service clearance 4 ft on each side. 1. Roof curb accessory is shipped disassembled. 7. Direction of airflow. 2. Insulated panels. 8. Connector packages CRBTMPWR001A 3. Dimensions in [ ] are in millimeters. and 002A00 are for thru-the-curb conn 4. Roof curb: galvanized steel. tions. Packages CRBTMP003A00 a 5. Attach ductwork to curb (flanges of duct 004A00 are for thru-the-bottom connectio rest on curb).
11 | 1 | Accessory dimensions | 1 | 2 | NPT NPT
15 | 1 | Performance data | 1 | 1 | 700/0.05
15 | 1 | Performance data | 1 | 2 | 950/0.07
15 | 2 | Performance data | 1 | 2 | 13
15 | 2 | Performance data | 1 | 3 | 16
15 | 2 | Performance data | 1 | 4 | 19
15 | 2 | Performance data | 1 | 5 | 22
15 | 2 | Performance data | 1 | 6 | 13
15 | 2 | Performance data | 1 | 7 | 16
15 | 2 | Performance data | 1 | 8 | 19
15 | 2 | Performance data | 1 | 9 | 22
15 | 2 | Performance data | 1 | 10 | 13
15 | 2 | Performance data | 1 | 11 | 16
15 | 2 | Performance data | 1 | 12 | 19
15 | 2 | Performance data | 2 | 1 | TC SHC kW
15 | 2 | Performance data | 2 | 2 | 15.8 15.8 3.98
15 | 2 | Performance data | 2 | 3 | 17.7 15.5 4.11
15 | 2 | Performance data | 2 | 4 | 19.6 13.1 4.25
15 | 2 | Performance data | 2 | 5 | 21.5 10.4 4.39
15 | 2 | Performance data | 2 | 6 | 16.8 16.8 4.08
15 | 2 | Performance data | 2 | 7 | 18.7 18.1 4.21
15 | 2 | Performance data | 2 | 8 | 20.7 14.9 4.35
15 | 2 | Performance data | 2 | 9 | 22.6 11.6 4.49
15 | 2 | Performance data | 2 | 10 | 17.4 17.4 4.12
15 | 2 | Performance data | 2 | 11 | 19.3 19.3 4.27
15 | 2 | Performance data | 2 | 12 | 21.3 16.6 4.41
15 | 2 | Performance data | 3 | 1 | TC SHC kW
15 | 2 | Performance data | 3 | 2 | 15.2 15.2 4.26
15 | 2 | Performance data | 3 | 3 | 17.1 15.3 4.41
15 | 2 | Performance data | 3 | 4 | 19.0 12.8 4.56
15 | 2 | Performance data | 3 | 5 | 20.6 10.2 4.71
15 | 2 | Performance data | 3 | 6 | 16.2 16.2 4.38
15 | 2 | Performance data | 3 | 7 | 18.1 17.9 4.51
15 | 2 | Performance data | 3 | 8 | 20.1 14.7 4.66
15 | 2 | Performance data | 3 | 9 | 22.0 11.4 4.82
15 | 2 | Performance data | 3 | 10 | 17.0 17.0 4.43
15 | 2 | Performance data | 3 | 11 | 18.8 18.8 4.58
15 | 2 | Performance data | 3 | 12 | 20.7 16.4 4.73
15 | 2 | Performance data | 4 | 1 | TC SHC kW
15 | 2 | Performance data | 4 | 2 | 14.7 14.7 4.54
15 | 2 | Performance data | 4 | 3 | 16.5 15.0 4.70
15 | 2 | Performance data | 4 | 4 | 18.4 12.6 4.87
15 | 2 | Performance data | 4 | 5 | 20.3 10.0 5.04
15 | 2 | Performance data | 4 | 6 | 15.6 15.6 4.66
15 | 2 | Performance data | 4 | 7 | 17.5 17.5 4.82
15 | 2 | Performance data | 4 | 8 | 19.4 14.5 4.98
15 | 2 | Performance data | 4 | 9 | 21.3 11.2 5.15
15 | 2 | Performance data | 4 | 10 | 16.6 16.6 4.74
15 | 2 | Performance data | 4 | 11 | 18.2 18.2 4.89
15 | 2 | Performance data | 4 | 12 | 20.0 16.1 5.05
15 | 2 | Performance data | 5 | 1 | TC SHC kW
15 | 2 | Performance data | 5 | 2 | 14.1 14.1 4.81
15 | 2 | Performance data | 5 | 3 | 15.9 14.7 4.99
15 | 2 | Performance data | 5 | 4 | 17.8 12.3 5.17
15 | 2 | Performance data | 5 | 5 | 19.7 9.8 5.36
15 | 2 | Performance data | 5 | 6 | 15.0 15.0 4.92
15 | 2 | Performance data | 5 | 7 | 16.9 16.9 5.10
15 | 2 | Performance data | 5 | 8 | 18.8 14.3 5.29
15 | 2 | Performance data | 5 | 9 | 20.7 11.0 5.48
15 | 2 | Performance data | 5 | 10 | 16.2 16.2 5.05
15 | 2 | Performance data | 5 | 11 | 17.7 17.7 5.20
15 | 2 | Performance data | 5 | 12 | 19.4 15.8 5.37
15 | 2 | Performance data | 6 | 1 | TC SHC kW
15 | 2 | Performance data | 6 | 2 | 13.7 13.7 5.01
15 | 2 | Performance data | 6 | 3 | 15.5 14.5 5.20
15 | 2 | Performance data | 6 | 4 | 17.3 12.2 5.39
15 | 2 | Performance data | 6 | 5 | 19.3 9.6 5.60
15 | 2 | Performance data | 6 | 6 | 14.5 14.5 5.12
15 | 2 | Performance data | 6 | 7 | 16.4 16.4 5.31
15 | 2 | Performance data | 6 | 8 | 18.2 14.1 5.52
15 | 2 | Performance data | 6 | 9 | 20.2 10.9 5.73
15 | 2 | Performance data | 6 | 10 | 15.8 15.8 5.28
15 | 2 | Performance data | 6 | 11 | 17.3 17.3 5.61
15 | 2 | Performance data | 6 | 12 | 18.8 15.6 5.61
15 | 2 | Performance data | 7 | 1 | TC SHC kW
15 | 2 | Performance data | 7 | 2 | 12.7 12.7 5.33
15 | 2 | Performance data | 7 | 3 | 14.6 14.1 5.54
15 | 2 | Performance data | 7 | 4 | 16.5 11.8 5.76
15 | 2 | Performance data | 7 | 5 | 18.3 9.3 5.99
15 | 2 | Performance data | 7 | 6 | 14.0 14.0 5.46
15 | 2 | Performance data | 7 | 7 | 15.6 15.6 5.68
15 | 2 | Performance data | 7 | 8 | 17.3 13.7 5.90
15 | 2 | Performance data | 7 | 9 | 19.2 10.6 6.13
15 | 2 | Performance data | 7 | 10 | 15.4 15.4 5.68
15 | 2 | Performance data | 7 | 11 | 16.6 16.6 5.83
15 | 2 | Performance data | 7 | 12 | 17.9 15.2 5.99
15 | 2 | Performance data | 8 | 1 | TC SHC kW
15 | 2 | Performance data | 8 | 2 | 12.0 12.0 5.60
15 | 2 | Performance data | 8 | 3 | 13.8 13.8 5.82
15 | 2 | Performance data | 8 | 4 | 15.8 11.5 6.05
15 | 2 | Performance data | 8 | 5 | 17.6 9.1 6.29
15 | 2 | Performance data | 8 | 6 | 13.5 13.5 5.75
15 | 2 | Performance data | 8 | 7 | 15.1 15.1 5.97
15 | 2 | Performance data | 8 | 8 | 16.7 13.4 6.20
15 | 2 | Performance data | 8 | 9 | 18.5 10.3 6.45
15 | 2 | Performance data | 8 | 10 | 15.1 15.1 5.99
15 | 2 | Performance data | 8 | 11 | 16.1 16.1 6.14
15 | 2 | Performance data | 8 | 12 | 17.2 14.8 6.31
15 | 2 | Performance data | 9 | 1 | TC SHC kW
15 | 2 | Performance data | 9 | 2 | 11.2 11.2 5.85
15 | 2 | Performance data | 9 | 3 | 13.1 13.1 6.09
15 | 2 | Performance data | 9 | 4 | 15.1 11.2 6.34
15 | 2 | Performance data | 9 | 5 | 16.9 8.8 6.60
15 | 2 | Performance data | 9 | 6 | 13.0 13.0 6.04
15 | 2 | Performance data | 9 | 7 | 14.5 14.5 6.26
15 | 2 | Performance data | 9 | 8 | 15.9 13.1 6.50
15 | 2 | Performance data | 9 | 9 | 17.7 10.0 6.76
15 | 2 | Performance data | 9 | 10 | 14.8 14.8 6.31
15 | 2 | Performance data | 9 | 11 | 15.5 15.5 6.46
15 | 2 | Performance data | 9 | 12 | 16.5 14.4 6.61
15 | 2 | Performance data | 10 | 1 | TC SHC kW
15 | 2 | Performance data | 10 | 2 | 10.5 10.5 6.11
15 | 2 | Performance data | 10 | 3 | 12.4 12.4 6.36
15 | 2 | Performance data | 10 | 4 | 14.4 11.0 6.63
15 | 2 | Performance data | 10 | 5 | 16.2 8.6 6.91
15 | 2 | Performance data | 10 | 6 | 12.7 12.7 6.31
15 | 2 | Performance data | 10 | 7 | 13.9 13.9 6.56
15 | 2 | Performance data | 10 | 8 | 15.3 12.8 6.81
15 | 2 | Performance data | 10 | 9 | 16.9 9.8 7.08
15 | 2 | Performance data | 10 | 10 | 14.4 14.4 6.62
15 | 2 | Performance data | 10 | 11 | 15.0 15.0 6.77
15 | 2 | Performance data | 10 | 12 | 15.7 14.1 6.92
16 | 1 | Performance data (cont) | 1 | 2 | 14
16 | 1 | Performance data (cont) | 1 | 3 | 16
16 | 1 | Performance data (cont) | 1 | 4 | 18
16 | 1 | Performance data (cont) | 1 | 5 | 20
16 | 1 | Performance data (cont) | 1 | 6 | 22
16 | 1 | Performance data (cont) | 1 | 7 | 14
16 | 1 | Performance data (cont) | 1 | 8 | 16
16 | 1 | Performance data (cont) | 1 | 9 | 18
16 | 1 | Performance data (cont) | 1 | 10 | 20
16 | 1 | Performance data (cont) | 2 | 1 | TC SHC kW
16 | 1 | Performance data (cont) | 2 | 2 | 19.5 19.4 5.02
16 | 1 | Performance data (cont) | 2 | 3 | 20.9 18.0 5.16
16 | 1 | Performance data (cont) | 2 | 4 | 22.5 16.2 5.34
16 | 1 | Performance data (cont) | 2 | 5 | 24.3 14.3 5.54
16 | 1 | Performance data (cont) | 2 | 6 | 26.0 12.3 5.72
16 | 1 | Performance data (cont) | 2 | 7 | 21.6 21.4 5.28
16 | 1 | Performance data (cont) | 2 | 8 | 22.3 20.5 5.37
16 | 1 | Performance data (cont) | 2 | 9 | 23.7 18.5 5.52
16 | 1 | Performance data (cont) | 2 | 10 | 25.3 16.1 5.70
16 | 1 | Performance data (cont) | 3 | 1 | TC SHC kW
16 | 1 | Performance data (cont) | 3 | 2 | 19.1 18.9 5.25
16 | 1 | Performance data (cont) | 3 | 3 | 20.4 17.7 5.38
16 | 1 | Performance data (cont) | 3 | 4 | 21.9 16.0 5.56
16 | 1 | Performance data (cont) | 3 | 5 | 23.7 14.1 5.76
16 | 1 | Performance data (cont) | 3 | 6 | 25.4 12.1 5.96
16 | 1 | Performance data (cont) | 3 | 7 | 21.0 21.0 5.51
16 | 1 | Performance data (cont) | 3 | 8 | 21.7 20.2 5.58
16 | 1 | Performance data (cont) | 3 | 9 | 23.1 18.3 5.74
16 | 1 | Performance data (cont) | 3 | 10 | 24.7 15.9 5.92
16 | 1 | Performance data (cont) | 4 | 1 | TC SHC kW
16 | 1 | Performance data (cont) | 4 | 2 | 18.6 18.4 5.49
16 | 1 | Performance data (cont) | 4 | 3 | 19.8 17.3 5.61
16 | 1 | Performance data (cont) | 4 | 4 | 21.3 15.7 5.78
16 | 1 | Performance data (cont) | 4 | 5 | 23.0 13.9 5.98
16 | 1 | Performance data (cont) | 4 | 6 | 24.8 11.9 6.19
16 | 1 | Performance data (cont) | 4 | 7 | 20.5 20.5 5.74
16 | 1 | Performance data (cont) | 4 | 8 | 21.1 19.8 5.8
16 | 1 | Performance data (cont) | 4 | 9 | 22.4 18.0 5.96
16 | 1 | Performance data (cont) | 4 | 10 | 24.1 15.7 6.15
16 | 1 | Performance data (cont) | 5 | 1 | TC SHC kW
16 | 1 | Performance data (cont) | 5 | 2 | 18.0 17.8 5.77
16 | 1 | Performance data (cont) | 5 | 3 | 19.1 16.9 5.88
16 | 1 | Performance data (cont) | 5 | 4 | 20.6 15.4 6.04
16 | 1 | Performance data (cont) | 5 | 5 | 22.2 13.6 6.25
16 | 1 | Performance data (cont) | 5 | 6 | 23.9 11.6 6.47
16 | 1 | Performance data (cont) | 5 | 7 | 19.9 19.8 6.03
16 | 1 | Performance data (cont) | 5 | 8 | 20.3 19.4 6.07
16 | 1 | Performance data (cont) | 5 | 9 | 21.5 17.7 6.22
16 | 1 | Performance data (cont) | 5 | 10 | 23.2 15.4 6.43
16 | 1 | Performance data (cont) | 6 | 1 | TC SHC kW
16 | 1 | Performance data (cont) | 6 | 2 | 17.3 17.2 6.09
16 | 1 | Performance data (cont) | 6 | 3 | 18.2 16.4 6.18
16 | 1 | Performance data (cont) | 6 | 4 | 19.63 15.0 6.34
16 | 1 | Performance data (cont) | 6 | 5 | 21.3 13.2 6.55
16 | 1 | Performance data (cont) | 6 | 6 | 23.0 11.3 6.77
16 | 1 | Performance data (cont) | 6 | 7 | 18.2 19.1 6.33
16 | 1 | Performance data (cont) | 6 | 8 | 19.4 18.9 6.37
16 | 1 | Performance data (cont) | 6 | 9 | 20.6 17.3 6.61
16 | 1 | Performance data (cont) | 6 | 10 | 22.3 15.0 6.73
16 | 1 | Performance data (cont) | 7 | 1 | TC SHC kW
16 | 1 | Performance data (cont) | 7 | 2 | 16.6 16.6 6.40
16 | 1 | Performance data (cont) | 7 | 3 | 18.3 15.9 6.48
16 | 1 | Performance data (cont) | 7 | 4 | 18.7 14.6 6.63
16 | 1 | Performance data (cont) | 7 | 5 | 20.3 12.8 6.84
16 | 1 | Performance data (cont) | 7 | 6 | 22.0 10.9 7.07
16 | 1 | Performance data (cont) | 7 | 7 | 18.4 18.4 6.65
16 | 1 | Performance data (cont) | 7 | 8 | 18.6 18.3 6.67
16 | 1 | Performance data (cont) | 7 | 9 | 19.6 16.9 6.81
16 | 1 | Performance data (cont) | 7 | 10 | 21.3 14.7 7.02
16 | 1 | Performance data (cont) | 8 | 1 | TC SHC kW
16 | 1 | Performance data (cont) | 8 | 2 | 15.9 15.9 6.71
16 | 1 | Performance data (cont) | 8 | 3 | 16.4 15.4 6.77
16 | 1 | Performance data (cont) | 8 | 4 | 17.7 14.2 6.92
16 | 1 | Performance data (cont) | 8 | 5 | 19.4 12.5 7.13
16 | 1 | Performance data (cont) | 8 | 6 | 21.0 10.6 7.36
16 | 1 | Performance data (cont) | 8 | 7 | 17.7 17.7 6.97
16 | 1 | Performance data (cont) | 8 | 8 | 17.7 17.6 6.97
16 | 1 | Performance data (cont) | 8 | 9 | 18.7 16.4 7.10
16 | 1 | Performance data (cont) | 8 | 10 | 20.2 14.3 7.30
16 | 1 | Performance data (cont) | 9 | 1 | TC SHC kW
16 | 1 | Performance data (cont) | 9 | 2 | 15.2 15.2 7.02
16 | 1 | Performance data (cont) | 9 | 3 | 15.5 14.9 7.05
16 | 1 | Performance data (cont) | 9 | 4 | 16.7 13.8 7.20
16 | 1 | Performance data (cont) | 9 | 5 | 18.3 12.1 7.41
16 | 1 | Performance data (cont) | 9 | 6 | 19.9 10.2 7.64
16 | 1 | Performance data (cont) | 9 | 7 | 16.9 16.9 7.27
16 | 1 | Performance data (cont) | 9 | 8 | 16.9 16.9 7.27
16 | 1 | Performance data (cont) | 9 | 9 | 17.7 15.8 7.39
16 | 1 | Performance data (cont) | 9 | 10 | 19.1 13.9 7.57
16 | 1 | Performance data (cont) | 10 | 1 | TC SHC kW
16 | 1 | Performance data (cont) | 10 | 2 | 14.4 14.4 7.33
16 | 1 | Performance data (cont) | 10 | 3 | 14.5 14.3 7.33
16 | 1 | Performance data (cont) | 10 | 4 | 15.6 13.3 7.47
16 | 1 | Performance data (cont) | 10 | 5 | 17.3 11.7 7.67
16 | 1 | Performance data (cont) | 10 | 6 | 18.8 9.9 7.91
16 | 1 | Performance data (cont) | 10 | 7 | 16.1 16.1 7.56
16 | 1 | Performance data (cont) | 10 | 8 | 16.1 16.1 7.57
16 | 1 | Performance data (cont) | 10 | 9 | 16.8 15.2 7.67
16 | 1 | Performance data (cont) | 10 | 10 | 18.0 13.5 7.85
16 | 2 | Performance data (cont) | 1 | 2 | 14
16 | 2 | Performance data (cont) | 1 | 3 | 16
16 | 2 | Performance data (cont) | 1 | 4 | 18
16 | 2 | Performance data (cont) | 1 | 5 | 20
16 | 2 | Performance data (cont) | 1 | 6 | 22
16 | 2 | Performance data (cont) | 1 | 7 | 14
16 | 2 | Performance data (cont) | 1 | 8 | 16
16 | 2 | Performance data (cont) | 1 | 9 | 18
16 | 2 | Performance data (cont) | 1 | 10 | 20
16 | 2 | Performance data (cont) | 2 | 1 | TC SHC kW
16 | 2 | Performance data (cont) | 2 | 2 | 21.8 21.8 5.33
16 | 2 | Performance data (cont) | 2 | 3 | 22.5 20.9 5.41
16 | 2 | Performance data (cont) | 2 | 4 | 23.9 18.9 5.55
16 | 2 | Performance data (cont) | 2 | 5 | 25.5 16.4 5.73
16 | 2 | Performance data (cont) | 2 | 6 | 27.1 13.6 5.91
16 | 2 | Performance data (cont) | 2 | 7 | 22.9 22.8 5.49
16 | 2 | Performance data (cont) | 2 | 8 | 23.1 22.4 5.51
16 | 2 | Performance data (cont) | 2 | 9 | 24.3 20.5 5.65
16 | 2 | Performance data (cont) | 2 | 10 | 26.1 17.7 5.83
16 | 2 | Performance data (cont) | 3 | 1 | TC SHC kW
16 | 2 | Performance data (cont) | 3 | 2 | 21.3 21.2 5.55
16 | 2 | Performance data (cont) | 3 | 3 | 21.9 20.6 5.62
16 | 2 | Performance data (cont) | 3 | 4 | 23.3 18.7 5.77
16 | 2 | Performance data (cont) | 3 | 5 | 24.9 16.2 5.96
16 | 2 | Performance data (cont) | 3 | 6 | 26.5 13.5 6.14
16 | 2 | Performance data (cont) | 3 | 7 | 22.4 22.3 5.72
16 | 2 | Performance data (cont) | 3 | 8 | 22.5 22.0 5.73
16 | 2 | Performance data (cont) | 3 | 9 | 23.7 20.2 5.86
16 | 2 | Performance data (cont) | 3 | 10 | 25.4 17.5 6.05
16 | 2 | Performance data (cont) | 4 | 1 | TC SHC kW
16 | 2 | Performance data (cont) | 4 | 2 | 20.8 20.7 5.78
16 | 2 | Performance data (cont) | 4 | 3 | 21.2 20.2 5.84
16 | 2 | Performance data (cont) | 4 | 4 | 22.5 18.4 5.98
16 | 2 | Performance data (cont) | 4 | 5 | 24.2 16.0 6.17
16 | 2 | Performance data (cont) | 4 | 6 | 25.9 13.3 6.38
16 | 2 | Performance data (cont) | 4 | 7 | 21.8 21.8 5.94
16 | 2 | Performance data (cont) | 4 | 8 | 21.9 21.7 5.96
16 | 2 | Performance data (cont) | 4 | 9 | 23.1 20.0 6.08
16 | 2 | Performance data (cont) | 4 | 10 | 24.7 17.3 6.28
16 | 2 | Performance data (cont) | 5 | 1 | TC SHC kW
16 | 2 | Performance data (cont) | 5 | 2 | 20.2 20.2 6.07
16 | 2 | Performance data (cont) | 5 | 3 | 20.5 19.8 6.11
16 | 2 | Performance data (cont) | 5 | 4 | 21.7 18.1 6.25
16 | 2 | Performance data (cont) | 5 | 5 | 23.4 15.7 6.45
16 | 2 | Performance data (cont) | 5 | 6 | 25.2 13.0 6.66
16 | 2 | Performance data (cont) | 5 | 7 | 21.2 21.2 6.23
16 | 2 | Performance data (cont) | 5 | 8 | 21.2 21.0 6.23
16 | 2 | Performance data (cont) | 5 | 9 | 22.2 19.5 6.36
16 | 2 | Performance data (cont) | 5 | 10 | 23.8 17.0 6.54
16 | 2 | Performance data (cont) | 6 | 1 | TC SHC kW
16 | 2 | Performance data (cont) | 6 | 2 | 19.5 19.4 6.39
16 | 2 | Performance data (cont) | 6 | 3 | 19.6 19.2 6.41
16 | 2 | Performance data (cont) | 6 | 4 | 20.7 17.7 6.55
16 | 2 | Performance data (cont) | 6 | 5 | 22.4 15.3 6.75
16 | 2 | Performance data (cont) | 6 | 6 | 24.1 12.7 6.96
16 | 2 | Performance data (cont) | 6 | 7 | 20.4 20.4 6.54
16 | 2 | Performance data (cont) | 6 | 8 | 20.4 20.4 6.54
16 | 2 | Performance data (cont) | 6 | 9 | 20.7 19.0 6.66
16 | 2 | Performance data (cont) | 6 | 10 | 22.8 16.6 6.84
16 | 2 | Performance data (cont) | 7 | 1 | TC SHC kW
16 | 2 | Performance data (cont) | 7 | 2 | 18.7 18.7 6.69
16 | 2 | Performance data (cont) | 7 | 3 | 18.7 18.6 6.70
16 | 2 | Performance data (cont) | 7 | 4 | 19.8 17.2 6.83
16 | 2 | Performance data (cont) | 7 | 5 | 21.3 15.0 7.04
16 | 2 | Performance data (cont) | 7 | 6 | 23.1 12.4 7.26
16 | 2 | Performance data (cont) | 7 | 7 | 19.6 19.6 6.86
16 | 2 | Performance data (cont) | 7 | 8 | 19.6 19.6 6.86
16 | 2 | Performance data (cont) | 7 | 9 | 20.4 18.4 6.95
16 | 2 | Performance data (cont) | 7 | 10 | 21.7 16.3 7.12
16 | 2 | Performance data (cont) | 8 | 1 | TC SHC kW
16 | 2 | Performance data (cont) | 8 | 2 | 17.9 17.9 7.01
16 | 2 | Performance data (cont) | 8 | 3 | 17.9 17.9 7.01
16 | 2 | Performance data (cont) | 8 | 4 | 18.8 16.7 7.13
16 | 2 | Performance data (cont) | 8 | 5 | 20.3 14.6 7.33
16 | 2 | Performance data (cont) | 8 | 6 | 22.0 12.1 7.55
16 | 2 | Performance data (cont) | 8 | 7 | 18.8 18.8 7.16
16 | 2 | Performance data (cont) | 8 | 8 | 18.8 18.8 7.16
16 | 2 | Performance data (cont) | 8 | 9 | 19.4 17.8 7.25
16 | 2 | Performance data (cont) | 8 | 10 | 20.6 15.9 7.41
16 | 2 | Performance data (cont) | 9 | 1 | TC SHC kW
16 | 2 | Performance data (cont) | 9 | 2 | 17.1 17.1 7.31
16 | 2 | Performance data (cont) | 9 | 3 | 17.1 17.1 7.31
16 | 2 | Performance data (cont) | 9 | 4 | 17.9 16.1 7.42
16 | 2 | Performance data (cont) | 9 | 5 | 19.2 14.2 7.59
16 | 2 | Performance data (cont) | 9 | 6 | 20.8 11.7 7.83
16 | 2 | Performance data (cont) | 9 | 7 | 17.9 17.9 7.46
16 | 2 | Performance data (cont) | 9 | 8 | 17.9 17.9 7.47
16 | 2 | Performance data (cont) | 9 | 9 | 18.5 17.2 7.54
16 | 2 | Performance data (cont) | 9 | 10 | 19.5 15.5 7.69
16 | 2 | Performance data (cont) | 10 | 1 | TC SHC kW
16 | 2 | Performance data (cont) | 10 | 2 | 16.3 16.3 7.61
16 | 2 | Performance data (cont) | 10 | 3 | 16.3 16.3 7.61
16 | 2 | Performance data (cont) | 10 | 4 | 16.9 15.4 7.70
16 | 2 | Performance data (cont) | 10 | 5 | 18.0 13.9 7.87
16 | 2 | Performance data (cont) | 10 | 6 | 19.6 11.4 8.1
16 | 2 | Performance data (cont) | 10 | 7 | 17.1 17.1 7.76
16 | 2 | Performance data (cont) | 10 | 8 | 17.1 17.1 7.77
16 | 2 | Performance data (cont) | 10 | 9 | 17.4 16.5 7.82
16 | 2 | Performance data (cont) | 10 | 10 | 18.3 15.1 7.95
17 | 1 | COOLING CAPACITIES — SI (cont) | 1 | 1 | 1200/0.07
17 | 1 | COOLING CAPACITIES — SI (cont) | 1 | 2 | 1400/.08
17 | 2 | COOLING CAPACITIES — SI (cont) | 1 | 2 | 13
17 | 2 | COOLING CAPACITIES — SI (cont) | 1 | 3 | 16
17 | 2 | COOLING CAPACITIES — SI (cont) | 1 | 4 | 19
17 | 2 | COOLING CAPACITIES — SI (cont) | 1 | 5 | 22
17 | 2 | COOLING CAPACITIES — SI (cont) | 1 | 6 | 13
17 | 2 | COOLING CAPACITIES — SI (cont) | 1 | 7 | 16
17 | 2 | COOLING CAPACITIES — SI (cont) | 1 | 8 | 19
17 | 2 | COOLING CAPACITIES — SI (cont) | 1 | 9 | 22
17 | 2 | COOLING CAPACITIES — SI (cont) | 1 | 10 | 13
17 | 2 | COOLING CAPACITIES — SI (cont) | 1 | 11 | 16
17 | 2 | COOLING CAPACITIES — SI (cont) | 1 | 12 | 19
17 | 2 | COOLING CAPACITIES — SI (cont) | 2 | 1 | TC SHC kW
17 | 2 | COOLING CAPACITIES — SI (cont) | 2 | 2 | 24.7 24.1 6.25
17 | 2 | COOLING CAPACITIES — SI (cont) | 2 | 3 | 25.2 23.2 6.38
17 | 2 | COOLING CAPACITIES — SI (cont) | 2 | 4 | 28.4 19.3 6.60
17 | 2 | COOLING CAPACITIES — SI (cont) | 2 | 5 | 30.8 15.0 6.70
17 | 2 | COOLING CAPACITIES — SI (cont) | 2 | 6 | 26.0 25.2 6.60
17 | 2 | COOLING CAPACITIES — SI (cont) | 2 | 7 | 26.2 24.6 6.68
17 | 2 | COOLING CAPACITIES — SI (cont) | 2 | 8 | 29.1 20.5 6.97
17 | 2 | COOLING CAPACITIES — SI (cont) | 2 | 9 | 31.5 15.5 7.06
17 | 2 | COOLING CAPACITIES — SI (cont) | 2 | 10 | 27.9 26.5 7.25
17 | 2 | COOLING CAPACITIES — SI (cont) | 2 | 11 | 27.9 26.5 7.25
17 | 2 | COOLING CAPACITIES — SI (cont) | 2 | 12 | 29.9 22.0 7.66
17 | 2 | COOLING CAPACITIES — SI (cont) | 3 | 1 | TC SHC kW
17 | 2 | COOLING CAPACITIES — SI (cont) | 3 | 2 | 24.0 23.4 6.61
17 | 2 | COOLING CAPACITIES — SI (cont) | 3 | 3 | 24.3 22.8 6.69
17 | 2 | COOLING CAPACITIES — SI (cont) | 3 | 4 | 27.5 19.0 6.96
17 | 2 | COOLING CAPACITIES — SI (cont) | 3 | 5 | 30.3 14.8 7.09
17 | 2 | COOLING CAPACITIES — SI (cont) | 3 | 6 | 25.5 24.6 6.97
17 | 2 | COOLING CAPACITIES — SI (cont) | 3 | 7 | 25.5 24.3 7.02
17 | 2 | COOLING CAPACITIES — SI (cont) | 3 | 8 | 28.4 20.4 7.35
17 | 2 | COOLING CAPACITIES — SI (cont) | 3 | 9 | 30.9 15.4 7.46
17 | 2 | COOLING CAPACITIES — SI (cont) | 3 | 10 | 27.1 25.7 7.61
17 | 2 | COOLING CAPACITIES — SI (cont) | 3 | 11 | 27.1 25.8 7.60
17 | 2 | COOLING CAPACITIES — SI (cont) | 3 | 12 | 29.3 22.0 8.04
17 | 2 | COOLING CAPACITIES — SI (cont) | 4 | 1 | TC SHC kW
17 | 2 | COOLING CAPACITIES — SI (cont) | 4 | 2 | 23.0 22.5 7.00
17 | 2 | COOLING CAPACITIES — SI (cont) | 4 | 3 | 23.2 22.0 7.06
17 | 2 | COOLING CAPACITIES — SI (cont) | 4 | 4 | 26.5 18.7 7.33
17 | 2 | COOLING CAPACITIES — SI (cont) | 4 | 5 | 29.6 14.6 7.48
17 | 2 | COOLING CAPACITIES — SI (cont) | 4 | 6 | 24.7 23.9 7.34
17 | 2 | COOLING CAPACITIES — SI (cont) | 4 | 7 | 24.7 23.9 7.34
17 | 2 | COOLING CAPACITIES — SI (cont) | 4 | 8 | 27.5 20.1 7.71
17 | 2 | COOLING CAPACITIES — SI (cont) | 4 | 9 | 30.3 15.2 7.86
17 | 2 | COOLING CAPACITIES — SI (cont) | 4 | 10 | 26.4 25.0 7.98
17 | 2 | COOLING CAPACITIES — SI (cont) | 4 | 11 | 26.4 25.0 7.97
17 | 2 | COOLING CAPACITIES — SI (cont) | 4 | 12 | 28.4 21.8 8.42
17 | 2 | COOLING CAPACITIES — SI (cont) | 5 | 1 | TC SHC kW
17 | 2 | COOLING CAPACITIES — SI (cont) | 5 | 2 | 22.3 21.7 7.32
17 | 2 | COOLING CAPACITIES — SI (cont) | 5 | 3 | 22.4 21.4 7.36
17 | 2 | COOLING CAPACITIES — SI (cont) | 5 | 4 | 25.5 18.4 7.71
17 | 2 | COOLING CAPACITIES — SI (cont) | 5 | 5 | 28.7 14.3 7.87
17 | 2 | COOLING CAPACITIES — SI (cont) | 5 | 6 | 23.7 22.8 7.72
17 | 2 | COOLING CAPACITIES — SI (cont) | 5 | 7 | 23.7 22.8 7.72
17 | 2 | COOLING CAPACITIES — SI (cont) | 5 | 8 | 26.3 19.7 8.09
17 | 2 | COOLING CAPACITIES — SI (cont) | 5 | 9 | 29.4 15.0 8.25
17 | 2 | COOLING CAPACITIES — SI (cont) | 5 | 10 | 25.6 24.2 8.37
17 | 2 | COOLING CAPACITIES — SI (cont) | 5 | 11 | 25.6 24.2 8.36
17 | 2 | COOLING CAPACITIES — SI (cont) | 5 | 12 | 27.3 21.5 8.77
17 | 2 | COOLING CAPACITIES — SI (cont) | 6 | 1 | TC SHC kW
17 | 2 | COOLING CAPACITIES — SI (cont) | 6 | 2 | 21.7 21.1 7.56
17 | 2 | COOLING CAPACITIES — SI (cont) | 6 | 3 | 21.7 20.9 7.59
17 | 2 | COOLING CAPACITIES — SI (cont) | 6 | 4 | 24.6 17.9 8.01
17 | 2 | COOLING CAPACITIES — SI (cont) | 6 | 5 | 28.0 14.1 8.17
17 | 2 | COOLING CAPACITIES — SI (cont) | 6 | 6 | 23.1 22.2 8.00
17 | 2 | COOLING CAPACITIES — SI (cont) | 6 | 7 | 23.0 22.2 7.99
17 | 2 | COOLING CAPACITIES — SI (cont) | 6 | 8 | 25.6 19.5 8.37
17 | 2 | COOLING CAPACITIES — SI (cont) | 6 | 9 | 28.7 14.8 8.57
17 | 2 | COOLING CAPACITIES — SI (cont) | 6 | 10 | 25.0 23.6 8.66
17 | 2 | COOLING CAPACITIES — SI (cont) | 6 | 11 | 25.0 23.6 8.65
17 | 2 | COOLING CAPACITIES — SI (cont) | 6 | 12 | 26.4 21.2 9.03
17 | 2 | COOLING CAPACITIES — SI (cont) | 7 | 1 | TC SHC kW
17 | 2 | COOLING CAPACITIES — SI (cont) | 7 | 2 | 20.7 20.1 7.96
17 | 2 | COOLING CAPACITIES — SI (cont) | 7 | 3 | 20.7 20.1 7.96
17 | 2 | COOLING CAPACITIES — SI (cont) | 7 | 4 | 23.1 17.4 8.44
17 | 2 | COOLING CAPACITIES — SI (cont) | 7 | 5 | 26.7 13.6 8.66
17 | 2 | COOLING CAPACITIES — SI (cont) | 7 | 6 | 22.0 21.2 8.42
17 | 2 | COOLING CAPACITIES — SI (cont) | 7 | 7 | 22.0 21.2 8.41
17 | 2 | COOLING CAPACITIES — SI (cont) | 7 | 8 | 23.9 18.8 8.82
17 | 2 | COOLING CAPACITIES — SI (cont) | 7 | 9 | 27.4 14.3 9.06
17 | 2 | COOLING CAPACITIES — SI (cont) | 7 | 10 | 23.6 22.2 9.15
17 | 2 | COOLING CAPACITIES — SI (cont) | 7 | 11 | 23.6 22.2 9.14
17 | 2 | COOLING CAPACITIES — SI (cont) | 7 | 12 | 25.0 20.7 9.47
17 | 2 | COOLING CAPACITIES — SI (cont) | 8 | 1 | TC SHC kW
17 | 2 | COOLING CAPACITIES — SI (cont) | 8 | 2 | 19.9 19.3 8.29
17 | 2 | COOLING CAPACITIES — SI (cont) | 8 | 3 | 19.9 19.3 8.29
17 | 2 | COOLING CAPACITIES — SI (cont) | 8 | 4 | 22.0 16.9 8.78
17 | 2 | COOLING CAPACITIES — SI (cont) | 8 | 5 | 25.5 13.2 9.04
17 | 2 | COOLING CAPACITIES — SI (cont) | 8 | 6 | 21.2 20.3 8.75
17 | 2 | COOLING CAPACITIES — SI (cont) | 8 | 7 | 21.2 20.3 8.75
17 | 2 | COOLING CAPACITIES — SI (cont) | 8 | 8 | 22.7 18.3 9.15
17 | 2 | COOLING CAPACITIES — SI (cont) | 8 | 9 | 26.3 14.0 9.44
17 | 2 | COOLING CAPACITIES — SI (cont) | 8 | 10 | 22.7 21.3 9.52
17 | 2 | COOLING CAPACITIES — SI (cont) | 8 | 11 | 22.7 21.3 9.51
17 | 2 | COOLING CAPACITIES — SI (cont) | 8 | 12 | 23.7 20.2 9.80
17 | 2 | COOLING CAPACITIES — SI (cont) | 9 | 1 | TC SHC kW
17 | 2 | COOLING CAPACITIES — SI (cont) | 9 | 2 | 19.1 18.5 8.62
17 | 2 | COOLING CAPACITIES — SI (cont) | 9 | 3 | 19.1 18.5 8.62
17 | 2 | COOLING CAPACITIES — SI (cont) | 9 | 4 | 20.8 16.4 9.05
17 | 2 | COOLING CAPACITIES — SI (cont) | 9 | 5 | 24.3 12.8 9.42
17 | 2 | COOLING CAPACITIES — SI (cont) | 9 | 6 | 20.3 19.4 9.08
17 | 2 | COOLING CAPACITIES — SI (cont) | 9 | 7 | 20.3 19.4 9.08
17 | 2 | COOLING CAPACITIES — SI (cont) | 9 | 8 | 21.5 17.8 9.48
17 | 2 | COOLING CAPACITIES — SI (cont) | 9 | 9 | 25.0 13.5 9.83
17 | 2 | COOLING CAPACITIES — SI (cont) | 9 | 10 | 21.8 20.4 9.88
17 | 2 | COOLING CAPACITIES — SI (cont) | 9 | 11 | 21.8 20.4 9.87
17 | 2 | COOLING CAPACITIES — SI (cont) | 9 | 12 | 22.3 19.5 10.10
18 | 1 | Performance data (cont) | 1 | 2 | 14
18 | 1 | Performance data (cont) | 1 | 3 | 16
18 | 1 | Performance data (cont) | 1 | 4 | 18
18 | 1 | Performance data (cont) | 1 | 5 | 20
18 | 1 | Performance data (cont) | 1 | 6 | 22
18 | 1 | Performance data (cont) | 1 | 7 | 14
18 | 1 | Performance data (cont) | 1 | 8 | 16
18 | 1 | Performance data (cont) | 1 | 9 | 18
18 | 1 | Performance data (cont) | 1 | 10 | 20
18 | 1 | Performance data (cont) | 2 | 1 | TC SHC kW
18 | 1 | Performance data (cont) | 2 | 2 | 26.6 26.4 6.82
18 | 1 | Performance data (cont) | 2 | 3 | 28.2 24.8 6.98
18 | 1 | Performance data (cont) | 2 | 4 | 30.5 22.8 7.17
18 | 1 | Performance data (cont) | 2 | 5 | 33.1 20.3 7.35
18 | 1 | Performance data (cont) | 2 | 6 | 34.7 17.3 7.42
18 | 1 | Performance data (cont) | 2 | 7 | 30.5 30.4 7.09
18 | 1 | Performance data (cont) | 2 | 8 | 31.4 29.3 7.17
18 | 1 | Performance data (cont) | 2 | 9 | 32.7 26.2 7.27
18 | 1 | Performance data (cont) | 2 | 10 | 34.3 22.2 7.39
18 | 1 | Performance data (cont) | 3 | 1 | TC SHC kW
18 | 1 | Performance data (cont) | 3 | 2 | 25.8 25.6 7.20
18 | 1 | Performance data (cont) | 3 | 3 | 27.0 24.2 7.34
18 | 1 | Performance data (cont) | 3 | 4 | 29.4 22.3 7.54
18 | 1 | Performance data (cont) | 3 | 5 | 32.1 19.9 7.73
18 | 1 | Performance data (cont) | 3 | 6 | 33.8 16.8 7.82
18 | 1 | Performance data (cont) | 3 | 7 | 29.6 29.5 7.47
18 | 1 | Performance data (cont) | 3 | 8 | 30.4 28.7 7.53
18 | 1 | Performance data (cont) | 3 | 9 | 31.8 25.9 7.65
18 | 1 | Performance data (cont) | 3 | 10 | 33.5 22.2 7.80
18 | 1 | Performance data (cont) | 4 | 1 | TC SHC kW
18 | 1 | Performance data (cont) | 4 | 2 | 24.7 24.6 7.61
18 | 1 | Performance data (cont) | 4 | 3 | 25.8 23.5 7.93
18 | 1 | Performance data (cont) | 4 | 4 | 28.2 21.7 8.11
18 | 1 | Performance data (cont) | 4 | 5 | 30.8 19.4 8.32
18 | 1 | Performance data (cont) | 4 | 6 | 32.8 16.4 8.45
18 | 1 | Performance data (cont) | 4 | 7 | 28.5 28.5 8.09
18 | 1 | Performance data (cont) | 4 | 8 | 29.1 27.9 8.12
18 | 1 | Performance data (cont) | 4 | 9 | 30.7 25.4 8.26
18 | 1 | Performance data (cont) | 4 | 10 | 32.6 21.9 8.46
18 | 1 | Performance data (cont) | 5 | 1 | TC SHC kW
18 | 1 | Performance data (cont) | 5 | 2 | 23.6 23.5 8.03
18 | 1 | Performance data (cont) | 5 | 3 | 24.5 22.7 8.13
18 | 1 | Performance data (cont) | 5 | 4 | 26.6 21.1 8.31
18 | 1 | Performance data (cont) | 5 | 5 | 29.4 18.8 8.53
18 | 1 | Performance data (cont) | 5 | 6 | 31.8 16.1 8.67
18 | 1 | Performance data (cont) | 5 | 7 | 27.3 27.3 8.30
18 | 1 | Performance data (cont) | 5 | 8 | 27.7 27.0 8.32
18 | 1 | Performance data (cont) | 5 | 9 | 29.4 24.8 8.47
18 | 1 | Performance data (cont) | 5 | 10 | 31.5 21.6 8.67
18 | 1 | Performance data (cont) | 6 | 1 | TC SHC kW
18 | 1 | Performance data (cont) | 6 | 2 | 22.4 22.3 8.47
18 | 1 | Performance data (cont) | 6 | 3 | 23.0 21.8 8.53
18 | 1 | Performance data (cont) | 6 | 4 | 25.0 20.3 8.73
18 | 1 | Performance data (cont) | 6 | 5 | 27.9 18.2 8.96
18 | 1 | Performance data (cont) | 6 | 6 | 30.7 17.8 9.15
18 | 1 | Performance data (cont) | 6 | 7 | 26.1 26.0 8.74
18 | 1 | Performance data (cont) | 6 | 8 | 26.3 26.0 8.74
18 | 1 | Performance data (cont) | 6 | 9 | 27.9 24.1 8.89
18 | 1 | Performance data (cont) | 6 | 10 | 30.1 21.2 9.11
18 | 1 | Performance data (cont) | 7 | 1 | TC SHC kW
18 | 1 | Performance data (cont) | 7 | 2 | 21.1 21.1 8.95
18 | 1 | Performance data (cont) | 7 | 3 | 21.5 20.9 8.97
18 | 1 | Performance data (cont) | 7 | 4 | 23.4 19.6 9.15
18 | 1 | Performance data (cont) | 7 | 5 | 26.2 17.5 9.40
18 | 1 | Performance data (cont) | 7 | 6 | 29.5 15.3 9.64
18 | 1 | Performance data (cont) | 7 | 7 | 24.7 24.7 9.20
18 | 1 | Performance data (cont) | 7 | 8 | 24.7 24.7 9.20
18 | 1 | Performance data (cont) | 7 | 9 | 26.4 23.3 9.34
18 | 1 | Performance data (cont) | 7 | 10 | 28.7 20.7 9.56
18 | 1 | Performance data (cont) | 8 | 1 | TC SHC kW
18 | 1 | Performance data (cont) | 8 | 2 | 20.0 20.0 9.40
18 | 1 | Performance data (cont) | 8 | 3 | 20.1 19.9 9.40
18 | 1 | Performance data (cont) | 8 | 4 | 21.7 18.7 9.60
18 | 1 | Performance data (cont) | 8 | 5 | 24.4 16.8 9.86
18 | 1 | Performance data (cont) | 8 | 6 | 27.9 14.8 10.11
18 | 1 | Performance data (cont) | 8 | 7 | 23.1 23.1 9.70
18 | 1 | Performance data (cont) | 8 | 8 | 23.1 23.1 9.71
18 | 1 | Performance data (cont) | 8 | 9 | 24.4 22.0 9.82
18 | 1 | Performance data (cont) | 8 | 10 | 26.6 20.0 10.03
18 | 1 | Performance data (cont) | 9 | 1 | TC SHC kW
18 | 1 | Performance data (cont) | 9 | 2 | 19.1 10.1 9.89
18 | 1 | Performance data (cont) | 9 | 3 | 19.1 19.1 9.89
18 | 1 | Performance data (cont) | 9 | 4 | 20.3 17.9 10.06
18 | 1 | Performance data (cont) | 9 | 5 | 22.6 16.2 10.32
18 | 1 | Performance data (cont) | 9 | 6 | 26.0 14.2 10.59
18 | 1 | Performance data (cont) | 9 | 7 | 21.5 21.5 10.22
18 | 1 | Performance data (cont) | 9 | 8 | 21.5 21.5 10.22
18 | 1 | Performance data (cont) | 9 | 9 | 22.4 20.7 10.31
18 | 1 | Performance data (cont) | 9 | 10 | 24.3 19.1 10.50
18 | 1 | Performance data (cont) | 10 | 1 | TC SHC kW
18 | 1 | Performance data (cont) | 10 | 2 | 18.3 18.3 10.37
18 | 1 | Performance data (cont) | 10 | 3 | 18.3 18.3 10.37
18 | 1 | Performance data (cont) | 10 | 4 | 19.1 17.2 10.52
18 | 1 | Performance data (cont) | 10 | 5 | 20.9 15.5 10.77
18 | 1 | Performance data (cont) | 10 | 6 | 24.0 13.5 11.07
18 | 1 | Performance data (cont) | 10 | 7 | 20.0 20.0 10.74
18 | 1 | Performance data (cont) | 10 | 8 | 20.0 20.0 10.74
18 | 1 | Performance data (cont) | 10 | 9 | 20.4 18.4 10.81
18 | 1 | Performance data (cont) | 10 | 10 | 21.9 18.1 10.98
18 | 2 | Performance data (cont) | 1 | 2 | 14
18 | 2 | Performance data (cont) | 1 | 3 | 16
18 | 2 | Performance data (cont) | 1 | 4 | 18
18 | 2 | Performance data (cont) | 1 | 5 | 20
18 | 2 | Performance data (cont) | 1 | 6 | 22
18 | 2 | Performance data (cont) | 1 | 7 | 14
18 | 2 | Performance data (cont) | 1 | 8 | 16
18 | 2 | Performance data (cont) | 1 | 9 | 18
18 | 2 | Performance data (cont) | 1 | 10 | 20
18 | 2 | Performance data (cont) | 2 | 1 | TC SHC kW
18 | 2 | Performance data (cont) | 2 | 2 | 31.5 31.4 7.12
18 | 2 | Performance data (cont) | 2 | 3 | 31.9 30.6 7.16
18 | 2 | Performance data (cont) | 2 | 4 | 33.3 27.8 7.30
18 | 2 | Performance data (cont) | 2 | 5 | 35.3 24.0 7.50
18 | 2 | Performance data (cont) | 2 | 6 | 37.2 19.9 7.70
18 | 2 | Performance data (cont) | 2 | 7 | 31.7 31.7 7.15
18 | 2 | Performance data (cont) | 2 | 8 | 23.1 31.1 7.18
18 | 2 | Performance data (cont) | 2 | 9 | 33.5 28.3 7.32
18 | 2 | Performance data (cont) | 2 | 10 | 35.3 24.4 7.51
18 | 2 | Performance data (cont) | 3 | 1 | TC SHC kW
18 | 2 | Performance data (cont) | 3 | 2 | 30.8 30.8 7.53
18 | 2 | Performance data (cont) | 3 | 3 | 31.0 30.1 7.54
18 | 2 | Performance data (cont) | 3 | 4 | 32.4 27.4 7.68
18 | 2 | Performance data (cont) | 3 | 5 | 34.2 23.6 7.88
18 | 2 | Performance data (cont) | 3 | 6 | 36.2 19.6 8.10
18 | 2 | Performance data (cont) | 3 | 7 | 31.0 31.0 7.54
18 | 2 | Performance data (cont) | 3 | 8 | 31.2 30.5 7.57
18 | 2 | Performance data (cont) | 3 | 9 | 32.5 27.9 7.71
18 | 2 | Performance data (cont) | 3 | 10 | 34.4 24.0 7.90
18 | 2 | Performance data (cont) | 4 | 1 | TC SHC kW
18 | 2 | Performance data (cont) | 4 | 2 | 30.0 30.0 7.95
18 | 2 | Performance data (cont) | 4 | 3 | 30.1 29.6 7.97
18 | 2 | Performance data (cont) | 4 | 4 | 31.4 27.2 8.11
18 | 2 | Performance data (cont) | 4 | 5 | 33.2 23.4 8.30
18 | 2 | Performance data (cont) | 4 | 6 | 35.2 19.3 8.51
18 | 2 | Performance data (cont) | 4 | 7 | 30.3 30.2 7.99
18 | 2 | Performance data (cont) | 4 | 8 | 30.4 30.1 7.99
18 | 2 | Performance data (cont) | 4 | 9 | 31.6 27.6 8.13
18 | 2 | Performance data (cont) | 4 | 10 | 33.3 23.7 8.31
18 | 2 | Performance data (cont) | 5 | 1 | TC SHC kW
18 | 2 | Performance data (cont) | 5 | 2 | 29.1 29.1 8.40
18 | 2 | Performance data (cont) | 5 | 3 | 29.1 29.0 8.41
18 | 2 | Performance data (cont) | 5 | 4 | 30.3 26.7 8.54
18 | 2 | Performance data (cont) | 5 | 5 | 32.1 23.1 8.73
18 | 2 | Performance data (cont) | 5 | 6 | 34.0 18.9 8.95
18 | 2 | Performance data (cont) | 5 | 7 | 29.4 29.4 8.44
18 | 2 | Performance data (cont) | 5 | 8 | 29.4 29.4 8.44
18 | 2 | Performance data (cont) | 5 | 9 | 30.5 27.1 8.56
18 | 2 | Performance data (cont) | 5 | 10 | 32.2 23.5 8.75
18 | 2 | Performance data (cont) | 6 | 1 | TC SHC kW
18 | 2 | Performance data (cont) | 6 | 2 | 28.1 27.9 8.87
18 | 2 | Performance data (cont) | 6 | 3 | 28.0 28.0 8.87
18 | 2 | Performance data (cont) | 6 | 4 | 29.1 26.1 8.89
18 | 2 | Performance data (cont) | 6 | 5 | 30.8 22.8 9.17
18 | 2 | Performance data (cont) | 6 | 6 | 32.8 18.5 9.40
18 | 2 | Performance data (cont) | 6 | 7 | 28.3 28.3 8.91
18 | 2 | Performance data (cont) | 6 | 8 | 28.3 28.3 8.91
18 | 2 | Performance data (cont) | 6 | 9 | 29.3 26.5 9.01
18 | 2 | Performance data (cont) | 6 | 10 | 31.0 23.3 9.19
18 | 2 | Performance data (cont) | 7 | 1 | TC SHC kW
18 | 2 | Performance data (cont) | 7 | 2 | 26.5 14.7 9.37
18 | 2 | Performance data (cont) | 7 | 3 | 26.5 26.5 9.36
18 | 2 | Performance data (cont) | 7 | 4 | 27.7 25.1 9.46
18 | 2 | Performance data (cont) | 7 | 5 | 29.5 22.5 9.64
18 | 2 | Performance data (cont) | 7 | 6 | 31.5 18.3 9.88
18 | 2 | Performance data (cont) | 7 | 7 | 27.0 26.9 9.41
18 | 2 | Performance data (cont) | 7 | 8 | 27.0 27.0 9.40
18 | 2 | Performance data (cont) | 7 | 9 | 28.0 25.6 9.50
18 | 2 | Performance data (cont) | 7 | 10 | 29.7 23.0 9.66
18 | 2 | Performance data (cont) | 8 | 1 | TC SHC kW
18 | 2 | Performance data (cont) | 8 | 2 | 24.8 24.8 9.87
18 | 2 | Performance data (cont) | 8 | 3 | 24.8 24.8 9.87
18 | 2 | Performance data (cont) | 8 | 4 | 25.7 23.8 9.96
18 | 2 | Performance data (cont) | 8 | 5 | 27.5 21.8 10.12
18 | 2 | Performance data (cont) | 8 | 6 | 30.0 18.0 10.36
18 | 2 | Performance data (cont) | 8 | 7 | 25.2 25.2 9.92
18 | 2 | Performance data (cont) | 8 | 8 | 25.2 25.2 9.92
18 | 2 | Performance data (cont) | 8 | 9 | 26.1 24.4 9.99
18 | 2 | Performance data (cont) | 8 | 10 | 27.7 22.3 10.13
18 | 2 | Performance data (cont) | 9 | 1 | TC SHC kW
18 | 2 | Performance data (cont) | 9 | 2 | 23.0 23.0 10.39
18 | 2 | Performance data (cont) | 9 | 3 | 23.0 23.0 10.39
18 | 2 | Performance data (cont) | 9 | 4 | 23.7 22.4 10.45
18 | 2 | Performance data (cont) | 9 | 5 | 25.3 20.9 10.59
18 | 2 | Performance data (cont) | 9 | 6 | 28.3 17.5 10.86
18 | 2 | Performance data (cont) | 9 | 7 | 23.4 23.4 10.43
18 | 2 | Performance data (cont) | 9 | 8 | 23.4 23.4 10.43
18 | 2 | Performance data (cont) | 9 | 9 | 24.0 23.0 10.49
18 | 2 | Performance data (cont) | 9 | 10 | 25.5 21.4 10.61
18 | 2 | Performance data (cont) | 10 | 1 | TC SHC kW
18 | 2 | Performance data (cont) | 10 | 2 | 21.3 21.3 10.93
18 | 2 | Performance data (cont) | 10 | 3 | 21.3 21.3 10.93
18 | 2 | Performance data (cont) | 10 | 4 | 21.6 21.0 10.95
18 | 2 | Performance data (cont) | 10 | 5 | 22.8 19.9 11.07
18 | 2 | Performance data (cont) | 10 | 6 | 26.5 17.0 11.38
18 | 2 | Performance data (cont) | 10 | 7 | 21.6 21.6 10.97
18 | 2 | Performance data (cont) | 10 | 8 | 21.6 21.6 10.97
18 | 2 | Performance data (cont) | 10 | 9 | 21.8 21.4 10.99
18 | 2 | Performance data (cont) | 10 | 10 | 23.0 20.4 11.10
19 | 1 | COOLING CAPACITIES — SI (cont) | 1 | 1 | 1500/0.13
19 | 1 | COOLING CAPACITIES — SI (cont) | 1 | 2 | 2000/0.17
19 | 2 | COOLING CAPACITIES — SI (cont) | 1 | 2 | 13
19 | 2 | COOLING CAPACITIES — SI (cont) | 1 | 3 | 16
19 | 2 | COOLING CAPACITIES — SI (cont) | 1 | 4 | 19
19 | 2 | COOLING CAPACITIES — SI (cont) | 1 | 5 | 22
19 | 2 | COOLING CAPACITIES — SI (cont) | 1 | 6 | 13
19 | 2 | COOLING CAPACITIES — SI (cont) | 1 | 7 | 16
19 | 2 | COOLING CAPACITIES — SI (cont) | 1 | 8 | 19
19 | 2 | COOLING CAPACITIES — SI (cont) | 1 | 9 | 22
19 | 2 | COOLING CAPACITIES — SI (cont) | 1 | 10 | 13
19 | 2 | COOLING CAPACITIES — SI (cont) | 1 | 11 | 16
19 | 2 | COOLING CAPACITIES — SI (cont) | 1 | 12 | 19
19 | 2 | COOLING CAPACITIES — SI (cont) | 2 | 1 | TC SHC kW
19 | 2 | COOLING CAPACITIES — SI (cont) | 2 | 2 | 34.7 34.7 8.92
19 | 2 | COOLING CAPACITIES — SI (cont) | 2 | 3 | 38.0 33.8 8.99
19 | 2 | COOLING CAPACITIES — SI (cont) | 2 | 4 | 41.4 28.1 9.08
19 | 2 | COOLING CAPACITIES — SI (cont) | 2 | 5 | 44.4 22.0 9.13
19 | 2 | COOLING CAPACITIES — SI (cont) | 2 | 6 | 37.0 37.0 9.00
19 | 2 | COOLING CAPACITIES — SI (cont) | 2 | 7 | 40.0 39.9 9.06
19 | 2 | COOLING CAPACITIES — SI (cont) | 2 | 8 | 43.2 31.7 9.13
19 | 2 | COOLING CAPACITIES — SI (cont) | 2 | 9 | 46.3 24.0 9.22
19 | 2 | COOLING CAPACITIES — SI (cont) | 2 | 10 | 36.6 36.6 9.05
19 | 2 | COOLING CAPACITIES — SI (cont) | 2 | 11 | 40.1 40.1 9.10
19 | 2 | COOLING CAPACITIES — SI (cont) | 2 | 12 | 43.6 33.5 9.15
19 | 2 | COOLING CAPACITIES — SI (cont) | 3 | 1 | TC SHC kW
19 | 2 | COOLING CAPACITIES — SI (cont) | 3 | 2 | 32.1 32.1 9.34
19 | 2 | COOLING CAPACITIES — SI (cont) | 3 | 3 | 35.8 32.8 9.46
19 | 2 | COOLING CAPACITIES — SI (cont) | 3 | 4 | 39.6 27.4 9.60
19 | 2 | COOLING CAPACITIES — SI (cont) | 3 | 5 | 43.0 21.6 9.70
19 | 2 | COOLING CAPACITIES — SI (cont) | 3 | 6 | 34.8 34.8 9.47
19 | 2 | COOLING CAPACITIES — SI (cont) | 3 | 7 | 38.2 38.2 9.57
19 | 2 | COOLING CAPACITIES — SI (cont) | 3 | 8 | 41.6 31.1 9.68
19 | 2 | COOLING CAPACITIES — SI (cont) | 3 | 9 | 44.9 23.7 9.80
19 | 2 | COOLING CAPACITIES — SI (cont) | 3 | 10 | 35.5 35.5 9.60
19 | 2 | COOLING CAPACITIES — SI (cont) | 3 | 11 | 38.7 38.7 9.63
19 | 2 | COOLING CAPACITIES — SI (cont) | 3 | 12 | 42.1 32.4 9.74
19 | 2 | COOLING CAPACITIES — SI (cont) | 4 | 1 | TC SHC kW
19 | 2 | COOLING CAPACITIES — SI (cont) | 4 | 2 | 29.4 29.4 9.78
19 | 2 | COOLING CAPACITIES — SI (cont) | 4 | 3 | 33.6 31.9 9.94
19 | 2 | COOLING CAPACITIES — SI (cont) | 4 | 4 | 37.9 26.7 10.12
19 | 2 | COOLING CAPACITIES — SI (cont) | 4 | 5 | 41.6 21.1 10.27
19 | 2 | COOLING CAPACITIES — SI (cont) | 4 | 6 | 32.9 32.9 9.95
19 | 2 | COOLING CAPACITIES — SI (cont) | 4 | 7 | 36.3 36.3 10.08
19 | 2 | COOLING CAPACITIES — SI (cont) | 4 | 8 | 40.0 30.5 10.22
19 | 2 | COOLING CAPACITIES — SI (cont) | 4 | 9 | 43.4 23.3 10.39
19 | 2 | COOLING CAPACITIES — SI (cont) | 4 | 10 | 34.4 34.4 10.15
19 | 2 | COOLING CAPACITIES — SI (cont) | 4 | 11 | 37.4 37.4 10.10
19 | 2 | COOLING CAPACITIES — SI (cont) | 4 | 12 | 40.6 32.5 10.25
19 | 2 | COOLING CAPACITIES — SI (cont) | 5 | 1 | TC SHC kW
19 | 2 | COOLING CAPACITIES — SI (cont) | 5 | 2 | 26.7 26.7 10.20
19 | 2 | COOLING CAPACITIES — SI (cont) | 5 | 3 | 31.5 30.9 10.42
19 | 2 | COOLING CAPACITIES — SI (cont) | 5 | 4 | 36.2 26.0 10.64
19 | 2 | COOLING CAPACITIES — SI (cont) | 5 | 5 | 40.2 20.7 10.85
19 | 2 | COOLING CAPACITIES — SI (cont) | 5 | 6 | 30.8 30.8 10.40
19 | 2 | COOLING CAPACITIES — SI (cont) | 5 | 7 | 34.5 34.5 10.59
19 | 2 | COOLING CAPACITIES — SI (cont) | 5 | 8 | 38.3 29.9 10.76
19 | 2 | COOLING CAPACITIES — SI (cont) | 5 | 9 | 42.0 22.9 10.96
19 | 2 | COOLING CAPACITIES — SI (cont) | 5 | 10 | 33.0 33.0 10.49
19 | 2 | COOLING CAPACITIES — SI (cont) | 5 | 11 | 36.0 36.0 10.65
19 | 2 | COOLING CAPACITIES — SI (cont) | 5 | 12 | 39.1 31.9 10.82
19 | 2 | COOLING CAPACITIES — SI (cont) | 6 | 1 | TC SHC kW
19 | 2 | COOLING CAPACITIES — SI (cont) | 6 | 2 | 24.7 24.7 10.52
19 | 2 | COOLING CAPACITIES — SI (cont) | 6 | 3 | 29.9 29.7 10.80
19 | 2 | COOLING CAPACITIES — SI (cont) | 6 | 4 | 34.9 25.5 11.03
19 | 2 | COOLING CAPACITIES — SI (cont) | 6 | 5 | 39.1 20.3 11.30
19 | 2 | COOLING CAPACITIES — SI (cont) | 6 | 6 | 29.2 29.2 10.77
19 | 2 | COOLING CAPACITIES — SI (cont) | 6 | 7 | 33.1 33.1 11.00
19 | 2 | COOLING CAPACITIES — SI (cont) | 6 | 8 | 37.0 29.4 11.18
19 | 2 | COOLING CAPACITIES — SI (cont) | 6 | 9 | 40.9 22.7 11.40
19 | 2 | COOLING CAPACITIES — SI (cont) | 6 | 10 | 31.4 31.4 10.40
19 | 2 | COOLING CAPACITIES — SI (cont) | 6 | 11 | 35.0 35.0 11.07
19 | 2 | COOLING CAPACITIES — SI (cont) | 6 | 12 | 38.0 31.5 11.25
19 | 2 | COOLING CAPACITIES — SI (cont) | 7 | 1 | TC SHC kW
19 | 2 | COOLING CAPACITIES — SI (cont) | 7 | 2 | 21.1 21.1 11.10
19 | 2 | COOLING CAPACITIES — SI (cont) | 7 | 3 | 26.8 26.8 11.40
19 | 2 | COOLING CAPACITIES — SI (cont) | 7 | 4 | 32.3 24.4 11.71
19 | 2 | COOLING CAPACITIES — SI (cont) | 7 | 5 | 37.1 19.7 12.00
19 | 2 | COOLING CAPACITIES — SI (cont) | 7 | 6 | 26.9 26.9 11.42
19 | 2 | COOLING CAPACITIES — SI (cont) | 7 | 7 | 30.8 30.8 11.64
19 | 2 | COOLING CAPACITIES — SI (cont) | 7 | 8 | 34.7 28.3 11.88
19 | 2 | COOLING CAPACITIES — SI (cont) | 7 | 9 | 38.8 22.1 12.13
19 | 2 | COOLING CAPACITIES — SI (cont) | 7 | 10 | 30.5 30.5 11.64
19 | 2 | COOLING CAPACITIES — SI (cont) | 7 | 11 | 53.1 33.1 11.79
19 | 2 | COOLING CAPACITIES — SI (cont) | 7 | 12 | 35.8 30.6 11.96
19 | 2 | COOLING CAPACITIES — SI (cont) | 8 | 1 | TC SHC kW
19 | 2 | COOLING CAPACITIES — SI (cont) | 8 | 2 | 20.5 20.5 11.62
19 | 2 | COOLING CAPACITIES — SI (cont) | 8 | 3 | 25.3 25.3 11.93
19 | 2 | COOLING CAPACITIES — SI (cont) | 8 | 4 | 30.2 23.5 12.25
19 | 2 | COOLING CAPACITIES — SI (cont) | 8 | 5 | 35.2 19.1 12.58
19 | 2 | COOLING CAPACITIES — SI (cont) | 8 | 6 | 25.7 25.7 12.05
19 | 2 | COOLING CAPACITIES — SI (cont) | 8 | 7 | 28.8 28.8 12.24
19 | 2 | COOLING CAPACITIES — SI (cont) | 8 | 8 | 32.2 27.1 12.44
19 | 2 | COOLING CAPACITIES — SI (cont) | 8 | 9 | 36.9 21.5 12.73
19 | 2 | COOLING CAPACITIES — SI (cont) | 8 | 10 | 29.1 29.1 12.26
19 | 2 | COOLING CAPACITIES — SI (cont) | 8 | 11 | 31.0 31.0 12.38
19 | 2 | COOLING CAPACITIES — SI (cont) | 8 | 12 | 33.4 29.4 12.52
19 | 2 | COOLING CAPACITIES — SI (cont) | 9 | 1 | TC SHC kW
19 | 2 | COOLING CAPACITIES — SI (cont) | 9 | 2 | 20.4 20.4 12.15
19 | 2 | COOLING CAPACITIES — SI (cont) | 9 | 3 | 24.1 24.1 12.45
19 | 2 | COOLING CAPACITIES — SI (cont) | 9 | 4 | 27.9 27.9 12.78
19 | 2 | COOLING CAPACITIES — SI (cont) | 9 | 5 | 33.2 33.2 13.17
19 | 2 | COOLING CAPACITIES — SI (cont) | 9 | 6 | 24.5 24.5 12.68
19 | 2 | COOLING CAPACITIES — SI (cont) | 9 | 7 | 26.9 26.9 12.84
19 | 2 | COOLING CAPACITIES — SI (cont) | 9 | 8 | 29.6 25.8 13.00
19 | 2 | COOLING CAPACITIES — SI (cont) | 9 | 9 | 34.9 21.0 13.33
19 | 2 | COOLING CAPACITIES — SI (cont) | 9 | 10 | 27.7 27.7 12.88
19 | 2 | COOLING CAPACITIES — SI (cont) | 9 | 11 | 29.0 29.0 12.97
19 | 2 | COOLING CAPACITIES — SI (cont) | 9 | 12 | 30.8 28.1 13.10
19 | 2 | COOLING CAPACITIES — SI (cont) | 10 | 1 | TC SHC kW
19 | 2 | COOLING CAPACITIES — SI (cont) | 10 | 2 | 20.1 20.1 12.67
19 | 2 | COOLING CAPACITIES — SI (cont) | 10 | 3 | 22.8 22.8 12.98
19 | 2 | COOLING CAPACITIES — SI (cont) | 10 | 4 | 25.8 21.4 13.31
19 | 2 | COOLING CAPACITIES — SI (cont) | 10 | 5 | 31.3 17.8 13.75
19 | 2 | COOLING CAPACITIES — SI (cont) | 10 | 6 | 23.3 23.3 13.34
19 | 2 | COOLING CAPACITIES — SI (cont) | 10 | 7 | 24.9 24.9 13.43
19 | 2 | COOLING CAPACITIES — SI (cont) | 10 | 8 | 27.0 24.5 13.56
19 | 2 | COOLING CAPACITIES — SI (cont) | 10 | 9 | 33.1 20.3 13.93
19 | 2 | COOLING CAPACITIES — SI (cont) | 10 | 10 | 26.2 26.0 13.49
19 | 2 | COOLING CAPACITIES — SI (cont) | 10 | 11 | 26.9 26.8 13.57
19 | 2 | COOLING CAPACITIES — SI (cont) | 10 | 12 | 28.2 26.7 13.67
20 | 1 | Performance data (cont) | 1 | 1 | 1500/0.05
20 | 1 | Performance data (cont) | 1 | 2 | 2000/0.07
20 | 2 | Performance data (cont) | 1 | 2 | 62
20 | 2 | Performance data (cont) | 1 | 3 | 67
20 | 2 | Performance data (cont) | 1 | 4 | 72
20 | 2 | Performance data (cont) | 1 | 5 | 62
20 | 2 | Performance data (cont) | 1 | 6 | 67
20 | 2 | Performance data (cont) | 1 | 7 | 72
20 | 2 | Performance data (cont) | 1 | 8 | 62
20 | 2 | Performance data (cont) | 1 | 9 | 67
20 | 2 | Performance data (cont) | 2 | 1 | TC SHC kW
20 | 2 | Performance data (cont) | 2 | 2 | 60.0 50.5 4.44
20 | 2 | Performance data (cont) | 2 | 3 | 66.0 42.6 4.57
20 | 2 | Performance data (cont) | 2 | 4 | 72.1 34.5 4.71
20 | 2 | Performance data (cont) | 2 | 5 | 63.0 58.2 4.52
20 | 2 | Performance data (cont) | 2 | 6 | 69.2 48.5 4.66
20 | 2 | Performance data (cont) | 2 | 7 | 76.1 38.3 4.84
20 | 2 | Performance data (cont) | 2 | 8 | 65.2 64.3 4.58
20 | 2 | Performance data (cont) | 2 | 9 | 71.5 54.0 4.74
20 | 2 | Performance data (cont) | 3 | 1 | TC SHC kW
20 | 2 | Performance data (cont) | 3 | 2 | 57.2 49.4 4.85
20 | 2 | Performance data (cont) | 3 | 3 | 63.2 41.6 5.00
20 | 2 | Performance data (cont) | 3 | 4 | 69.4 33.5 5.17
20 | 2 | Performance data (cont) | 3 | 5 | 60.3 57.3 4.96
20 | 2 | Performance data (cont) | 3 | 6 | 66.3 47.5 5.11
20 | 2 | Performance data (cont) | 3 | 7 | 72.4 37.1 5.28
20 | 2 | Performance data (cont) | 3 | 8 | 62.6 62.6 5.03
20 | 2 | Performance data (cont) | 3 | 9 | 68.0 52.8 5.18
20 | 2 | Performance data (cont) | 4 | 1 | TC SHC kW
20 | 2 | Performance data (cont) | 4 | 2 | 54.4 48.1 5.25
20 | 2 | Performance data (cont) | 4 | 3 | 60.2 40.4 5.43
20 | 2 | Performance data (cont) | 4 | 4 | 66.3 32.4 5.62
20 | 2 | Performance data (cont) | 4 | 5 | 57.1 55.6 5.35
20 | 2 | Performance data (cont) | 4 | 6 | 62.9 46.4 5.54
20 | 2 | Performance data (cont) | 4 | 7 | 69.4 36.2 5.75
20 | 2 | Performance data (cont) | 4 | 8 | 60.0 60.0 5.47
20 | 2 | Performance data (cont) | 4 | 9 | 64.7 52.0 5.62
20 | 2 | Performance data (cont) | 5 | 1 | TC SHC kW
20 | 2 | Performance data (cont) | 5 | 2 | 51.0 46.5 5.64
20 | 2 | Performance data (cont) | 5 | 3 | 56.9 39.1 5.83
20 | 2 | Performance data (cont) | 5 | 4 | 62.9 31.2 6.05
20 | 2 | Performance data (cont) | 5 | 5 | 54.2 53.5 5.76
20 | 2 | Performance data (cont) | 5 | 6 | 59.5 45.2 5.97
20 | 2 | Performance data (cont) | 5 | 7 | 65.7 35.0 6.19
20 | 2 | Performance data (cont) | 5 | 8 | 57.2 57.2 5.90
20 | 2 | Performance data (cont) | 5 | 9 | 61.1 50.7 6.05
20 | 2 | Performance data (cont) | 6 | 1 | TC SHC kW
20 | 2 | Performance data (cont) | 6 | 2 | 47.6 45.0 6.02
20 | 2 | Performance data (cont) | 6 | 3 | 53.7 37.8 6.24
20 | 2 | Performance data (cont) | 6 | 4 | 59.5 30.0 6.48
20 | 2 | Performance data (cont) | 6 | 5 | 51.4 51.3 6.17
20 | 2 | Performance data (cont) | 6 | 6 | 56.0 44.0 6.39
20 | 2 | Performance data (cont) | 6 | 7 | 62.0 33.8 6.63
20 | 2 | Performance data (cont) | 6 | 8 | 54.4 54.4 6.33
20 | 2 | Performance data (cont) | 6 | 9 | 57.4 49.4 6.48
20 | 2 | Performance data (cont) | 7 | 1 | TC SHC kW
20 | 2 | Performance data (cont) | 7 | 2 | 44.7 43.5 6.39
20 | 2 | Performance data (cont) | 7 | 3 | 50.3 36.6 6.65
20 | 2 | Performance data (cont) | 7 | 4 | 55.8 28.8 6.90
20 | 2 | Performance data (cont) | 7 | 5 | 48.7 48.7 6.61
20 | 2 | Performance data (cont) | 7 | 6 | 52.3 42.5 6.77
20 | 2 | Performance data (cont) | 7 | 7 | 58.0 32.4 7.03
20 | 2 | Performance data (cont) | 7 | 8 | 51.6 51.6 6.79
20 | 2 | Performance data (cont) | 7 | 9 | 53.5 47.7 6.87
20 | 3 | Performance data (cont) | 1 | 1 | 1950/0.06
20 | 3 | Performance data (cont) | 1 | 2 | 2400/0.075
20 | 3 | Performance data (cont) | 1 | 3 | 2500/0.075
20 | 4 | Performance data (cont) | 1 | 2 | 62
20 | 4 | Performance data (cont) | 1 | 3 | 67
20 | 4 | Performance data (cont) | 1 | 4 | 72
20 | 4 | Performance data (cont) | 1 | 5 | 62
20 | 4 | Performance data (cont) | 1 | 6 | 67
20 | 4 | Performance data (cont) | 1 | 7 | 72
20 | 4 | Performance data (cont) | 1 | 8 | 62
20 | 4 | Performance data (cont) | 1 | 9 | 67
20 | 4 | Performance data (cont) | 1 | 10 | 72
20 | 4 | Performance data (cont) | 1 | 11 | 62
20 | 4 | Performance data (cont) | 1 | 12 | 67
20 | 4 | Performance data (cont) | 2 | 1 | TC SHC kW
20 | 4 | Performance data (cont) | 2 | 2 | 71.9 56.3 5.47
20 | 4 | Performance data (cont) | 2 | 3 | 80.1 46.6 5.73
20 | 4 | Performance data (cont) | 2 | 4 | 88.3 55.1 6.02
20 | 4 | Performance data (cont) | 2 | 5 | 74.9 62.3 5.60
20 | 4 | Performance data (cont) | 2 | 6 | 83.0 50.5 5.86
20 | 4 | Performance data (cont) | 2 | 7 | 90.9 57.0 6.14
20 | 4 | Performance data (cont) | 2 | 8 | 75.3 63.6 5.64
20 | 4 | Performance data (cont) | 2 | 9 | 83.6 51.2 5.90
20 | 4 | Performance data (cont) | 2 | 10 | 91.3 60.4 6.14
20 | 4 | Performance data (cont) | 2 | 11 | 77.4 69.1 5.74
20 | 4 | Performance data (cont) | 2 | 12 | 85.2 55.3 6.00
20 | 4 | Performance data (cont) | 3 | 1 | TC SHC kW
20 | 4 | Performance data (cont) | 3 | 2 | 69.0 59.7 5.77
20 | 4 | Performance data (cont) | 3 | 3 | 77.1 50.5 6.04
20 | 4 | Performance data (cont) | 3 | 4 | 85.4 40.6 6.34
20 | 4 | Performance data (cont) | 3 | 5 | 71.7 66.6 5.90
20 | 4 | Performance data (cont) | 3 | 6 | 79.8 55.6 6.17
20 | 4 | Performance data (cont) | 3 | 7 | 88.2 43.6 6.47
20 | 4 | Performance data (cont) | 3 | 8 | 72.2 68.0 5.93
20 | 4 | Performance data (cont) | 3 | 9 | 80.2 56.6 6.19
20 | 4 | Performance data (cont) | 3 | 10 | 88.5 44.1 6.49
20 | 4 | Performance data (cont) | 3 | 11 | 74.3 73.8 6.05
20 | 4 | Performance data (cont) | 3 | 12 | 82.0 62.0 6.31
20 | 4 | Performance data (cont) | 4 | 1 | TC SHC kW
20 | 4 | Performance data (cont) | 4 | 2 | 64.9 57.9 6.32
20 | 4 | Performance data (cont) | 4 | 3 | 72.7 48.8 6.61
20 | 4 | Performance data (cont) | 4 | 4 | 80.8 39.1 6.54
20 | 4 | Performance data (cont) | 4 | 5 | 67.4 64.6 6.45
20 | 4 | Performance data (cont) | 4 | 6 | 75.2 54.0 6.75
20 | 4 | Performance data (cont) | 4 | 7 | 83.5 42.1 6.60
20 | 4 | Performance data (cont) | 4 | 8 | 67.8 65.8 6.48
20 | 4 | Performance data (cont) | 4 | 9 | 75.6 55.1 6.76
20 | 4 | Performance data (cont) | 4 | 10 | 83.8 42.7 6.69
20 | 4 | Performance data (cont) | 4 | 11 | 70.7 70.5 6.60
20 | 4 | Performance data (cont) | 4 | 12 | 77.1 60.2 6.86
20 | 4 | Performance data (cont) | 5 | 1 | TC SHC kW
20 | 4 | Performance data (cont) | 5 | 2 | 60.4 55.7 6.59
20 | 4 | Performance data (cont) | 5 | 3 | 68.1 47.2 6.86
20 | 4 | Performance data (cont) | 5 | 4 | 76.2 37.5 7.19
20 | 4 | Performance data (cont) | 5 | 5 | 63.0 62.2 6.71
20 | 4 | Performance data (cont) | 5 | 6 | 70.4 52.4 7.00
20 | 4 | Performance data (cont) | 5 | 7 | 78.6 40.8 7.32
20 | 4 | Performance data (cont) | 5 | 8 | 63.5 63.2 6.74
20 | 4 | Performance data (cont) | 5 | 9 | 70.8 53.4 7.02
20 | 4 | Performance data (cont) | 5 | 10 | 78.8 41.3 7.34
20 | 4 | Performance data (cont) | 5 | 11 | 66.7 66.7 6.90
20 | 4 | Performance data (cont) | 5 | 12 | 72.0 58.6 7.11
20 | 4 | Performance data (cont) | 6 | 1 | TC SHC kW
20 | 4 | Performance data (cont) | 6 | 2 | 55.9 53.2 6.99
20 | 4 | Performance data (cont) | 6 | 3 | 63.4 45.4 7.26
20 | 4 | Performance data (cont) | 6 | 4 | 71.1 35.9 7.58
20 | 4 | Performance data (cont) | 6 | 5 | 59.0 59.0 7.13
20 | 4 | Performance data (cont) | 6 | 6 | 65.4 50.6 7.39
20 | 4 | Performance data (cont) | 6 | 7 | 73.2 39.0 7.71
20 | 4 | Performance data (cont) | 6 | 8 | 59.7 59.7 7.17
20 | 4 | Performance data (cont) | 6 | 9 | 65.6 51.6 7.41
20 | 4 | Performance data (cont) | 6 | 10 | 73.5 39.6 7.72
20 | 4 | Performance data (cont) | 6 | 11 | 62.5 62.7 7.34
20 | 4 | Performance data (cont) | 6 | 12 | 66.8 56.8 7.49
20 | 4 | Performance data (cont) | 7 | 1 | TC SHC kW
20 | 4 | Performance data (cont) | 7 | 2 | 51.1 50.4 7.37
20 | 4 | Performance data (cont) | 7 | 3 | 58.4 43.5 7.63
20 | 4 | Performance data (cont) | 7 | 4 | 65.8 34.1 7.95
20 | 4 | Performance data (cont) | 7 | 5 | 55.1 55.0 7.54
20 | 4 | Performance data (cont) | 7 | 6 | 60.0 48.6 7.75
20 | 4 | Performance data (cont) | 7 | 7 | 67.7 37.3 8.08
20 | 4 | Performance data (cont) | 7 | 8 | 55.8 55.8 7.58
20 | 4 | Performance data (cont) | 7 | 9 | 60.3 49.8 6.77
20 | 4 | Performance data (cont) | 7 | 10 | 57.9 37.9 8.10
20 | 4 | Performance data (cont) | 7 | 11 | 58.7 58.6 7.75
20 | 4 | Performance data (cont) | 7 | 12 | 61.3 54.8 7.87
20 | 5 | Performance data (cont) | 1 | 1 | 2000/0.07
20 | 5 | Performance data (cont) | 1 | 2 | 2500/.08
20 | 5 | Performance data (cont) | 1 | 3 | 3000/0.10
20 | 6 | Performance data (cont) | 1 | 2 | 62
20 | 6 | Performance data (cont) | 1 | 3 | 67
20 | 6 | Performance data (cont) | 1 | 4 | 72
20 | 6 | Performance data (cont) | 1 | 5 | 62
20 | 6 | Performance data (cont) | 1 | 6 | 67
20 | 6 | Performance data (cont) | 1 | 7 | 72
20 | 6 | Performance data (cont) | 1 | 8 | 62
20 | 6 | Performance data (cont) | 1 | 9 | 67
20 | 6 | Performance data (cont) | 1 | 10 | 72
20 | 6 | Performance data (cont) | 1 | 11 | 62
20 | 6 | Performance data (cont) | 1 | 12 | 67
20 | 6 | Performance data (cont) | 2 | 1 | TC SHC kW
20 | 6 | Performance data (cont) | 2 | 2 | 79.2 65.7 6.44
20 | 6 | Performance data (cont) | 2 | 3 | 90.1 56.4 6.56
20 | 6 | Performance data (cont) | 2 | 4 | 99.5 46.2 6.68
20 | 6 | Performance data (cont) | 2 | 5 | 85.0 74.9 6.76
20 | 6 | Performance data (cont) | 2 | 6 | 95.2 62.5 6.93
20 | 6 | Performance data (cont) | 2 | 7 | 103.7 49.2 7.06
20 | 6 | Performance data (cont) | 2 | 8 | 88.9 81.9 7.12
20 | 6 | Performance data (cont) | 2 | 9 | 98.5 67.3 7.39
20 | 6 | Performance data (cont) | 2 | 10 | 106.4 51.4 7.49
20 | 6 | Performance data (cont) | 2 | 11 | 92.3 86.0 7.56
20 | 6 | Performance data (cont) | 2 | 12 | 100.9 71.2 7.93
20 | 6 | Performance data (cont) | 3 | 1 | TC SHC kW
20 | 6 | Performance data (cont) | 3 | 2 | 74.6 63.7 6.85
20 | 6 | Performance data (cont) | 3 | 3 | 85.8 54.8 7.06
20 | 6 | Performance data (cont) | 3 | 4 | 96.0 44.9 7.21
20 | 6 | Performance data (cont) | 3 | 5 | 79.4 72.2 7.25
20 | 6 | Performance data (cont) | 3 | 6 | 90.6 60.8 7.46
20 | 6 | Performance data (cont) | 3 | 7 | 100.2 48.1 7.59
20 | 6 | Performance data (cont) | 3 | 8 | 84.4 78.9 7.59
20 | 6 | Performance data (cont) | 3 | 9 | 94.3 66.0 7.90
20 | 6 | Performance data (cont) | 3 | 10 | 103.0 50.5 8.04
20 | 6 | Performance data (cont) | 3 | 11 | 88.3 83.9 8.01
20 | 6 | Performance data (cont) | 3 | 12 | 96.7 70.3 8.45
20 | 6 | Performance data (cont) | 4 | 1 | TC SHC kW
20 | 6 | Performance data (cont) | 4 | 2 | 70.2 61.6 7.26
20 | 6 | Performance data (cont) | 4 | 3 | 80.4 52.5 7.58
20 | 6 | Performance data (cont) | 4 | 4 | 91.4 43.2 7.75
20 | 6 | Performance data (cont) | 4 | 5 | 74.7 69.6 7.62
20 | 6 | Performance data (cont) | 4 | 6 | 82.9 59.2 7.98
20 | 6 | Performance data (cont) | 4 | 7 | 96.1 46.8 8.15
20 | 6 | Performance data (cont) | 4 | 8 | 79.1 75.3 8.08
20 | 6 | Performance data (cont) | 4 | 9 | 84.1 64.4 8.43
20 | 6 | Performance data (cont) | 4 | 10 | 98.9 49.3 8.60
20 | 6 | Performance data (cont) | 4 | 11 | 84.5 80.1 8.53
20 | 6 | Performance data (cont) | 4 | 12 | 91.5 68.7 8.99
20 | 6 | Performance data (cont) | 5 | 1 | TC SHC kW
20 | 6 | Performance data (cont) | 5 | 2 | 65.5 59.3 7.64
20 | 6 | Performance data (cont) | 5 | 3 | 75.6 50.5 8.05
20 | 6 | Performance data (cont) | 5 | 4 | 86.8 41.6 8.28
20 | 6 | Performance data (cont) | 5 | 5 | 70.4 55.4 8.03
20 | 6 | Performance data (cont) | 5 | 6 | 79.9 56.7 8.50
20 | 6 | Performance data (cont) | 5 | 7 | 91.0 45.0 8.69
20 | 6 | Performance data (cont) | 5 | 8 | 75.1 72.2 8.50
20 | 6 | Performance data (cont) | 5 | 9 | 83.0 61.8 8.98
20 | 6 | Performance data (cont) | 5 | 10 | 93.9 47.7 9.16
20 | 6 | Performance data (cont) | 5 | 11 | 79.3 75.0 9.07
20 | 6 | Performance data (cont) | 5 | 12 | 85.9 67.0 9.48
20 | 6 | Performance data (cont) | 6 | 1 | TC SHC kW
20 | 6 | Performance data (cont) | 6 | 2 | 60.7 56.5 8.01
20 | 6 | Performance data (cont) | 6 | 3 | 70.5 48.5 8.47
20 | 6 | Performance data (cont) | 6 | 4 | 81.7 39.8 8.81
20 | 6 | Performance data (cont) | 6 | 5 | 66.0 63.5 8.45
20 | 6 | Performance data (cont) | 6 | 6 | 74.4 54.5 8.96
20 | 6 | Performance data (cont) | 6 | 7 | 85.6 43.2 9.21
20 | 6 | Performance data (cont) | 6 | 8 | 70.9 68.0 8.96
20 | 6 | Performance data (cont) | 6 | 9 | 77.3 59.8 9.44
20 | 6 | Performance data (cont) | 6 | 10 | 88.4 45.9 9.69
20 | 6 | Performance data (cont) | 6 | 11 | 75.0 70.6 9.57
20 | 6 | Performance data (cont) | 6 | 12 | 79.5 64.3 10.00
20 | 6 | Performance data (cont) | 7 | 1 | TC SHC kW
20 | 6 | Performance data (cont) | 7 | 2 | 45.4 53.6 8.43
20 | 6 | Performance data (cont) | 7 | 3 | 65.1 46.3 8.90
20 | 6 | Performance data (cont) | 7 | 4 | 75.7 37.5 9.35
20 | 6 | Performance data (cont) | 7 | 5 | 61.8 60.0 8.88
20 | 6 | Performance data (cont) | 7 | 6 | 68.7 52.4 9.39
20 | 6 | Performance data (cont) | 7 | 7 | 79.9 41.3 9.77
20 | 6 | Performance data (cont) | 7 | 8 | 66.6 63.7 9.43
20 | 6 | Performance data (cont) | 7 | 9 | 71.3 57.6 9.88
20 | 6 | Performance data (cont) | 7 | 10 | 82.6 44.0 10.26
20 | 6 | Performance data (cont) | 7 | 11 | 70.6 66.2 10.06
20 | 6 | Performance data (cont) | 7 | 12 | 73.3 61.9 10.41
21 | 1 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 1 | 2500/0.09
21 | 1 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 2 | 3200/0.105
21 | 1 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 3 | 3800/0.12
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 2 | 62
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 3 | 67
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 4 | 72
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 5 | 62
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 6 | 67
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 7 | 72
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 8 | 62
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 9 | 67
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 10 | 72
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 11 | 62
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 12 | 67
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 2 | 1 | TC SHC kW
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 2 | 2 | 95.1 77.4 7.39
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 2 | 3 | 108.3 64.2 7.69
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 2 | 4 | 116.7 77.2 7.83
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 2 | 5 | 104.5 87.6 7.55
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 2 | 6 | 112.8 70.1 7.74
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 2 | 7 | 121.4 82.0 8.00
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 2 | 8 | 106.2 101.9 7.5
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 2 | 9 | 114.9 74.6 7.81
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 2 | 10 | 124.4 84.7 8.10
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 2 | 11 | 107.0 95.0 7.56
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 2 | 12 | 115.8 75.9 7.84
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 3 | 1 | TC SHC kW
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 3 | 2 | 88.9 79.9 7.91
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 3 | 3 | 102.3 69.3 8.24
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 3 | 4 | 112.0 55.1 8.42
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 3 | 5 | 98.5 93.5 8.08
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 3 | 6 | 108.3 77.7 8.34
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 3 | 7 | 116.9 60.0 8.60
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 3 | 8 | 101.8 100.3 8.10
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 3 | 9 | 110.3 83.4 8.39
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 3 | 10 | 119.2 63.7 8.69
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 3 | 11 | 102.7 102.2 8.15
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 3 | 12 | 110.8 85.1 8.41
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 4 | 1 | TC SHC kW
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 4 | 2 | 81.8 76.4 8.64
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 4 | 3 | 94.7 66.2 8.94
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 4 | 4 | 107.2 53.8 8.85
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 4 | 5 | 91.2 89.5 8.77
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 4 | 6 | 102.5 76.0 9.08
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 4 | 7 | 110.9 58.1 8.96
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 4 | 8 | 96.8 96.7 8.8
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 4 | 9 | 104.4 82.1 9.15
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 4 | 10 | 113.7 61.4 9.03
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 4 | 11 | 98.0 98.0 8.91
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 4 | 12 | 105.0 83.9 9.17
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 5 | 1 | TC SHC kW
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 5 | 2 | 74.2 72.1 9.06
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 5 | 3 | 86.4 62.8 9.42
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 5 | 4 | 101.8 51.8 9.74
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 5 | 5 | 83.4 83.4 9.26
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 5 | 6 | 95.2 73.4 9.56
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 5 | 7 | 105.3 56.9 9.88
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 5 | 8 | 89.7 89.7 9.4
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 5 | 9 | 98.2 80.5 9.65
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 5 | 10 | 107.6 60.8 9.96
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 5 | 11 | 91.3 91.3 9.48
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 5 | 12 | 98.7 82.6 9.66
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 6 | 1 | TC SHC kW
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 6 | 2 | 67.4 67.3 9.71
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 6 | 3 | 77.2 59.1 10.04
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 6 | 4 | 94.2 49.5 10.42
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 6 | 5 | 75.6 75.6 9.97
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 6 | 6 | 83.8 68.9 10.19
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 6 | 7 | 99.0 55.1 10.59
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 6 | 8 | 81.3 81.2 10.1
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 6 | 9 | 87.4 76.3 10.28
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 6 | 10 | 100.6 59.0 10.66
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 6 | 11 | 82.8 82.7 10.19
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 6 | 12 | 88.4 78.7 10.31
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 7 | 1 | TC SHC kW
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 7 | 2 | 63.2 63.2 10.37
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 7 | 3 | 69.2 56.0 10.68
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 7 | 4 | 84.4 46.0 11.09
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 7 | 5 | 68.5 68.5 10.69
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 7 | 6 | 71.8 64.3 10.85
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 7 | 7 | 88.8 51.9 11.27
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 7 | 8 | 73.1 73.0 10.9
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 7 | 9 | 75.0 70.9 10.95
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 7 | 10 | 92.3 56.9 11.37
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 7 | 11 | 74.2 74.2 10.93
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 7 | 12 | 76.0 73.0 10.97
21 | 3 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 1 | 3150/0.13
21 | 3 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 2 | 4200/0.17
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 2 | 62
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 3 | 67
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 4 | 72
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 5 | 62
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 6 | 67
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 7 | 72
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 8 | 62
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 9 | 67
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 2 | 1 | TC SHC kW
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 2 | 2 | 125.1 107.5 9.48
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 2 | 3 | 137.3 90.6 9.60
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 2 | 4 | 147.5 71.7 9.69
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 2 | 5 | 133.0 125.8 9.58
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 2 | 6 | 143.5 101.9 9.67
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 2 | 7 | 154.1 78.7 9.79
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 2 | 8 | 135.1 134.0 9.59
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 2 | 9 | 145.6 109.7 9.69
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 3 | 1 | TC SHC kW
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 3 | 2 | 115.4 103.1 10.15
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 3 | 3 | 129.6 87.7 10.33
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 3 | 4 | 140.9 69.8 10.49
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 3 | 5 | 124.4 120.8 10.29
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 3 | 6 | 135.9 99.8 10.43
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 3 | 7 | 147.3 77.0 10.61
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 3 | 8 | 128.9 128.3 10.34
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 3 | 9 | 138.6 108.6 10.48
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 4 | 1 | TC SHC kW
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 4 | 2 | 105.5 98.9 10.83
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 4 | 3 | 122.0 84.8 11.06
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 4 | 4 | 134.4 67.8 11.30
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 4 | 5 | 115.8 115.7 11.01
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 4 | 6 | 128.2 97.8 11.20
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 4 | 7 | 140.4 75.3 11.41
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 4 | 8 | 122.7 122.7 11.11
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 4 | 9 | 131.5 107.6 11.27
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 5 | 1 | TC SHC kW
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 5 | 2 | 94.1 92.7 11.54
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 5 | 3 | 112.2 81.2 11.83
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 5 | 4 | 126.9 65.3 12.10
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 5 | 5 | 106.5 106.5 11.76
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 5 | 6 | 118.9 94.8 11.98
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 5 | 7 | 132.4 73.2 12.22
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 5 | 8 | 115.2 115.2 11.92
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 5 | 9 | 122.6 105.6 12.06
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 6 | 1 | TC SHC kW
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 6 | 2 | 86.9 86.8 12.26
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 6 | 3 | 100.4 76.4 12.55
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 6 | 4 | 117.9 62.5 12.91
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 6 | 5 | 96.5 96.5 12.58
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 6 | 6 | 105.3 89.8 12.74
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 6 | 7 | 123.7 70.5 13.07
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 6 | 8 | 104.6 104.6 12.73
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 6 | 9 | 109.2 100.4 12.83
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 7 | 1 | TC SHC kW
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 7 | 2 | 79.9 79.9 13.00
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 7 | 3 | 88.5 71.7 13.29
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 7 | 4 | 108.8 59.6 13.72
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 7 | 5 | 86.4 86.3 13.40
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 7 | 6 | 91.7 84.8 13.49
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 7 | 7 | 115.0 67.8 13.91
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 7 | 8 | 94.1 99.1 13.55
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 7 | 9 | 96.0 94.6 13.62
22 | 1 | Performance data (cont) | 1 | 1 | 25
22 | 1 | Performance data (cont) | 1 | 3 | 50
22 | 1 | Performance data (cont) | 1 | 5 | 100
22 | 1 | Performance data (cont) | 1 | 7 | 150
22 | 1 | Performance data (cont) | 1 | 9 | 200
22 | 1 | Performance data (cont) | 1 | 11 | 250
22 | 1 | Performance data (cont) | 1 | 13 | 300
22 | 1 | Performance data (cont) | 1 | 15 | 350
22 | 1 | Performance data (cont) | 2 | 1 | R/s
22 | 1 | Performance data (cont) | 2 | 2 | kW
22 | 1 | Performance data (cont) | 2 | 3 | R/s
22 | 1 | Performance data (cont) | 2 | 4 | kW
22 | 1 | Performance data (cont) | 2 | 5 | R/s
22 | 1 | Performance data (cont) | 2 | 6 | kW
22 | 1 | Performance data (cont) | 2 | 7 | R/s
22 | 1 | Performance data (cont) | 2 | 8 | kW
22 | 1 | Performance data (cont) | 2 | 9 | R/s
22 | 1 | Performance data (cont) | 2 | 10 | kW
22 | 1 | Performance data (cont) | 2 | 11 | R/s
22 | 1 | Performance data (cont) | 2 | 12 | kW
22 | 1 | Performance data (cont) | 2 | 13 | R/s
22 | 1 | Performance data (cont) | 2 | 14 | kW
22 | 1 | Performance data (cont) | 2 | 15 | R/s
22 | 1 | Performance data (cont) | 2 | 16 | kW
22 | 1 | Performance data (cont) | 2 | 17 | R/s
22 | 1 | Performance data (cont) | 3 | 1 | 12.1 12.8 13.5 14.2 14.9 15.7 16.4 17.2 18.0 18.7 19.4
22 | 1 | Performance data (cont) | 3 | 2 | 0.30 0.36 0.42 0.56 0.63 0.72 0.81 0.92 1.03 1.17 1.23
22 | 1 | Performance data (cont) | 3 | 3 | 13.1 13.7 14.4 15.1 15.8 16.5 17.2 17.9 18.6 19.2 19.8
22 | 1 | Performance data (cont) | 3 | 4 | 0.36 0.42 0.49 0.61 0.70 0.78 0.88 0.99 1.10 1.23 1.36
22 | 1 | Performance data (cont) | 3 | 5 | 14.8 15.5 16.1 16.7 17.3 17.9 18.6 19.2 19.9 20.6 21.3
22 | 1 | Performance data (cont) | 3 | 6 | 0.48 0.56 0.63 0.74 0.82 0.91 1.02 1.13 1.26 1.41 1.55
22 | 1 | Performance data (cont) | 3 | 7 | 16.4 17.0 17.5 18.1 18.7 19.3 19.9 20.6 21.2 21.8 22.4
22 | 1 | Performance data (cont) | 3 | 8 | 0.61 0.68 0.77 0.85 0.95 1.06 1.18 1.30 1.44 1.58 1.72
22 | 1 | Performance data (cont) | 3 | 9 | 17.8 18.4 18.9 19.4 19.9 20.5 21.1 21.7 22.3 23.0 23.6
22 | 1 | Performance data (cont) | 3 | 10 | 0.75 0.84 0.93 1.00 1.10 1.21 1.34 1.48 1.63 1.78 1.92
22 | 1 | Performance data (cont) | 3 | 11 | 18.7 19.5 20.1 20.6 21.1 21.7 22.2 22.8 23.4 24.0 24.6
22 | 1 | Performance data (cont) | 3 | 12 | 0.85 0.98 1.09 1.15 1.26 1.37 1.50 1.64 1.79 1.97 2.12
22 | 1 | Performance data (cont) | 3 | 13 | 18.7 20.1 21.1 21.7 22.2 22.8 23.3 23.8 24.4
22 | 1 | Performance data (cont) | 3 | 14 | 0.83 1.05 1.22 1.31 1.42 1.55 1.69 1.83 1.98
22 | 1 | Performance data (cont) | 3 | 15 | 17.8 20.0 21.5 22.9 23.3 23.8 24.3 24.9
22 | 1 | Performance data (cont) | 3 | 16 | 0.67 1.23 1.28 1.50 1.62 1.73 1.86 2.01
22 | 1 | Performance data (cont) | 3 | 17 | 16.0 19.1 21.3 23.9 24.4 24.8 25.2
22 | 1 | Performance data (cont) | 4 | 17 | 25.7
22 | 1 | Performance data (cont) | 4 | 18 | 2.21
22 | 1 | Performance data (cont) | 5 | 15 | 25.4
22 | 1 | Performance data (cont) | 5 | 16 | 2.18
22 | 1 | Performance data (cont) | 5 | 17 | 26.3
22 | 1 | Performance data (cont) | 5 | 18 | 2.38
22 | 1 | Performance data (cont) | 6 | 13 | 24.9
22 | 1 | Performance data (cont) | 6 | 14 | 2.14
22 | 1 | Performance data (cont) | 6 | 15 | 25.9
22 | 1 | Performance data (cont) | 6 | 16 | 2.34
22 | 1 | Performance data (cont) | 6 | 17 | — —
22 | 1 | Performance data (cont) | 7 | 13 | 25.5
22 | 1 | Performance data (cont) | 7 | 14 | 2.29
22 | 1 | Performance data (cont) | 7 | 15
22 | 1 | Performance data (cont) | 7 | 16
22 | 2 | Performance data (cont) | 1 | 1 | 50
22 | 2 | Performance data (cont) | 1 | 3 | 100
22 | 2 | Performance data (cont) | 1 | 5 | 150
22 | 2 | Performance data (cont) | 1 | 7 | 200
22 | 2 | Performance data (cont) | 1 | 9 | 250
22 | 2 | Performance data (cont) | 1 | 11 | 300
22 | 2 | Performance data (cont) | 1 | 13 | 350
22 | 2 | Performance data (cont) | 1 | 15 | 400
22 | 2 | Performance data (cont) | 1 | 17 | 450
22 | 2 | Performance data (cont) | 2 | 1 | R/s
22 | 2 | Performance data (cont) | 2 | 2 | kW
22 | 2 | Performance data (cont) | 2 | 3 | R/s
22 | 2 | Performance data (cont) | 2 | 4 | kW
22 | 2 | Performance data (cont) | 2 | 5 | R/s
22 | 2 | Performance data (cont) | 2 | 6 | kW
22 | 2 | Performance data (cont) | 2 | 7 | R/s
22 | 2 | Performance data (cont) | 2 | 8 | kW
22 | 2 | Performance data (cont) | 2 | 9 | R/s
22 | 2 | Performance data (cont) | 2 | 10 | kW
22 | 2 | Performance data (cont) | 2 | 11 | R/s
22 | 2 | Performance data (cont) | 2 | 12 | kW
22 | 2 | Performance data (cont) | 2 | 13 | R/s
22 | 2 | Performance data (cont) | 2 | 14 | kW
22 | 2 | Performance data (cont) | 2 | 15 | R/s
22 | 2 | Performance data (cont) | 2 | 16 | kW
22 | 2 | Performance data (cont) | 2 | 17 | R/s
22 | 2 | Performance data (cont) | 2 | 18 | kW
22 | 2 | Performance data (cont) | 2 | 19 | R/s
22 | 2 | Performance data (cont) | 3 | 1 | 7.0 7.5 8.1 8.7 9.3 9.8 10.4 11.0
22 | 2 | Performance data (cont) | 3 | 2 | 0.27 0.37 0.47 0.57 0.67 0.80 0.94 1.11
22 | 2 | Performance data (cont) | 3 | 3 | 9.0 9.3 9.7 10.1 10.5 11.0 11.5 12.0
22 | 2 | Performance data (cont) | 3 | 4 | 0.45 0.55 0.65 0.75 0.85 0.99 1.13 1.31
22 | 2 | Performance data (cont) | 3 | 5 | 9.6 10.1 10.6 11.1 11.6 12.1 12.6 13.0
22 | 2 | Performance data (cont) | 3 | 6 | 0.53 0.66 0.79 0.92 1.05 1.21 1.38 1.58
22 | 2 | Performance data (cont) | 3 | 7 | 11.0 11.4 11.8 12.2 12.6 13.0 13.5 13.9
22 | 2 | Performance data (cont) | 3 | 8 | 0.70 0.84 0.98 1.12 1.26 1.43 1.63 1.85
22 | 2 | Performance data (cont) | 3 | 9 | 12.0 12.3 12.7 13.1 13.5 13.9 14.3 14.7
22 | 2 | Performance data (cont) | 3 | 10 | 1.86 1.02 1.18 1.34 1.50 1.67 1.87 2.11
22 | 2 | Performance data (cont) | 3 | 11 | 13.1 13.4 13.7 14.0 14.3 14.7
22 | 2 | Performance data (cont) | 3 | 12 | 1.03 1.19 1.37 1.55 1.73 1.93
22 | 2 | Performance data (cont) | 3 | 13 | 13.9 14.2 14.5 14.8 15.1
22 | 2 | Performance data (cont) | 3 | 14 | 1.25 1.43 1.61 1.79 1.97
22 | 2 | Performance data (cont) | 3 | 15 | 15.0 15.3 15.5 15.7
22 | 2 | Performance data (cont) | 3 | 16 | 1.74 1.86 1.98 2.10
22 | 2 | Performance data (cont) | 3 | 17 | 15.5 15.8
22 | 2 | Performance data (cont) | 3 | 18 | 1.96 2.10
22 | 2 | Performance data (cont) | 3 | 19 | 16.6
22 | 2 | Performance data (cont) | 3 | 20 | 2.45
22 | 2 | Performance data (cont) | 4 | 19 | 16.8
22 | 2 | Performance data (cont) | 4 | 20 | 2.55
22 | 2 | Performance data (cont) | 5 | 17 | 16.1
22 | 2 | Performance data (cont) | 5 | 18 | 2.24
22 | 2 | Performance data (cont) | 5 | 19 | 17
22 | 2 | Performance data (cont) | 5 | 20 | 2.65
22 | 2 | Performance data (cont) | 6 | 17 | 16.4
22 | 2 | Performance data (cont) | 6 | 18 | 2.38
22 | 2 | Performance data (cont) | 6 | 19 | 17.2
22 | 2 | Performance data (cont) | 6 | 20 | 2.75
22 | 2 | Performance data (cont) | 7 | 15 | 15.9
22 | 2 | Performance data (cont) | 7 | 16 | 2.22
22 | 2 | Performance data (cont) | 7 | 17 | 16.7
22 | 2 | Performance data (cont) | 7 | 18 | 2.52
22 | 2 | Performance data (cont) | 7 | 19 | 17.4
22 | 2 | Performance data (cont) | 7 | 20 | 2.85
22 | 2 | Performance data (cont) | 8 | 13 | 15.5
22 | 2 | Performance data (cont) | 8 | 14 | 2.18
22 | 2 | Performance data (cont) | 8 | 15 | 16.2
22 | 2 | Performance data (cont) | 8 | 16 | 2.34
22 | 2 | Performance data (cont) | 8 | 17 | 16.9
22 | 2 | Performance data (cont) | 8 | 18 | 2.69
22 | 2 | Performance data (cont) | 8 | 19 | 17.6
22 | 2 | Performance data (cont) | 8 | 20 | 2.97
22 | 2 | Performance data (cont) | 9 | 11 | 15.1
22 | 2 | Performance data (cont) | 9 | 12 | 2.13
22 | 2 | Performance data (cont) | 9 | 13 | 15.9
22 | 2 | Performance data (cont) | 9 | 14 | 2.41
22 | 2 | Performance data (cont) | 9 | 15 | 16.6
22 | 2 | Performance data (cont) | 9 | 16 | 2.66
22 | 2 | Performance data (cont) | 9 | 17 | 17.3
22 | 2 | Performance data (cont) | 9 | 18 | 2.92
22 | 2 | Performance data (cont) | 9 | 19 | — —
22 | 2 | Performance data (cont) | 10 | 11 | 15.5
22 | 2 | Performance data (cont) | 10 | 12 | 2.36
22 | 2 | Performance data (cont) | 10 | 13 | 16.3
22 | 2 | Performance data (cont) | 10 | 14 | 2.64
22 | 2 | Performance data (cont) | 10 | 15 | 17
22 | 2 | Performance data (cont) | 10 | 16 | 2.91
22 | 2 | Performance data (cont) | 10 | 17
22 | 2 | Performance data (cont) | 10 | 18
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 1 | 1 | 50
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 1 | 3 | 100
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 1 | 5 | 150
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 1 | 7 | 200
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 1 | 9 | 250
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 1 | 11 | 300
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 1 | 13 | 350
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 1 | 15 | 400
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 1 | 17 | 450
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 1 | R/s
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 2 | kW
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 3 | R/s
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 4 | kW
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 5 | R/s
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 6 | kW
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 7 | R/s
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 8 | kW
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 9 | R/s
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 10 | kW
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 11 | R/s
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 12 | kW
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 13 | R/s
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 14 | kW
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 15 | R/s
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 16 | kW
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 17 | R/s
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 18 | kW
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 19 | R/s
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 1 | 7.6 7.9 8.2 8.4 8.8 9.2 9.7 10.2 10.6 11.1
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 2 | 0.36 0.39 0.42 0.56 0.66 0.74 0.85 0.96 1.09 1.24
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 3 | 9.2 9.3 9.5 9.6 10.0 10.4 10.8 11.2 11.7 12.1
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 4 | 0.46 0.51 0.55 0.78 0.86 0.95 1.07 1.19 1.34 1.49
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 5 | 10.2 10.4 10.6 10.8 11.1 11.5 11.8 12.2 12.6 13.0
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 6 | 0.56 0.63 0.69 0.88 0.98 1.09 1.22 1.35 1.51 1.67
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 7 | 11.3 11.4 11.5 11.7 12.0 12.4 12.8 13.1 13.5 13.9
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 8 | 0.70 0.75 0.80 0.96 1.10 1.23 1.37 1.51 1.67 1.86
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 9 | 12.7 12.8 12.9 12.6 12.9 13.2 13.6 13.9 14.3 14.7
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 10 | 0.74 0.86 1.92 1.09 1.22 1.35 1.49 1.66 1.85 2.04
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 11 | 12.9 13.0 13.1 13.3 13.7 14.0 14.4 14.7 15.0
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 12 | 0.80 0.90 1.02 1.18 1.33 1.49 1.65 1.81 2.01
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 13 | 13.6 13.9 14.2 14.3 14.5 14.8 15.1 15.4
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 14 | 0.90 1.02 1.14 1.34 1.47 1.57 1.79 1.98
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 15 | 14.4 14.6 14.8 15.1 15.4 15.6 15.8
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 16 | 1.09 1.13 1.38 1.58 1.67 1.77 1.94
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 17 | 15.2 15.4 15.6 15.9 16.2 16.4 16.5
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 18 | 1.20 1.38 1.65 1.81 1.90 1.97 2.09
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 19 | 16.2 16.3 16.5 16.7 16.8
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 4 | 19 | 17.1
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 4 | 20 | 2.21
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 5 | 19 | 17.3
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 5 | 20 | 2.31
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 6 | 15 | 16.1
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 6 | 16 | 2.13
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 6 | 17 | 16.7
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 6 | 18 | 2.29
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 6 | 19 | 17.4
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 6 | 20 | 2.46
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 7 | 13 | 15.7
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 7 | 14 | 2.18
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 7 | 15 | 16.4
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 7 | 16 | 2.36
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 7 | 17 | 17.1
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 7 | 18 | 2.54
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 7 | 19 | 17.7
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 7 | 20 | 2.71
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 8 | 11 | 15.4
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 8 | 12 | 2.23
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 8 | 13 | 16.1
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 8 | 14 | 2.4
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 8 | 15 | 16.8
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 8 | 16 | 2.59
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 8 | 17 | 17.4
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 8 | 18 | 2.8
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 8 | 19 | 18
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 8 | 20 | 2.99
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 1 | 1 | 50
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 1 | 3 | 100
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 1 | 5 | 150
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 1 | 7 | 200
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 1 | 9 | 250
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 1 | 11 | 300
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 1 | 13 | 350
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 1 | 15 | 400
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 1 | 17 | 450
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 1 | R/s
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 2 | kW
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 3 | R/s
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 4 | kW
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 5 | R/s
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 6 | kW
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 7 | R/s
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 8 | kW
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 9 | R/s
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 10 | kW
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 11 | R/s
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 12 | kW
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 13 | R/s
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 14 | kW
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 15 | R/s
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 16 | kW
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 17 | R/s
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 18 | kW
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 19 | R/s
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 1 | 9.7 9.9 10.2 10.4 10.7 10.9 11.1 11.4 11.6 11.9 12.1 12.4 12.6 12.8 13.1 13.3 13.6 13.8
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 2 | 0.66 0.72 0.78 0.85 0.91 1.07 1.12 1.19 1.26 1.34 1.42 1.51 1.60 1.70 1.79 1.91 2.01 2.13
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 3 | 10.8 11.0 11.2 11.5 11.7 11.9 12.1 12.4 12.6 12.8 13.0 13.2 13.5 13.7 13.9 14.2 14.4 14.6
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 4 | 0.84 0.89 0.95 1.01 1.08 1.22 1.29 1.36 1.45 1.53 1.62 1.71 1.81 1.92 2.02 2.14 2.26 2.38
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 5 | 11.7 11.9 12.1 12.4 12.6 12.8 13.0 13.2 13.4 13.7 13.9 14.1 14.3 14.5 14.7 15.0 15.2 15.4
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 6 | 0.91 1.01 1.10 1.20 1.29 1.37 1.45 1.54 1.62 1.71 1.80 1.89 2.00 2.12 2.22 2.34 2.47 2.60
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 7 | 12.6 12.8 13.0 13.2 13.4 13.6 13.8 14.0 14.2 14.4 14.6 14.8 15.0 15.3 15.5 15.7 15.9 16.1
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 8 | 1.09 1.15 1.22 1.29 1.38 1.52 1.60 1.69 1.78 1.88 1.99 2.09 2.21 2.33 2.45 2.57 2.69 2.82
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 9 | 13.5 13.7 13.8 14.0 14.2 14.4 14.6 14.7 14.9 15.1 15.3 15.5 15.7 15.9 16.1 16.4 16.6 16.8
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 10 | 1.27 1.34 1.41 1.48 1.55 1.67 1.75 1.84 1.93 2.03 2.15 2.26 2.39 2.51 2.64 2.77 2.92 3.07
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 11 | 14.3 14.5 14.6 14.8 15.0 15.1 15.3 15.5 15.6 15.8 16.0 16.2 16.4 16.6 16.8 17.0 17.2 17.4
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 12 | 1.32 1.46 1.58 1.67 1.76 1.86 1.95 2.03 2.12 2.22 2.32 2.42 2.54 2.68 2.82 2.97 3.12 3.26
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 13 | 15.1 15.2 15.4 15.5 15.7 15.8 16.0 16.2 16.3 16.5 16.7 16.9 17.0 17.2 17.4 17.6 17.8
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 14 | 1.44 1.38 1.71 1.76 1.92 2.02 2.12 2.22 2.33 2.44 2.54 2.64 2.76 2.88 3.01 3.14 3.30
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 15 | 16.0 16.1 16.2 16.3 16.4 16.5 16.7 16.8 17.0 17.2 17.3 17.5 17.7 17.8 18.0
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 16 | 1.55 1.71 1.79 1.89 2.01 2.20 2.29 2.40 2.52 2.64 2.76 2.88 3.01 3.14 3.25
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 17 | 16.9 17.0 17.0 17.1 17.1 17.2 17.3 17.5 17.7 17.8 18.0 18.1 18.3
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 18 | 1.66 1.79 1.92 2.06 2.18 2.36 2.47 2.59 2.71 2.83 2.96 3.09 3.23
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 19 | 17.5 17.5 17.6 17.6 17.7 17.7 17.9 18.1 18.3 18.4 18.6 17.7
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 4 | 19 | 18.9
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 4 | 20 | 3.44
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 5 | 17 | 18.5
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 5 | 18 | 3.36
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 5 | 19 | 19.1
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 5 | 20 | 3.59
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 6 | 17 | 18.6
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 6 | 18 | 3.51
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 6 | 19 | 19.2
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 6 | 20 | 3.75
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 7 | 15 | 18.2
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 7 | 16 | 3.39
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 7 | 17 | 18.8
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 7 | 18 | 3.65
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 7 | 19 | 19.4
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 7 | 20 | 3.9
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 8 | 15 | 18.4
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 8 | 16 | 3.52
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 8 | 17 | 19
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 8 | 18 | 3.8
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 8 | 19 | 19.5
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 8 | 20 | 4.06
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 9 | 13 | 18
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 9 | 14 | 3.47
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 9 | 15 | 18.6
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 9 | 16 | 3.67
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 9 | 17 | 19.2
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 9 | 18 | 3.93
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 9 | 19 | 19.7
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 9 | 20 | 4.22
24 | 1 | Performance data (cont) | 1 | 1 | 25
24 | 1 | Performance data (cont) | 1 | 3 | 50
24 | 1 | Performance data (cont) | 1 | 5 | 100
24 | 1 | Performance data (cont) | 1 | 7 | 150
24 | 1 | Performance data (cont) | 1 | 9 | 200
24 | 1 | Performance data (cont) | 1 | 11 | 250
24 | 1 | Performance data (cont) | 1 | 13 | 300
24 | 1 | Performance data (cont) | 1 | 15 | 350
24 | 1 | Performance data (cont) | 2 | 1 | R/s
24 | 1 | Performance data (cont) | 2 | 2 | kW
24 | 1 | Performance data (cont) | 2 | 3 | R/s
24 | 1 | Performance data (cont) | 2 | 4 | kW
24 | 1 | Performance data (cont) | 2 | 5 | R/s
24 | 1 | Performance data (cont) | 2 | 6 | kW
24 | 1 | Performance data (cont) | 2 | 7 | R/s
24 | 1 | Performance data (cont) | 2 | 8 | kW
24 | 1 | Performance data (cont) | 2 | 9 | R/s
24 | 1 | Performance data (cont) | 2 | 10 | kW
24 | 1 | Performance data (cont) | 2 | 11 | R/s
24 | 1 | Performance data (cont) | 2 | 12 | kW
24 | 1 | Performance data (cont) | 2 | 13 | R/s
24 | 1 | Performance data (cont) | 2 | 14 | kW
24 | 1 | Performance data (cont) | 2 | 15 | R/s
24 | 1 | Performance data (cont) | 2 | 16 | kW
24 | 1 | Performance data (cont) | 2 | 17 | R/s
24 | 1 | Performance data (cont) | 3 | 1 | 10.8 11.5 12.1 12.8 13.4 14.1 14.7 15.4 16.1 16.8 17.5
24 | 1 | Performance data (cont) | 3 | 2 | 0.25 0.30 0.35 0.49 0.54 0.61 0.67 0.75 0.85 0.95 1.05
24 | 1 | Performance data (cont) | 3 | 3 | 12.0 12.5 13.1 13.7 14.3 14.9 15.5 16.1 16.7 17.4 18.1
24 | 1 | Performance data (cont) | 3 | 4 | 0.30 0.35 0.41 0.53 0.59 0.65 0.73 0.82 0.91 1.01 1.10
24 | 1 | Performance data (cont) | 3 | 5 | 13.9 14.4 14.9 15.4 15.9 16.5 17.0 17.6 18.2 18.7 19.6
24 | 1 | Performance data (cont) | 3 | 6 | 0.41 0.47 0.53 0.64 0.71 0.78 0.85 0.95 1.05 1.17 1.25
24 | 1 | Performance data (cont) | 3 | 7 | 15.6 16.1 16.5 17.0 17.5 17.9 18.4 18.9 19.5 20.0 20.5
24 | 1 | Performance data (cont) | 3 | 8 | 0.53 0.60 0.67 0.76 0.84 0.92 1.00 1.10 1.21 1.31 1.41
24 | 1 | Performance data (cont) | 3 | 9 | 17.0 17.5 17.9 18.3 18.8 19.3 19.8 20.3 20.8 21.2 21.8
24 | 1 | Performance data (cont) | 3 | 10 | 0.67 0.74 0.81 0.89 0.97 1.06 1.15 1.27 1.37 1.49 1.61
24 | 1 | Performance data (cont) | 3 | 11 | 18.4 18.8 19.2 19.6 20.0 20.5 21.0 21.5 22.0 22.4 22.8
24 | 1 | Performance data (cont) | 3 | 12 | 0.83 0.88 0.96 1.03 1.11 1.20 1.31 1.43 1.56 1.69 1.77
24 | 1 | Performance data (cont) | 3 | 13 | 19.8 20.1 20.4 20.8 21.3 21.7 22.1 22.5 23.0 23.5 24.1
24 | 1 | Performance data (cont) | 3 | 14 | 1.04 1.09 1.12 1.19 1.28 1.37 1.48 1.60 1.73 1.87 2.01
24 | 1 | Performance data (cont) | 3 | 15 | 21.2 21.5 21.7 21.9 22.3 22.8 23.2 23.6 24.0 24.5
24 | 1 | Performance data (cont) | 3 | 16 | 1.27 1.31 1.36 1.35 1.44 1.55 1.66 1.78 1.91 2.05
24 | 1 | Performance data (cont) | 3 | 17 | 21.9 22.3 22.6 23.0 23.4 23.8 24.2 24.6 25.1
24 | 1 | Performance data (cont) | 4 | 17 | 25.5
24 | 1 | Performance data (cont) | 4 | 18 | 2.23
24 | 1 | Performance data (cont) | 5 | 15 | 25
24 | 1 | Performance data (cont) | 5 | 16 | 2.2
24 | 1 | Performance data (cont) | 5 | 17 | 26
24 | 1 | Performance data (cont) | 5 | 18 | 2.39
24 | 2 | Performance data (cont) | 1 | 1 | 50
24 | 2 | Performance data (cont) | 1 | 3 | 100
24 | 2 | Performance data (cont) | 1 | 5 | 150
24 | 2 | Performance data (cont) | 1 | 7 | 200
24 | 2 | Performance data (cont) | 1 | 9 | 250
24 | 2 | Performance data (cont) | 1 | 11 | 300
24 | 2 | Performance data (cont) | 1 | 13 | 350
24 | 2 | Performance data (cont) | 1 | 15 | 400
24 | 2 | Performance data (cont) | 1 | 17 | 450
24 | 2 | Performance data (cont) | 2 | 1 | R/s
24 | 2 | Performance data (cont) | 2 | 2 | kW
24 | 2 | Performance data (cont) | 2 | 3 | R/s
24 | 2 | Performance data (cont) | 2 | 4 | kW
24 | 2 | Performance data (cont) | 2 | 5 | R/s
24 | 2 | Performance data (cont) | 2 | 6 | kW
24 | 2 | Performance data (cont) | 2 | 7 | R/s
24 | 2 | Performance data (cont) | 2 | 8 | kW
24 | 2 | Performance data (cont) | 2 | 9 | R/s
24 | 2 | Performance data (cont) | 2 | 10 | kW
24 | 2 | Performance data (cont) | 2 | 11 | R/s
24 | 2 | Performance data (cont) | 2 | 12 | kW
24 | 2 | Performance data (cont) | 2 | 13 | R/s
24 | 2 | Performance data (cont) | 2 | 14 | kW
24 | 2 | Performance data (cont) | 2 | 15 | R/s
24 | 2 | Performance data (cont) | 2 | 16 | kW
24 | 2 | Performance data (cont) | 2 | 17 | R/s
24 | 2 | Performance data (cont) | 2 | 18 | kW
24 | 2 | Performance data (cont) | 2 | 19 | R/s
24 | 2 | Performance data (cont) | 3 | 1 | 6.5 7.1 7.5 7.9 8.3 8.8 9.2 9.7
24 | 2 | Performance data (cont) | 3 | 2 | 0.29 0.36 0.43 0.50 0.57 0.66 0.76 0.88
24 | 2 | Performance data (cont) | 3 | 3 | 8.2 8.6 9.0 9.4 9.8 10.2 10.6 11.0
24 | 2 | Performance data (cont) | 3 | 4 | 0.35 0.45 0.55 0.65 0.75 0.85 0.97 1.10
24 | 2 | Performance data (cont) | 3 | 5 | 9.4 9.8 10.2 10.6 11.0 11.3 11.7 12.1
24 | 2 | Performance data (cont) | 3 | 6 | 0.53 0.62 0.73 0.84 0.95 1.06 1.19 1.34
24 | 2 | Performance data (cont) | 3 | 7 | 10.8 11.1 11.4 11.7 12.0 12.4 12.7 13.0
24 | 2 | Performance data (cont) | 3 | 8 | 0.71 0.81 0.92 1.03 1.14 1.29 1.45 1.60
24 | 2 | Performance data (cont) | 3 | 9 | 11.9 12.1 12.4 12.7 13.0 13.3 13.7 14.0
24 | 2 | Performance data (cont) | 3 | 10 | 0.86 0.95 1.09 1.23 1.37 1.52 1.69 1.88
24 | 2 | Performance data (cont) | 3 | 11 | 12.7 13.0 13.3 13.6 13.9 14.2 14.5
24 | 2 | Performance data (cont) | 3 | 12 | 1.10 1.23 1.36 1.49 1.62 1.77 1.93
24 | 2 | Performance data (cont) | 3 | 13 | 13.3 13.6 13.9 14.4 14.8 15.0
24 | 2 | Performance data (cont) | 3 | 14 | 1.31 1.45 1.59 1.73 1.87 2.04
24 | 2 | Performance data (cont) | 3 | 15 | 13.3 13.7 14.1 14.9
24 | 2 | Performance data (cont) | 3 | 16 | 1.55 1.70 1.85 2.00
24 | 2 | Performance data (cont) | 3 | 17 | 13.5 13.9 14.3
24 | 2 | Performance data (cont) | 3 | 18 | 1.80 1.95 2.11
24 | 2 | Performance data (cont) | 3 | 19 | 13.8
24 | 2 | Performance data (cont) | 4 | 19 | 14.2
24 | 2 | Performance data (cont) | 4 | 20 | 2.19
24 | 2 | Performance data (cont) | 5 | 19 | 14.6
24 | 2 | Performance data (cont) | 5 | 20 | 2.35
24 | 2 | Performance data (cont) | 6 | 17 | 15.1
24 | 2 | Performance data (cont) | 6 | 18 | 2.27
24 | 2 | Performance data (cont) | 6 | 19 | 15
24 | 2 | Performance data (cont) | 6 | 20 | 2.53
24 | 2 | Performance data (cont) | 7 | 15 | 15.5
24 | 2 | Performance data (cont) | 7 | 16 | 2.15
24 | 2 | Performance data (cont) | 7 | 17 | 16
24 | 2 | Performance data (cont) | 7 | 18 | 2.43
24 | 2 | Performance data (cont) | 7 | 19 | 16.4
24 | 2 | Performance data (cont) | 7 | 20 | 2.71
24 | 2 | Performance data (cont) | 8 | 15 | 15.8
24 | 2 | Performance data (cont) | 8 | 16 | 2.32
24 | 2 | Performance data (cont) | 8 | 17 | 16.5
24 | 2 | Performance data (cont) | 8 | 18 | 2.6
24 | 2 | Performance data (cont) | 8 | 19 | 17.1
24 | 2 | Performance data (cont) | 8 | 20 | 2.88
24 | 2 | Performance data (cont) | 9 | 13 | 15.3
24 | 2 | Performance data (cont) | 9 | 14 | 2.21
24 | 2 | Performance data (cont) | 9 | 15 | 16.1
24 | 2 | Performance data (cont) | 9 | 16 | 2.5
24 | 2 | Performance data (cont) | 9 | 17 | 16.9
24 | 2 | Performance data (cont) | 9 | 18 | 2.78
24 | 2 | Performance data (cont) | 9 | 19 | — —
24 | 2 | Performance data (cont) | 10 | 11 | 14.8
24 | 2 | Performance data (cont) | 10 | 12 | 2.14
24 | 2 | Performance data (cont) | 10 | 13 | 15.6
24 | 2 | Performance data (cont) | 10 | 14 | 2.41
24 | 2 | Performance data (cont) | 10 | 15 | 16.4
24 | 2 | Performance data (cont) | 10 | 16 | 2.7
24 | 2 | Performance data (cont) | 10 | 17
24 | 2 | Performance data (cont) | 10 | 18
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 1 | 50
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 3 | 100
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 5 | 150
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 7 | 200
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 9 | 250
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 11 | 300
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 13 | 350
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 15 | 400
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 17 | 450
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 1 | R/s
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 2 | kW
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 3 | R/s
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 4 | kW
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 5 | R/s
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 6 | kW
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 7 | R/s
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 8 | kW
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 9 | R/s
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 10 | kW
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 11 | R/s
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 12 | kW
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 13 | R/s
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 14 | kW
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 15 | R/s
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 16 | kW
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 17 | R/s
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 18 | kW
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 19 | R/s
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 1 | 7.3 7.4 7.6 7.6 8.0 8.4 8.8 9.1 9.5 9.9
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 2 | 0.30 0.35 0.39 0.56 0.66 0.74 0.85 0.96 1.09 1.24
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 3 | 8.6 8.7 8.8 8.9 9.3 9.6 10.0 10.3 10.7 11.0
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 4 | 0.43 0.46 0.49 0.67 0.78 0.87 0.96 1.06 1.18 1.31
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 5 | 9.8 9.9 10.0 10.2 10.5 10.7 11.1 11.3 11.7 12.0
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 6 | 0.47 0.58 0.69 0.83 0.91 0.99 1.10 1.22 1.34 1.48
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 7 | 10.8 11.0 11.1 11.1 11.4 11.8 12.1 12.3 12.6 12.9
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 8 | 0.60 0.72 0.77 0.91 1.03 1.14 1.25 1.37 1.51 1.66
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 9 | 11.8 11.9 12.0 12.1 12.4 12.7 12.9 13.2 13.5 13.8
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 10 | 0.72 0.80 0.88 1.05 1.16 1.28 1.40 1.53 1.68 1.84
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 11 | 12.8 12.9 13.0 13.1 13.3 13.5 13.8 14.0 14.3 14.6
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 12 | 0.85 0.86 0.87 1.21 1.30 1.42 1.55 1.69 1.86 2.04
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 13 | 13.6 13.7 13.8 13.9 14.1 14.3 14.5 14.8 15.0
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 14 | 0.90 0.96 1.02 1.22 1.41 1.57 1.70 1.86 2.03
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 15 | 13.6 13.8 13.9 14.0 14.6 15.1 15.3 15.5
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 16 | 0.95 1.02 1.08 0.79 1.25 1.67 1.88 2.02
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 17 | 14.2 14.4 14.6 15.0 15.4 15.7 16.0
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 18 | 0.98 1.08 1.20 1.43 1.64 1.83 2.00
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 19 | 14.4 14.7 15.0 15.6 16.0 16.4 16.7
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 4 | 17 | 16.3
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 4 | 18 | 2.23
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 4 | 19 | 17
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 4 | 20 | 2.36
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 5 | 15 | 15.8
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 5 | 16 | 2.21
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 5 | 17 | 16.4
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 5 | 18 | 2.4
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 5 | 19 | 17.2
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 5 | 20 | 2.62
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 6 | 13 | 15.3
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 6 | 14 | 2.21
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 6 | 15 | 16
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 6 | 16 | 2.42
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 6 | 17 | 16.7
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 6 | 18 | 2.61
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 6 | 19 | 17.3
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 6 | 20 | 2.82
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 1 | 50
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 3 | 100
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 5 | 150
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 7 | 200
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 9 | 250
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 11 | 300
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 13 | 350
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 15 | 400
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 17 | 450
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 1 | R/s
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 2 | kW
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 3 | R/s
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 4 | kW R/s
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 6 | kW
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 7 | R/s
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 8 | kW
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 9 | R/s
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 10 | kW
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 11 | R/s
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 12 | kW
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 13 | R/s
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 14 | kW
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 15 | R/s
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 16 | kW
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 17 | R/s
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 18 | kW
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 19 | R/s
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 1 | 9.0 9.2 9.4 9.7 9.9 10.1 10.4 10.6 10.8 11.1 11.3 11.6 11.9 12.0 12.4 12.6 12.9 13.2
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 2 | 0.58 0.62 0.67 0.73 0.79 0.94 1.01 1.07 1.13 1.21 1.29 1.36 1.45 1.54 1.64 1.75 1.85 1.95
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 3 | 10.2 10.4 10.6 10.8 11.0 11.2 11.4 11.6 11.8 12.0 12.1 12.3 12.5 12.7 12.9 13.1 13.3 13.5
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 4 | 0.73 0.79 0.84 0.89 0.96 1.11 1.17 1.22 1.29 1.35 1.43 1.51 1.58 1.67 1.76 1.85 1.95 2.06
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 5 | 11.3 11.5 11.7 11.9 12.1 12.2 12.4 12.5 12.7 12.9 13.1 13.2 13.4 13.6 13.8 14.0 14.2 14.4
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 6 | 0.88 0.94 1.01 1.08 1.14 1.26 1.33 1.40 1.46 1.55 1.63 1.71 1.81 1.89 1.99 2.08 2.19 2.29
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 7 | 12.1 12.3 12.5 12.7 12.9 13.0 13.3 13.5 13.7 13.8 14.0 14.1 14.3 14.5 14.6 14.8 15.0 15.2
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 8 | 1.00 1.06 1.14 1.21 1.29 1.42 1.51 1.59 1.68 1.76 1.84 1.92 2.00 2.09 2.19 2.30 2.42 2.54
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 9 | 13.2 13.2 13.3 13.5 13.6 13.9 14.0 14.2 14.4 14.5 14.7 14.9 15.1 15.3 15.5 15.6 15.8 16.0
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 10 | 1.21 1.24 1.28 1.35 1.44 1.56 1.64 1.72 1.81 1.91 2.01 2.12 2.23 2.34 2.45 2.56 2.65 2.77
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 11 | 14.2 14.3 14.4 14.5 14.6 14.7 14.8 15.0 15.1 15.3 15.4 15.6 15.8 15.9 16.1 16.3 16.5 16.7
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 12 | 1.24 1.29 1.38 1.48 1.64 1.75 1.81 1.89 1.98 2.07 2.17 2.28 2.39 2.51 2.64 2.77 2.91 3.04
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 13 | 15.1 15.1 15.2 15.3 15.4 15.5 15.6 15.7 15.8 16.0 16.2 16.3 16.5 16.6 16.8 16.9 17.1
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 14 | 1.28 1.41 1.54 1.67 1.82 1.94 2.02 2.10 2.19 2.27 2.36 2.47 2.58 2.69 2.82 2.94 3.08
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 15 | 16.0 16.0 16.1 16.1 16.2 16.2 16.3 16.5 16.6 16.7 16.8 17.0 17.1 17.3 17.4 17.6 17.7
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 16 | 1.44 1.59 1.73 1.86 1.94 2.12 2.21 2.32 2.40 2.51 2.60 2.70 2.80 2.90 3.02 3.14 3.29
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 17 | 16.5 16.6 16.6 16.7 16.8 16.9 17.0 17.2 17.3 17.4 17.5 17.6 17.8 17.9 18.1
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 18 | 1.68 1.81 1.94 2.02 2.13 2.29 2.40 2.51 2.60 2.71 2.82 2.93 3.04 3.16 3.28
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 19 | 17.3 17.3 17.4 17.4 17.5 17.4 17.6 17.8 18.0 18.1 18.2 18.3 18.4
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 4 | 19 | 18.6
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 4 | 20 | 3.41
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 5 | 19 | 18.7
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 5 | 20 | 3.55
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 6 | 17 | 18.2
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 6 | 18 | 3.4
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 6 | 19 | 18.8
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 6 | 20 | 3.67
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 7 | 17 | 18.4
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 7 | 18 | 3.51
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 7 | 19 | 19
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 7 | 20 | 3.8
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 8 | 13 | 17.3
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 8 | 14 | 3.23
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 8 | 15 | 17.9
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 8 | 16 | 3.44
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 8 | 17 | 18.5
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 8 | 18 | 3.65
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 8 | 19 | 19.1
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 8 | 20 | 3.92
26 | 1 | Performance data (cont) | 1 | 1 | 0.1
26 | 1 | Performance data (cont) | 1 | 3 | 0.2
26 | 1 | Performance data (cont) | 1 | 5 | 0.4
26 | 1 | Performance data (cont) | 1 | 7 | 0.6
26 | 1 | Performance data (cont) | 1 | 9 | 0.8
26 | 1 | Performance data (cont) | 1 | 11 | 1
26 | 1 | Performance data (cont) | 1 | 13 | 1.2
26 | 1 | Performance data (cont) | 1 | 15 | 1.4
26 | 1 | Performance data (cont) | 2 | 1 | Rpm
26 | 1 | Performance data (cont) | 2 | 2 | Watts
26 | 1 | Performance data (cont) | 2 | 3 | Rpm
26 | 1 | Performance data (cont) | 2 | 4 | Watts
26 | 1 | Performance data (cont) | 2 | 5 | Rpm
26 | 1 | Performance data (cont) | 2 | 6 | Watts
26 | 1 | Performance data (cont) | 2 | 7 | Rpm
26 | 1 | Performance data (cont) | 2 | 8 | Watts
26 | 1 | Performance data (cont) | 2 | 9 | Rpm
26 | 1 | Performance data (cont) | 2 | 10 | Watts
26 | 1 | Performance data (cont) | 2 | 11 | Rpm
26 | 1 | Performance data (cont) | 2 | 12 | Watts
26 | 1 | Performance data (cont) | 2 | 13 | Rpm
26 | 1 | Performance data (cont) | 2 | 14 | Watts
26 | 1 | Performance data (cont) | 2 | 15 | Rpm
26 | 1 | Performance data (cont) | 2 | 16 | Watts
26 | 1 | Performance data (cont) | 2 | 17 | Rpm
26 | 1 | Performance data (cont) | 2 | 18 | Watts
26 | 1 | Performance data (cont) | 3 | 1 | 731 772 814 852 894 936 978 1021 1064 1107 1150
26 | 1 | Performance data (cont) | 3 | 2 | 304 359 424 562 630 708 795 891 998 1114 1241
26 | 1 | Performance data (cont) | 3 | 3 | 789 826 865 905 945 984 1024 1064 1104 1145 1186
26 | 1 | Performance data (cont) | 3 | 4 | 368 424 497 615 692 771 859 956 1064 1182 1318
26 | 1 | Performance data (cont) | 3 | 5 | 895 930 964 1002 1037 1072 1108 1145 1183 1222 1262
26 | 1 | Performance data (cont) | 3 | 6 | 488 562 636 739 818 899 998 1097 1216 1353 1491
26 | 1 | Performance data (cont) | 3 | 7 | 990 1019 1050 1084 1119 1154 1190 1225 1260 1296 1331
26 | 1 | Performance data (cont) | 3 | 8 | 617 691 774 859 948 1047 1156 1275 1396 1534 1674
26 | 1 | Performance data (cont) | 3 | 9 | 1074 1105 1134 1163 1194 1226 1259 1294 1330 1365 1400
26 | 1 | Performance data (cont) | 3 | 10 | 764 847 930 998 1089 1190 1310 1439 1578 1718 1875
26 | 1 | Performance data (cont) | 3 | 11 | 1130 1174 1208 1235 1266 1297 1327 1359 1392 1426 1461
26 | 1 | Performance data (cont) | 3 | 12 | 875 985 1096 1156 1250 1361 1473 1604 1744 1901 2067
26 | 1 | Performance data (cont) | 3 | 13 | 1168 1213 1265 1303 1330 1362 1393 1423 1454 1485
26 | 1 | Performance data (cont) | 3 | 14 | 921 1078 1234 1318 1413 1534 1656 1779 1927 2084
26 | 1 | Performance data (cont) | 3 | 15 | 1250 1315 1348 1371 1396 1422 1452 1483
26 | 1 | Performance data (cont) | 3 | 16 | 1059 1197 1455 1499 1604 1718 1840 1980
26 | 1 | Performance data (cont) | 3 | 17 | 1345 1401 1421 1433 1460 1485 1510
26 | 1 | Performance data (cont) | 3 | 18 | 1216 1335 1639 1638 1796 1910 2041
26 | 1 | Performance data (cont) | 4 | 17 | 1538
26 | 1 | Performance data (cont) | 4 | 18 | 2171
26 | 1 | Performance data (cont) | 5 | 15 | 1515
26 | 1 | Performance data (cont) | 5 | 16 | 2128
26 | 1 | Performance data (cont) | 5 | 17 | 1569
26 | 1 | Performance data (cont) | 5 | 18 | 2326
26 | 1 | Performance data (cont) | 6 | 15 | 1544
26 | 1 | Performance data (cont) | 6 | 16 | 2283
26 | 1 | Performance data (cont) | 6 | 17 | 1601
26 | 1 | Performance data (cont) | 6 | 18 | 2459
26 | 1 | Performance data (cont) | 7 | 13 | 1518
26 | 1 | Performance data (cont) | 7 | 14 | 2249
26 | 1 | Performance data (cont) | 7 | 15 | 1575
26 | 1 | Performance data (cont) | 7 | 16 | 2445
26 | 1 | Performance data (cont) | 7 | 17
26 | 1 | Performance data (cont) | 7 | 18
26 | 2 | Performance data (cont) | 1 | 1 | 0.2
26 | 2 | Performance data (cont) | 1 | 3 | 0.4
26 | 2 | Performance data (cont) | 1 | 5 | 0.6
26 | 2 | Performance data (cont) | 1 | 7 | 0.8
26 | 2 | Performance data (cont) | 1 | 9 | 1
26 | 2 | Performance data (cont) | 1 | 11 | 1.2
26 | 2 | Performance data (cont) | 1 | 13 | 1.4
26 | 2 | Performance data (cont) | 1 | 15 | 1.6
26 | 2 | Performance data (cont) | 1 | 17 | 1.8
26 | 2 | Performance data (cont) | 2 | 1 | Rpm
26 | 2 | Performance data (cont) | 2 | 2 | Watts
26 | 2 | Performance data (cont) | 2 | 3 | Rpm
26 | 2 | Performance data (cont) | 2 | 4 | Watts
26 | 2 | Performance data (cont) | 2 | 5 | Rpm
26 | 2 | Performance data (cont) | 2 | 6 | Watts
26 | 2 | Performance data (cont) | 2 | 7 | Rpm
26 | 2 | Performance data (cont) | 2 | 8 | Watts
26 | 2 | Performance data (cont) | 2 | 9 | Rpm
26 | 2 | Performance data (cont) | 2 | 10 | Watts
26 | 2 | Performance data (cont) | 2 | 11 | Rpm
26 | 2 | Performance data (cont) | 2 | 12 | Watts
26 | 2 | Performance data (cont) | 2 | 13 | Rpm
26 | 2 | Performance data (cont) | 2 | 14 | Watts
26 | 2 | Performance data (cont) | 2 | 15 | Rpm
26 | 2 | Performance data (cont) | 2 | 16 | Watts
26 | 2 | Performance data (cont) | 2 | 17 | Rpm
26 | 2 | Performance data (cont) | 2 | 18 | Watts
26 | 2 | Performance data (cont) | 2 | 19 | Rpm
26 | 2 | Performance data (cont) | 3 | 1 | 466 473 488 503 511 518 534 549 557 565 581 597 613 629 646 662 679 696 712
26 | 2 | Performance data (cont) | 3 | 2 | 429 448 486 524 539 562 607 653 684 708 763 827 891 965 1039 1123 1207 1301 1396
26 | 2 | Performance data (cont) | 3 | 3 | 564 571 585 585 592 599 613 627 633 639 652 665 679 694 709 724 740 756 771
26 | 2 | Performance data (cont) | 3 | 4 | 567 590 637 684 708 731 787 835 867 891 948 1014 1081 1156 1241 1335 1430 1534 1639
26 | 2 | Performance data (cont) | 3 | 5 | 623 571 641 653 659 665 677 690 697 703 717 713 745 759 772 785 798 811 824
26 | 2 | Performance data (cont) | 3 | 6 | 731 755 803 851 875 899 965 1031 1064 1097 1173 1250 1335 1413 1508 1595 1691 1788 1892
26 | 2 | Performance data (cont) | 3 | 7 | 689 694 705 716 722 727 738 750 756 761 773 786 799 812 825 840 854 868
26 | 2 | Performance data (cont) | 3 | 8 | 894 923 981 1039 1072 1097 1165 1233 1267 1301 1378 1473 1560 1665 1761 1866 1980 2093
26 | 2 | Performance data (cont) | 3 | 9 | 745 750 761 772 778 783 794 805 811 816 827 839 850 862 875
26 | 2 | Performance data (cont) | 3 | 10 | 1041 1079 1156 1233 1275 1310 1378 1456 1499 1543 1621 1709 1805 1901 2015
26 | 2 | Performance data (cont) | 3 | 11 | 799 804 814 824 829 834 844 855 861 866 878 889 900
26 | 2 | Performance data (cont) | 3 | 12 | 1250 1289 1368 1447 1491 1526 1604 1691 1735 1779 1875 1971 2067
26 | 2 | Performance data (cont) | 3 | 13 | 861 864 871 878 884 885 892 902 908 913
26 | 2 | Performance data (cont) | 3 | 14 | 1616 1638 1682 1727 1744 1770 1840 1927 1980 2023
26 | 2 | Performance data (cont) | 3 | 15 | 922 924 929 934 937 939 944
26 | 2 | Performance data (cont) | 3 | 16 | 1902 1928 1980 2032 2058 2084 2119
26 | 2 | Performance data (cont) | 3 | 17 | 759
26 | 2 | Performance data (cont) | 3 | 18 | 2219
26 | 2 | Performance data (cont) | 3 | 19 | 1004
26 | 2 | Performance data (cont) | 3 | 20 | 2640
26 | 2 | Performance data (cont) | 4 | 17 | 790
26 | 2 | Performance data (cont) | 4 | 18 | 2246
26 | 2 | Performance data (cont) | 4 | 19 | 1007
26 | 2 | Performance data (cont) | 4 | 20 | 2652
26 | 2 | Performance data (cont) | 5 | 17 | 853
26 | 2 | Performance data (cont) | 5 | 18 | 2283
26 | 2 | Performance data (cont) | 5 | 19 | 1013
26 | 2 | Performance data (cont) | 5 | 20 | 2677
26 | 2 | Performance data (cont) | 6 | 17 | 916
26 | 2 | Performance data (cont) | 6 | 18 | 2326
26 | 2 | Performance data (cont) | 6 | 19 | 1019
26 | 2 | Performance data (cont) | 6 | 20 | 2702
26 | 2 | Performance data (cont) | 7 | 17 | 947
26 | 2 | Performance data (cont) | 7 | 18 | 2343
26 | 2 | Performance data (cont) | 7 | 19 | 1022
26 | 2 | Performance data (cont) | 7 | 20 | 2710
26 | 2 | Performance data (cont) | 8 | 17 | 979
26 | 2 | Performance data (cont) | 8 | 18 | 2369
26 | 2 | Performance data (cont) | 8 | 19 | 1025
26 | 2 | Performance data (cont) | 8 | 20 | 2727
26 | 2 | Performance data (cont) | 9 | 17 | 987
26 | 2 | Performance data (cont) | 9 | 18 | 2428
26 | 2 | Performance data (cont) | 9 | 19 | 1039
26 | 2 | Performance data (cont) | 9 | 20 | 2791
26 | 2 | Performance data (cont) | 10 | 15 | 949
26 | 2 | Performance data (cont) | 10 | 16 | 2188
26 | 2 | Performance data (cont) | 10 | 17 | 1002
26 | 2 | Performance data (cont) | 10 | 18 | 2495
26 | 2 | Performance data (cont) | 10 | 19 | 1041
26 | 2 | Performance data (cont) | 10 | 20 | 2831
26 | 2 | Performance data (cont) | 11 | 15 | 953
26 | 2 | Performance data (cont) | 11 | 16 | 2232
26 | 2 | Performance data (cont) | 11 | 17 | 1003
26 | 2 | Performance data (cont) | 11 | 18 | 2521
26 | 2 | Performance data (cont) | 11 | 19 | 1045
26 | 2 | Performance data (cont) | 11 | 20 | 2854
26 | 2 | Performance data (cont) | 12 | 15 | 957
26 | 2 | Performance data (cont) | 12 | 16 | 2275
26 | 2 | Performance data (cont) | 12 | 17 | 1004
26 | 2 | Performance data (cont) | 12 | 18 | 2554
26 | 2 | Performance data (cont) | 12 | 19 | 1050
26 | 2 | Performance data (cont) | 12 | 20 | 2878
26 | 2 | Performance data (cont) | 13 | 13 | 924
26 | 2 | Performance data (cont) | 13 | 14 | 2128
26 | 2 | Performance data (cont) | 13 | 15 | 967
26 | 2 | Performance data (cont) | 13 | 16 | 2377
26 | 2 | Performance data (cont) | 13 | 17 | 1010
26 | 2 | Performance data (cont) | 13 | 18 | 2637
26 | 2 | Performance data (cont) | 13 | 19 | 1056
26 | 2 | Performance data (cont) | 13 | 20 | 2925
26 | 2 | Performance data (cont) | 14 | 13 | 935
26 | 2 | Performance data (cont) | 14 | 14 | 2223
26 | 2 | Performance data (cont) | 14 | 15 | 978
26 | 2 | Performance data (cont) | 14 | 16 | 2479
26 | 2 | Performance data (cont) | 14 | 17 | 1019
26 | 2 | Performance data (cont) | 14 | 18 | 2735
26 | 2 | Performance data (cont) | 14 | 19 | 1061
26 | 2 | Performance data (cont) | 14 | 20 | 3002
26 | 2 | Performance data (cont) | 15 | 13 | 946
26 | 2 | Performance data (cont) | 15 | 14 | 2335
26 | 2 | Performance data (cont) | 15 | 15 | 989
26 | 2 | Performance data (cont) | 15 | 16 | 2595
26 | 2 | Performance data (cont) | 15 | 17 | 1030
26 | 2 | Performance data (cont) | 15 | 18 | 2847
26 | 2 | Performance data (cont) | 15 | 19 | — — — — — — —
26 | 2 | Performance data (cont) | 16 | 11 | 911
26 | 2 | Performance data (cont) | 16 | 12 | 2171
26 | 2 | Performance data (cont) | 16 | 13 | 957
26 | 2 | Performance data (cont) | 16 | 14 | 2445
26 | 2 | Performance data (cont) | 16 | 15 | 1000
26 | 2 | Performance data (cont) | 16 | 16 | 2702
26 | 2 | Performance data (cont) | 16 | 17 | 1040
26 | 2 | Performance data (cont) | 16 | 18 | 2956
26 | 2 | Performance data (cont) | 17 | 11 | 923
26 | 2 | Performance data (cont) | 17 | 12 | 2275
26 | 2 | Performance data (cont) | 17 | 13 | 968
26 | 2 | Performance data (cont) | 17 | 14 | 2554
26 | 2 | Performance data (cont) | 17 | 15 | 1011
26 | 2 | Performance data (cont) | 17 | 16 | 2832
26 | 2 | Performance data (cont) | 17 | 17 | — — — — —
26 | 2 | Performance data (cont) | 17 | 18 | — — — — —
26 | 2 | Performance data (cont) | 18 | 9 | 887
26 | 2 | Performance data (cont) | 18 | 10 | 2128
26 | 2 | Performance data (cont) | 18 | 11 | 934
26 | 2 | Performance data (cont) | 18 | 12 | 2386
26 | 2 | Performance data (cont) | 18 | 13 | 980
26 | 2 | Performance data (cont) | 18 | 14 | 2661
26 | 2 | Performance data (cont) | 18 | 15 | 1022
26 | 2 | Performance data (cont) | 18 | 16 | 2933
26 | 2 | Performance data (cont) | 19 | 9 | 900
26 | 2 | Performance data (cont) | 19 | 10 | 2240
26 | 2 | Performance data (cont) | 19 | 11 | 946
26 | 2 | Performance data (cont) | 19 | 12 | 2504
26 | 2 | Performance data (cont) | 19 | 13 | 991
26 | 2 | Performance data (cont) | 19 | 14 | 2775
26 | 2 | Performance data (cont) | 19 | 15 | — — —
26 | 2 | Performance data (cont) | 19 | 16 | — — —
26 | 2 | Performance data (cont) | 20 | 9 | 914
26 | 2 | Performance data (cont) | 20 | 10 | 2369
26 | 2 | Performance data (cont) | 20 | 11 | 959
26 | 2 | Performance data (cont) | 20 | 12 | 2629
26 | 2 | Performance data (cont) | 20 | 13 | 1003
26 | 2 | Performance data (cont) | 20 | 14 | 2886
26 | 2 | Performance data (cont) | 21 | 7 | 881
26 | 2 | Performance data (cont) | 21 | 8 | 2206
26 | 2 | Performance data (cont) | 21 | 9 | 928
26 | 2 | Performance data (cont) | 21 | 10 | 2495
26 | 2 | Performance data (cont) | 21 | 11 | 971
26 | 2 | Performance data (cont) | 21 | 12 | 2759
26 | 2 | Performance data (cont) | 21 | 13 | 1014
26 | 2 | Performance data (cont) | 21 | 14 | 3009
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 1 | 1 | 0.2
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 1 | 3 | 0.4
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 1 | 5 | 0.6
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 1 | 7 | 0.8
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 1 | 9 | 1
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 1 | 11 | 1.2
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 1 | 13 | 1.4
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 1 | 15 | 1.6
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 1 | 17 | 1.8
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 1 | Rpm
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 2 | Watts
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 3 | Rpm
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 4 | Watts
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 5 | Rpm
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 6 | Watts
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 7 | Rpm
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 8 | Watts
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 9 | Rpm
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 10 | Watts
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 11 | Rpm
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 12 | Watts
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 13 | Rpm
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 14 | Watts
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 15 | Rpm
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 16 | Watts
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 17 | Rpm
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 18 | Watts
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 19 | Rpm
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 1 | 471 483 495 508 521 532 544 557 570 583 596 609 622 635 649 662 675 689
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 2 | 369 404 449 485 530 630 677 716 763 818 867 924 989 1047 1123 1190 1267 1353
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 3 | 552 562 573 583 594 605 616 628 639 651 663 674 686 698 713 722 734 746
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 4 | 494 530 575 620 665 763 803 859 907 965 1031 1097 1165 1241 1318 1396 1482 1569
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 5 | 617 627 638 648 659 670 680 690 700 711 721 732 744 755 767 778 790 801
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 6 | 611 656 710 755 809 891 940 998 1064 1123 1190 1267 1335 1413 1491 1578 1674 1761
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 7 | 679 685 694 704 714 725 735 746 757 767 777 787 797 808 818 829 839 851
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 8 | 719 773 827 881 944 1014 1081 1148 1216 1284 1353 1430 1508 1595 1683 1779 1875 1971
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 9 | 740 754 757 759 766 778 787 796 805 815 826 836 847 857 867 878 888
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 10 | 818 881 944 1007 1070 1148 1216 1284 1353 1430 1517 1595 1691 1779 1866 1962 2058
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 11 | 757 765 775 791 807 825 835 844 854 863 871 880 890 901 912
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 12 | 881 944 1007 1070 1150 1275 1353 1430 1508 1587 1665 1753 1849 1945 2050
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 13 | 765 775 793 808 823 874 880 888 897 907 916 926 934
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 14 | 944 1025 1088 1186 1339 1422 1491 1569 1648 1744 1831 1927 2015
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 15 | 811 825 848 887 918 926 933 934 940 947 956
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 16 | 1034 1097 1240 1357 1519 1613 1656 1718 1853 1946 2039
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 17 | 889 907 929 954 963 974 983 988 989 991
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 18 | 1321 1429 1528 1690 1834 1920 1963 1980 2031 2099
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 19 | 946 959 975 987 999
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 4 | 19 | 1012
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 4 | 20 | 2134
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 5 | 19 | 1017
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 5 | 20 | 2177
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 6 | 19 | 1025
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 6 | 20 | 2230
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 7 | 19 | 1032
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 7 | 20 | 2282
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 8 | 19 | 1038
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 8 | 20 | 2318
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 9 | 17 | 997
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 9 | 18 | 2195
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 9 | 19 | 1043
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 9 | 20 | 2380
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 10 | 15 | 966
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 10 | 16 | 2134
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 10 | 17 | 1004
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 10 | 18 | 2291
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 10 | 19 | 1045
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 10 | 20 | 2478
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 11 | 15 | 976
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 11 | 16 | 2238
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 11 | 17 | 1013
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 11 | 18 | 2397
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 11 | 19 | 1051
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 11 | 20 | 2569
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 12 | 13 | 943
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 12 | 14 | 2160
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 12 | 15 | 985
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 12 | 16 | 2344
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 12 | 17 | 1023
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 12 | 18 | 2514
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 12 | 19 | 1059
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 12 | 20 | 2688
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 13 | 13 | 952
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 13 | 14 | 2265
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 13 | 15 | 994
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 13 | 16 | 2451
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 13 | 17 | 1032
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 13 | 18 | 2633
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 13 | 19 | 1068
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 13 | 20 | 2819
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 14 | 11 | 922
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 14 | 12 | 2203
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 14 | 13 | 962
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 14 | 14 | 2371
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 14 | 15 | 1003
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 14 | 16 | 2560
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 14 | 17 | 1042
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 14 | 18 | 2763
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 14 | 19 | 1078
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 14 | 20 | 2952
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 15 | 11 | 933
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 15 | 12 | 2309
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 15 | 13 | 973
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 15 | 14 | 2496
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 15 | 15 | 1011
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 15 | 16 | 2679
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 15 | 17 | 1051
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 15 | 18 | 2895
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 15 | 19 | 1087
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 15 | 20 | 3097
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 16 | 9 | 898
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 16 | 10 | 2212
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 16 | 11 | 943
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 16 | 12 | 2424
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 16 | 13 | 983
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 16 | 14 | 2624
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 16 | 15 | 1021
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 16 | 16 | 2810
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 16 | 17 | 1060
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 16 | 18 | 3029
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 16 | 19 | 1090
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 16 | 20 | 3276
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 1 | 1 | 0.2
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 1 | 3 | 0.4
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 1 | 5 | 0.6
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 1 | 7 | 0.8
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 1 | 9 | 1
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 1 | 11 | 1.2
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 1 | 13 | 1.4
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 1 | 15 | 1.6
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 1 | 17 | 1.8
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 1 | Rpm
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 2 | Watts
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 3 | Rpm
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 4 | Watts
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 5 | Rpm
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 6 | Watts
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 7 | Rpm
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 8 | Watts
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 9 | Rpm
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 10 | Watts
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 11 | Rpm
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 12 | Watts
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 13 | Rpm
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 14 | Watts
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 15 | Rpm
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 16 | Watts
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 17 | Rpm
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 18 | Watts
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 19 | Rpm
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 1 | 570 584 598 612 626 640 654 668 683 697 711 726 741 755 770 784 799 814 829 843 858
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 2 | 623 676 728 781 873 913 1065 1129 1194 1267 1340 1423 1506 1598 1700 1794 1905 2009 2131 2246 2378
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 3 | 636 649 662 675 688 702 714 727 741 754 767 780 794 808 821 835 849 863 877 892 906
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 4 | 799 842 904 957 1018 1080 1218 1291 1365 1448 1531 1624 1717 1819 1923 2027 2140 2254 2378 2503 2629
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 5 | 693 705 717 729 741 754 767 780 793 806 819 832 845 858 871 884 897 910 923 937 950
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 6 | 886 948 1027 1115 1202 1290 1373 1456 1540 1624 1708 1802 1897 2000 2114 2219 2343 2468 2602 2746 2891
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 7 | 748 759 769 780 792 803 815 827 839 851 864 877 889 902 915 928 941 954 967 980 993
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 8 | 1044 1097 1158 1229 1299 1378 1514 1598 1691 1785 1879 1983 2096 2210 2325 2450 2566 2692 2828 2964 3111
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 9 | 800 809 819 829 840 851 861 873 884 895 907 919 931 943 955 968 981 993 1006 1019
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 10 | 1202 1281 1342 1414 1483 1553 1666 1751 1836 1931 2035 2149 2263 2387 2512 2638 2773 2919 3065 3221
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 11 | 850 858 867 876 886 896 906 916 927 938 949 960 971 983 995 1006 1018 1030 1043
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 12 | 1281 1352 1483 1589 1676 1755 1862 1948 2035 2123 2219 2316 2423 2548 2683 2828 2964 3111 3267
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 13 | 901 907 914 922 930 940 950 959 969 979 989 1000 1011 1022 1033 1044 1056 1067
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 14 | 1360 1457 1536 1606 1773 1913 2027 2123 2228 2334 2441 2548 2647 2764 2882 3010 3147 3304
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 15 | 950 960 963 968 975 983 991 1001 1010 1020 1029 1039 1049 1059 1070 1081
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 16 | 1474 1571 1668 1764 1826 1887 2202 2299 2405 2521 2638 2764 2882 3010 3138 3258
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 17 | 989 1001 1010 1018 1021 1026 1030 1040 1049 1059 1068 1077 1087 1097
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 18 | 1597 1703 1799 1940 2062 2212 2361 2476 2593 2710 2837 2955 3092 3230
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 19 | 1000 1006 1018 1022 1039 1051 1064 1075 1085 1095 1105 1114 1124
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 4 | 19 | 1133
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 4 | 20 | 3442
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 5 | 17 | 1107
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 5 | 18 | 3368
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 5 | 19 | 1143
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 5 | 20 | 3590
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 6 | 17 | 1117
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 6 | 18 | 3516
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 6 | 19 | 1152
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 6 | 20 | 3748
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 7 | 15 | 1092
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 7 | 16 | 3387
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 7 | 17 | 1127
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 7 | 18 | 3655
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 7 | 19 | 1162
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 7 | 20 | 3897
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 8 | 15 | 1103
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 8 | 16 | 3525
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 8 | 17 | 1138
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 8 | 18 | 3804
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 8 | 19 | 1172
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 8 | 20 | 4055
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 9 | 13 | 1079
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 9 | 14 | 3470
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 9 | 15 | 1114
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 9 | 16 | 3674
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 9 | 17 | 1149
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 9 | 18 | 3934
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 9 | 19 | 1182
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 9 | 20 | 4223
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 10 | 11 | 1055
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 10 | 12 | 3424
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 10 | 13 | 1091
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 10 | 14 | 3637
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 10 | 15 | 1126
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 10 | 16 | 3822
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 10 | 17 | 1160
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 10 | 18 | 4083
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 10 | 19 | 1193
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 10 | 20 | 4382
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 11 | 9 | 1032
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 11 | 10 | 3388
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 11 | 11 | 1068
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 11 | 12 | 3590
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 11 | 13 | 1103
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 11 | 14 | 3804
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 11 | 15 | 1137
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 11 | 16 | 4009
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 11 | 17 | 1171
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 11 | 18 | 4242
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 11 | 19 | 1204
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 11 | 20 | 4531
28 | 1 | Performance data (cont) | 1 | 1 | 0.1
28 | 1 | Performance data (cont) | 1 | 3 | 0.2
28 | 1 | Performance data (cont) | 1 | 5 | 0.4
28 | 1 | Performance data (cont) | 1 | 7 | 0.6
28 | 1 | Performance data (cont) | 1 | 9 | 0.8
28 | 1 | Performance data (cont) | 1 | 11 | 1
28 | 1 | Performance data (cont) | 1 | 13 | 1.2
28 | 1 | Performance data (cont) | 1 | 15 | 1.4
28 | 1 | Performance data (cont) | 2 | 1 | Rpm
28 | 1 | Performance data (cont) | 2 | 2 | Watts
28 | 1 | Performance data (cont) | 2 | 3 | Rpm
28 | 1 | Performance data (cont) | 2 | 4 | Watts
28 | 1 | Performance data (cont) | 2 | 5 | Rpm
28 | 1 | Performance data (cont) | 2 | 6 | Watts
28 | 1 | Performance data (cont) | 2 | 7 | Rpm
28 | 1 | Performance data (cont) | 2 | 8 | Watts
28 | 1 | Performance data (cont) | 2 | 9 | Rpm
28 | 1 | Performance data (cont) | 2 | 10 | Watts
28 | 1 | Performance data (cont) | 2 | 11 | Rpm
28 | 1 | Performance data (cont) | 2 | 12 | Watts
28 | 1 | Performance data (cont) | 2 | 13 | Rpm
28 | 1 | Performance data (cont) | 2 | 14 | Watts
28 | 1 | Performance data (cont) | 2 | 15 | Rpm
28 | 1 | Performance data (cont) | 2 | 16 | Watts
28 | 1 | Performance data (cont) | 2 | 17 | Rpm
28 | 1 | Performance data (cont) | 3 | 1 | 656 691 727 765 802 840 878 916 954 993 1031
28 | 1 | Performance data (cont) | 3 | 2 | 258 304 350 487 539 600 669 739 827 916 1022
28 | 1 | Performance data (cont) | 3 | 3 | 722 753 785 821 854 888 923 958 993 1029 1066
28 | 1 | Performance data (cont) | 3 | 4 | 304 350 405 532 585 646 716 795 883 973 1081
28 | 1 | Performance data (cont) | 3 | 5 | 840 867 895 923 953 984 1015 1046 1079 1112 1145
28 | 1 | Performance data (cont) | 3 | 6 | 424 470 534 638 700 771 843 924 1022 1123 1241
28 | 1 | Performance data (cont) | 3 | 7 | 939 965 991 1019 1046 1073 1101 1129 1160 1190 1220
28 | 1 | Performance data (cont) | 3 | 8 | 543 608 672 843 835 907 981 1072 1173 1275 1396
28 | 1 | Performance data (cont) | 3 | 9 | 1024 1050 1076 1099 1126 1154 1182 1209 1237 1264 1292
28 | 1 | Performance data (cont) | 3 | 10 | 672 737 811 883 965 1047 1140 1241 1344 1447 1569
28 | 1 | Performance data (cont) | 3 | 11 | 1106 1127 1151 1178 1201 1226 1252 1280 1309 1336 1363
28 | 1 | Performance data (cont) | 3 | 12 | 829 884 958 1031 1106 1190 1292 1404 1517 1639 1770
28 | 1 | Performance data (cont) | 3 | 13 | 1195 1207 1222 1249 1274 1297 1320 1345 1372 1400 1428
28 | 1 | Performance data (cont) | 3 | 14 | 995 1078 1123 1182 1275 1361 1456 1569 1691 1823 1962
28 | 1 | Performance data (cont) | 3 | 15 | 1269 1285 1301 1316 1338 1363 1388 1410 1434 1459
28 | 1 | Performance data (cont) | 3 | 16 | 1179 1262 1354 1353 1439 1534 1639 1744 1866 1997
28 | 1 | Performance data (cont) | 3 | 17 | 1347 1360 1370 1382 1402 1424 1448 1473 1496
28 | 1 | Performance data (cont) | 4 | 17 | 1519
28 | 1 | Performance data (cont) | 4 | 18 | 2188
28 | 1 | Performance data (cont) | 5 | 15 | 1486
28 | 1 | Performance data (cont) | 5 | 16 | 2145
28 | 1 | Performance data (cont) | 5 | 17 | 1543
28 | 1 | Performance data (cont) | 5 | 18 | 2335
28 | 2 | Performance data (cont) | 1 | 1 | 0.2
28 | 2 | Performance data (cont) | 1 | 3 | 0.4
28 | 2 | Performance data (cont) | 1 | 5 | 0.6
28 | 2 | Performance data (cont) | 1 | 7 | 0.8
28 | 2 | Performance data (cont) | 1 | 9 | 1
28 | 2 | Performance data (cont) | 1 | 11 | 1.2
28 | 2 | Performance data (cont) | 1 | 13 | 1.4
28 | 2 | Performance data (cont) | 1 | 15 | 1.6
28 | 2 | Performance data (cont) | 1 | 17 | 1.8
28 | 2 | Performance data (cont) | 2 | 1 | Rpm
28 | 2 | Performance data (cont) | 2 | 2 | Watts
28 | 2 | Performance data (cont) | 2 | 3 | Rpm
28 | 2 | Performance data (cont) | 2 | 4 | Watts
28 | 2 | Performance data (cont) | 2 | 5 | Rpm
28 | 2 | Performance data (cont) | 2 | 6 | Watts
28 | 2 | Performance data (cont) | 2 | 7 | Rpm
28 | 2 | Performance data (cont) | 2 | 8 | Watts
28 | 2 | Performance data (cont) | 2 | 9 | Rpm
28 | 2 | Performance data (cont) | 2 | 10 | Watts
28 | 2 | Performance data (cont) | 2 | 11 | Rpm
28 | 2 | Performance data (cont) | 2 | 12 | Watts
28 | 2 | Performance data (cont) | 2 | 13 | Rpm
28 | 2 | Performance data (cont) | 2 | 14 | Watts
28 | 2 | Performance data (cont) | 2 | 15 | Rpm
28 | 2 | Performance data (cont) | 2 | 16 | Watts
28 | 2 | Performance data (cont) | 2 | 17 | Rpm
28 | 2 | Performance data (cont) | 2 | 18 | Watts
28 | 2 | Performance data (cont) | 2 | 19 | Rpm
28 | 2 | Performance data (cont) | 3 | 1 | 429 435 447 459 465 471 482 494 501 507 520 533 546 559 572 585 598 610 623
28 | 2 | Performance data (cont) | 3 | 2 | 410 421 443 465 473 487 524 554 577 592 638 684 731 779 835 883 940 998 1056
28 | 2 | Performance data (cont) | 3 | 3 | 424 429 439 549 554 559 569 581 587 592 604 615 626 637 648 660 671 682 694
28 | 2 | Performance data (cont) | 3 | 4 | 538 553 584 615 630 646 684 723 747 771 827 875 932 989 1056 1114 1182 1258 1335
28 | 2 | Performance data (cont) | 3 | 5 | 600 605 615 625 630 635 645 654 659 663 672 683 693 704 715 727 739 750 761
28 | 2 | Performance data (cont) | 3 | 6 | 659 683 731 779 803 827 875 924 956 981 1031 1081 1140 1207 1275 1353 1439 1526 1613
28 | 2 | Performance data (cont) | 3 | 7 | 671 675 683 691 695 699 708 717 722 727 737 747 756 765 775 785 795 806 817
28 | 2 | Performance data (cont) | 3 | 8 | 843 867 916 965 989 1014 1064 1123 1156 1182 1250 1327 1396 1473 1543 1321 1691 1779 1866
28 | 2 | Performance data (cont) | 3 | 9 | 736 739 746 753 757 760 768 776 780 784 793 802 813 823 832 841 851 860
28 | 2 | Performance data (cont) | 3 | 10 | 1046 1071 1122 1173 1199 1224 1284 1344 1378 1404 1473 1552 1630 1718 1814 1901 1997 2084
28 | 2 | Performance data (cont) | 3 | 11 | 778 783 794 805 810 816 824 832 836 839 846 855 863 872 882
28 | 2 | Performance data (cont) | 3 | 12 | 1252 1282 1343 1404 1439 1465 1526 1587 1621 1656 1726 1805 1884 1962 2058
28 | 2 | Performance data (cont) | 3 | 13 | 800 808 825 842 850 859 872 882 887 891 898 906
28 | 2 | Performance data (cont) | 3 | 14 | 1501 1532 1594 1656 1691 1718 1779 1849 1884 1919 1997 2076
28 | 2 | Performance data (cont) | 3 | 15 | 765 795 826 857 873 888 909 925
28 | 2 | Performance data (cont) | 3 | 16 | 1735 1770 1840 1910 1945 1980 2050 2119
28 | 2 | Performance data (cont) | 3 | 17 | 736 759 805
28 | 2 | Performance data (cont) | 3 | 18 | 1945 1988 2075
28 | 2 | Performance data (cont) | 3 | 19 | 666
28 | 2 | Performance data (cont) | 4 | 19 | 697
28 | 2 | Performance data (cont) | 4 | 20 | 2123
28 | 2 | Performance data (cont) | 5 | 19 | 760
28 | 2 | Performance data (cont) | 5 | 20 | 2250
28 | 2 | Performance data (cont) | 6 | 17 | 851
28 | 2 | Performance data (cont) | 6 | 18 | 2162
28 | 2 | Performance data (cont) | 6 | 19 | 823
28 | 2 | Performance data (cont) | 6 | 20 | 2377
28 | 2 | Performance data (cont) | 7 | 17 | 863
28 | 2 | Performance data (cont) | 7 | 18 | 2206
28 | 2 | Performance data (cont) | 7 | 19 | 855
28 | 2 | Performance data (cont) | 7 | 20 | 2445
28 | 2 | Performance data (cont) | 8 | 17 | 897
28 | 2 | Performance data (cont) | 8 | 18 | 2249
28 | 2 | Performance data (cont) | 8 | 19 | 887
28 | 2 | Performance data (cont) | 8 | 20 | 2504
28 | 2 | Performance data (cont) | 9 | 17 | 931
28 | 2 | Performance data (cont) | 9 | 18 | 2326
28 | 2 | Performance data (cont) | 9 | 19 | 935
28 | 2 | Performance data (cont) | 9 | 20 | 2595
28 | 2 | Performance data (cont) | 10 | 17 | 955
28 | 2 | Performance data (cont) | 10 | 18 | 2394
28 | 2 | Performance data (cont) | 10 | 19 | 972
28 | 2 | Performance data (cont) | 10 | 20 | 2678
28 | 2 | Performance data (cont) | 11 | 15 | 931
28 | 2 | Performance data (cont) | 11 | 16 | 2162
28 | 2 | Performance data (cont) | 11 | 17 | 964
28 | 2 | Performance data (cont) | 11 | 18 | 2436
28 | 2 | Performance data (cont) | 11 | 19 | 986
28 | 2 | Performance data (cont) | 11 | 20 | 2718
28 | 2 | Performance data (cont) | 12 | 15 | 936
28 | 2 | Performance data (cont) | 12 | 16 | 2197
28 | 2 | Performance data (cont) | 12 | 17 | 973
28 | 2 | Performance data (cont) | 12 | 18 | 2479
28 | 2 | Performance data (cont) | 12 | 19 | 999
28 | 2 | Performance data (cont) | 12 | 20 | 2759
28 | 2 | Performance data (cont) | 13 | 15 | 946
28 | 2 | Performance data (cont) | 13 | 16 | 2275
28 | 2 | Performance data (cont) | 13 | 17 | 987
28 | 2 | Performance data (cont) | 13 | 18 | 2554
28 | 2 | Performance data (cont) | 13 | 19 | 1019
28 | 2 | Performance data (cont) | 13 | 20 | 2839
28 | 2 | Performance data (cont) | 14 | 15 | 954
28 | 2 | Performance data (cont) | 14 | 16 | 2352
28 | 2 | Performance data (cont) | 14 | 17 | 997
28 | 2 | Performance data (cont) | 14 | 18 | 2637
28 | 2 | Performance data (cont) | 14 | 19 | 1034
28 | 2 | Performance data (cont) | 14 | 20 | 2917
28 | 2 | Performance data (cont) | 15 | 13 | 913
28 | 2 | Performance data (cont) | 15 | 14 | 2154
28 | 2 | Performance data (cont) | 15 | 15 | 961
28 | 2 | Performance data (cont) | 15 | 16 | 2436
28 | 2 | Performance data (cont) | 15 | 17 | 1006
28 | 2 | Performance data (cont) | 15 | 18 | 2727
28 | 2 | Performance data (cont) | 15 | 19 | — — — — — — —
28 | 2 | Performance data (cont) | 16 | 13 | 921
28 | 2 | Performance data (cont) | 16 | 14 | 2240
28 | 2 | Performance data (cont) | 16 | 15 | 969
28 | 2 | Performance data (cont) | 16 | 16 | 2529
28 | 2 | Performance data (cont) | 16 | 17 | 1014
28 | 2 | Performance data (cont) | 16 | 18 | 2807
28 | 2 | Performance data (cont) | 17 | 13 | 930
28 | 2 | Performance data (cont) | 17 | 14 | 2335
28 | 2 | Performance data (cont) | 17 | 15 | 976
28 | 2 | Performance data (cont) | 17 | 16 | 2620
28 | 2 | Performance data (cont) | 17 | 17 | 1021
28 | 2 | Performance data (cont) | 17 | 18 | 2902
28 | 2 | Performance data (cont) | 18 | 11 | 892
28 | 2 | Performance data (cont) | 18 | 12 | 2162
28 | 2 | Performance data (cont) | 18 | 13 | 939
28 | 2 | Performance data (cont) | 18 | 14 | 2428
28 | 2 | Performance data (cont) | 18 | 15 | 984
28 | 2 | Performance data (cont) | 18 | 16 | 2710
28 | 2 | Performance data (cont) | 18 | 17 | — — — —
28 | 2 | Performance data (cont) | 18 | 18 | — — — —
28 | 2 | Performance data (cont) | 19 | 11 | 902
28 | 2 | Performance data (cont) | 19 | 12 | 2266
28 | 2 | Performance data (cont) | 19 | 13 | 948
28 | 2 | Performance data (cont) | 19 | 14 | 2529
28 | 2 | Performance data (cont) | 19 | 15 | 993
28 | 2 | Performance data (cont) | 19 | 16 | 2799
28 | 2 | Performance data (cont) | 20 | 11 | 912
28 | 2 | Performance data (cont) | 20 | 12 | 2369
28 | 2 | Performance data (cont) | 20 | 13 | 958
28 | 2 | Performance data (cont) | 20 | 14 | 2637
28 | 2 | Performance data (cont) | 20 | 15 | 1002
28 | 2 | Performance data (cont) | 20 | 16 | 2902
28 | 2 | Performance data (cont) | 21 | 9 | 870
28 | 2 | Performance data (cont) | 21 | 10 | 2180
28 | 2 | Performance data (cont) | 21 | 11 | 921
28 | 2 | Performance data (cont) | 21 | 12 | 2479
28 | 2 | Performance data (cont) | 21 | 13 | 968
28 | 2 | Performance data (cont) | 21 | 14 | 2751
28 | 2 | Performance data (cont) | 21 | 15
28 | 2 | Performance data (cont) | 21 | 16
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 1 | 0.2
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 3 | 0.4
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 5 | 0.6
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 7 | 0.8
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 9 | 1
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 11 | 1.2
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 13 | 1.4
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 15 | 1.6
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 17 | 1.8
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 1 | Rpm
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 2 | Watts
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 3 | Rpm
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 4 | Watts
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 5 | Rpm
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 6 | Watts
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 7 | Rpm
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 8 | Watts
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 9 | Rpm
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 10 | Watts
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 11 | Rpm
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 12 | Watts
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 13 | Rpm
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 14 | Watts
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 15 | Rpm
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 16 | Watts
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 17 | Rpm
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 18 | Watts
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 19 | Rpm
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 1 | 437 448 460 471 483 484 495 505 516 527 537 548 560 571 582 593 605 616
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 2 | 333 369 404 449 494 562 607 646 692 739 795 851 916 981 1047 1123 1207 1292
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 3 | 517 526 534 544 553 560 570 579 589 599 609 619 629 639 649 659 670 680
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 4 | 440 476 512 557 593 677 723 763 810 859 907 956 1014 1072 1140 1207 1284 1361
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 5 | 590 597 605 613 620 631 638 646 655 664 672 680 688 698 708 717 727 737
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 6 | 566 602 638 683 728 810 851 899 956 1006 1064 1114 1173 1241 1310 1387 1465 1543
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 7 | 653 660 668 675 682 690 699 708 717 724 731 738 747 756 764 773 781 789
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 8 | 692 746 791 361 881 940 998 1047 1106 1165 1216 1275 1344 1422 1499 1578 1648 1726
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 9 | 712 717 723 730 738 747 755 761 767 775 784 794 802 810 816 823 832 841
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 10 | 755 836 908 971 1034 1081 1140 1199 1250 1318 1387 1456 1534 1604 1674 1753 1840 1927
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 11 | 770 778 779 783 789 800 805 812 819 827 833 840 847 856 865 875 883
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 12 | 827 881 944 1052 1150 1233 1284 1344 1413 1482 1552 1621 1700 1788 1875 1962 2050
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 13 | 805 815 825 830 840 850 857 862 867 873 880 888 895 901 908
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 14 | 881 926 980 1070 1159 1353 1447 1517 1578 1639 1718 1805 1884 1971 2050
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 15 | 811 822 835 843 860 879 896 908 915 920 926 931 938
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 16 | 944 989 1052 1150 1195 1233 1473 1639 1753 1831 1901 1971 2108
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 17 | 830 843 855 868 880 925 935 944 952 963
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 18 | 998 1079 1186 1303 1429 1604 1709 1836 1920 2005
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 19 | 883 898 910 924 942 964 975 984 993 1001
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 4 | 17 | 970
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 4 | 18 | 2134
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 4 | 19 | 1007
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 4 | 20 | 2221
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 5 | 17 | 976
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 5 | 18 | 2230
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 5 | 19 | 1017
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 5 | 20 | 2362
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 6 | 17 | 981
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 6 | 18 | 2309
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 6 | 19 | 1024
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 6 | 20 | 2496
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 7 | 15 | 945
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 7 | 16 | 2203
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 7 | 17 | 986
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 7 | 18 | 2389
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 7 | 19 | 1029
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 7 | 20 | 2605
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 8 | 15 | 953
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 8 | 16 | 2300
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 8 | 17 | 993
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 8 | 18 | 2478
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 8 | 19 | 1034
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 8 | 20 | 2707
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 9 | 13 | 915
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 9 | 14 | 2186
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 9 | 15 | 960
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 9 | 16 | 2389
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 9 | 17 | 1000
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 9 | 18 | 2587
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 9 | 19 | 1039
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 9 | 20 | 2800
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 10 | 13 | 924
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 10 | 14 | 2291
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 10 | 15 | 966
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 10 | 16 | 2487
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 10 | 17 | 1008
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 10 | 18 | 2698
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 10 | 19 | 1046
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 10 | 20 | 2904
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 11 | 11 | 889
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 11 | 12 | 2177
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 11 | 13 | 934
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 11 | 14 | 2389
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 11 | 15 | 972
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 11 | 16 | 2587
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 11 | 17 | 1015
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 11 | 18 | 2819
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 11 | 19 | 1053
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 11 | 20 | 3029
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 1 | 0.2
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 3 | 0.4
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 5 | 0.6
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 7 | 0.8
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 9 | 1
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 11 | 1.2
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 13 | 1.4
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 15 | 1.6
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 17 | 1.8
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 1 | Rpm
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 2 | Watts
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 3 | Rpm
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 4 | Watts
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 5 | Rpm
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 6 | Watts
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 7 | Rpm
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 8 | Watts
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 9 | Rpm
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 10 | Watts
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 11 | Rpm
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 12 | Watts
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 13 | Rpm
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 14 | Watts
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 15 | Rpm
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 16 | Watts
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 17 | Rpm
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 18 | Watts
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 19 | Rpm
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 1 | 529 541 553 566 579 593 607 621 636 650 665 680 696 711 727 742 758 773 789 805 821
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 2 | 535 579 632 685 737 790 947 1010 1073 1137 1210 1283 1365 1456 1540 1641 1742 1845 1958 2070 2202
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 3 | 605 615 626 636 647 659 670 681 693 705 717 728 739 750 762 774 786 799 812 826 840
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 4 | 693 746 790 843 904 957 1113 1170 1226 1291 1357 1431 1506 1582 1666 1759 1854 1948 2053 2166 2290
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 5 | 669 680 692 702 713 722 732 742 751 761 772 783 794 805 817 828 840 852 863 875 887
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 6 | 834 886 948 1018 1080 1141 1267 1332 1398 1464 1548 1632 1717 1811 1897 1992 2088 2193 2290 2405 2521
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 7 | 719 729 740 751 763 775 782 795 808 819 830 839 848 857 867 877 888 899 910 921 932
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 8 | 948 1009 1071 1141 1220 1290 1423 1506 1590 1674 1759 1836 1914 2000 2096 2193 2307 2423 2548 2665 2792
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 9 | 775 791 792 798 807 817 833 842 851 861 871 883 896 908 919 929 938 947 957 966 976
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 10 | 1158 1211 1237 1290 1352 1431 1565 1641 1725 1811 1905 2009 2123 2237 2343 2450 2557 2656 2773 2891 3019
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 11 | 815 827 832 845 856 867 879 889 898 908 917 925 935 945 955 967 980 992 1003 1014
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 12 | 1308 1369 1413 1510 1589 1624 1751 1819 1897 1974 2070 9175 2281 2387 2512 2638 2773 9910 3047 3184
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 13 | 880 889 895 903 911 920 927 934 942 950 960 969 979 988 996 1005 1015 1025 1036
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 14 | 1352 1448 1571 1668 1747 1799 1940 2018 2105 2193 2272 2370 2468 2575 2692 2819 2946 3083 3230
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 15 | 911 920 929 940 952 965 973 980 987 994 1001 1009 1018 1028 1037 1046 1056 1064
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 16 | 1606 1676 1755 1826 1887 2010 2123 2210 2307 2405 2503 2602 2701 2801 2901 3019 3147 3285
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 17 | 940 951 965 980 989 1000 1013 1022 1030 1037 1045 1051 1058 1066 1074 1084
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 18 | 1685 1747 1843 1940 2054 2150 2290 2396 2503 2602 2710 2828 2937 3047 3166 3276
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 19 | 971 985 999 1010 1021 1035 1046 1058 1068 1077 1085 1092 1100 1106
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 4 | 19 | 1113
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 4 | 20 | 3414
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 5 | 19 | 1121
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 5 | 20 | 3544
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 6 | 17 | 1093
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 6 | 18 | 3396
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 6 | 19 | 1129
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 6 | 20 | 3674
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 7 | 17 | 1103
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 7 | 18 | 3516
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 7 | 19 | 1137
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 7 | 20 | 3795
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 8 | 15 | 1073
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 8 | 16 | 3433
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 8 | 17 | 1112
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 8 | 18 | 3655
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 8 | 19 | 1147
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 8 | 20 | 3925
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 9 | 13 | 1049
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 9 | 14 | 3396
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 9 | 15 | 1083
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 9 | 16 | 3590
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 9 | 17 | 1121
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 9 | 18 | 3804
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 9 | 19 | 1157
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 9 | 20 | 4055
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 10 | 11 | 1024
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 10 | 12 | 3322
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 10 | 13 | 1061
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 10 | 14 | 3553
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 10 | 15 | 1093
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 10 | 16 | 3748
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 10 | 17 | 1129
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 10 | 18 | 3962
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 10 | 19 | 1166
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 10 | 20 | 4204
30 | 1 | Performance data (cont) | 1 | 1 | UNIT RATED VOLTAGE
30 | 1 | Performance data (cont) | 1 | 2 | MAXIMUM ACCEPTABLE CONTINUOUS BkW*
30 | 1 | Performance data (cont) | 1 | 3 | MAXIMUM ACCEPTABLE CONTINUOUS BHP*
30 | 1 | Performance data (cont) | 1 | 4 | MAXIMUM ACCEPTABLE OPERATING WATTS
30 | 1 | Performance data (cont) | 2 | 1 | 400
30 | 1 | Performance data (cont) | 2 | 2 | 1.79
30 | 1 | Performance data (cont) | 2 | 3 | 2.4
30 | 1 | Performance data (cont) | 2 | 4 | 2120
30 | 1 | Performance data (cont) | 3 | 1 | 400
30 | 1 | Performance data (cont) | 3 | 2 | 1.79
30 | 1 | Performance data (cont) | 3 | 3 | 2.4
30 | 1 | Performance data (cont) | 3 | 4 | 2120
30 | 1 | Performance data (cont) | 4 | 1 | 400
30 | 1 | Performance data (cont) | 4 | 2 | 1.79
30 | 1 | Performance data (cont) | 4 | 3 | 2.4
30 | 1 | Performance data (cont) | 4 | 4 | 2120
30 | 1 | Performance data (cont) | 5 | 1 | 400
30 | 1 | Performance data (cont) | 5 | 2 | 1.79
30 | 1 | Performance data (cont) | 5 | 3 | 2.4
30 | 1 | Performance data (cont) | 5 | 4 | 2120
30 | 1 | Performance data (cont) | 6 | 1 | 400
30 | 1 | Performance data (cont) | 6 | 2 | 2.76
30 | 1 | Performance data (cont) | 6 | 3 | 3.7
30 | 1 | Performance data (cont) | 6 | 4 | 3313
30 | 2 | Performance data (cont) | 1 | 1 | 0
30 | 2 | Performance data (cont) | 1 | 2 | 1/2
30 | 2 | Performance data (cont) | 1 | 3 | 1
30 | 2 | Performance data (cont) | 1 | 4 | 11/2
30 | 2 | Performance data (cont) | 1 | 5 | 2
30 | 2 | Performance data (cont) | 1 | 6 | 21/2
30 | 2 | Performance data (cont) | 1 | 7 | 3
30 | 2 | Performance data (cont) | 1 | 8 | 31/2
30 | 2 | Performance data (cont) | 1 | 9 | 4
30 | 2 | Performance data (cont) | 1 | 10 | 41/2
30 | 2 | Performance data (cont) | 2 | 1 | 20.08
30 | 2 | Performance data (cont) | 2 | 2 | 19.67
30 | 2 | Performance data (cont) | 2 | 3 | 19.17
30 | 2 | Performance data (cont) | 2 | 4 | 18.75
30 | 2 | Performance data (cont) | 2 | 5 | 18.25
30 | 2 | Performance data (cont) | 2 | 6 | 17.83
30 | 2 | Performance data (cont) | 2 | 7 | 17.33
30 | 2 | Performance data (cont) | 2 | 8 | 16.92
30 | 2 | Performance data (cont) | 2 | 9 | 16.42
30 | 2 | Performance data (cont) | 2 | 10 | 16
30 | 2 | Performance data (cont) | 3 | 1 | 14.67
30 | 2 | Performance data (cont) | 3 | 2 | 14.25
30 | 2 | Performance data (cont) | 3 | 3 | 13.83
30 | 2 | Performance data (cont) | 3 | 4 | 13.33
30 | 2 | Performance data (cont) | 3 | 5 | 12.92
30 | 2 | Performance data (cont) | 3 | 6 | 12.5
30 | 2 | Performance data (cont) | 3 | 7 | 12.08
30 | 2 | Performance data (cont) | 3 | 8 | 11.67
30 | 2 | Performance data (cont) | 3 | 9 | 11.25
30 | 2 | Performance data (cont) | 3 | 10 | 10.83
30 | 2 | Performance data (cont) | 4 | 1 | 15
30 | 2 | Performance data (cont) | 4 | 2 | 14.58
30 | 2 | Performance data (cont) | 4 | 3 | 14.25
30 | 2 | Performance data (cont) | 4 | 4 | 13.92
30 | 2 | Performance data (cont) | 4 | 5 | 13.58
30 | 2 | Performance data (cont) | 4 | 6 | 13.25
30 | 2 | Performance data (cont) | 4 | 7 | 12.92
30 | 2 | Performance data (cont) | 4 | 8 | 12.58
30 | 2 | Performance data (cont) | 4 | 9 | 12.25
30 | 2 | Performance data (cont) | 4 | 10 | 11.92
30 | 2 | Performance data (cont) | 5 | 1 | 14.83
30 | 2 | Performance data (cont) | 5 | 2 | 14.58
30 | 2 | Performance data (cont) | 5 | 3 | 14.25
30 | 2 | Performance data (cont) | 5 | 4 | 13.72
30 | 2 | Performance data (cont) | 5 | 5 | 13.67
30 | 2 | Performance data (cont) | 5 | 6 | 13.33
30 | 2 | Performance data (cont) | 5 | 7 | 13.08
30 | 2 | Performance data (cont) | 5 | 8 | 12.75
30 | 2 | Performance data (cont) | 5 | 9 | 12.5
30 | 2 | Performance data (cont) | 5 | 10 | 12.17
30 | 3 | Performance data (cont) | 1 | 1 | 0
30 | 3 | Performance data (cont) | 1 | 2 | 1/2
30 | 3 | Performance data (cont) | 1 | 3 | 1
30 | 3 | Performance data (cont) | 1 | 4 | 11/2
30 | 3 | Performance data (cont) | 1 | 5 | 2
30 | 3 | Performance data (cont) | 1 | 6 | 21/2
30 | 3 | Performance data (cont) | 1 | 7 | 3
30 | 3 | Performance data (cont) | 1 | 8 | 31/2
30 | 3 | Performance data (cont) | 1 | 9 | 4
30 | 3 | Performance data (cont) | 1 | 10 | 41/2
30 | 3 | Performance data (cont) | 2 | 1 | 1205
30 | 3 | Performance data (cont) | 2 | 2 | 1180
30 | 3 | Performance data (cont) | 2 | 3 | 1150
30 | 3 | Performance data (cont) | 2 | 4 | 1125
30 | 3 | Performance data (cont) | 2 | 5 | 1095
30 | 3 | Performance data (cont) | 2 | 6 | 1070
30 | 3 | Performance data (cont) | 2 | 7 | 1040
30 | 3 | Performance data (cont) | 2 | 8 | 1015
30 | 3 | Performance data (cont) | 2 | 9 | 985
30 | 3 | Performance data (cont) | 2 | 10 | 960
30 | 3 | Performance data (cont) | 3 | 1 | 880
30 | 3 | Performance data (cont) | 3 | 2 | 855
30 | 3 | Performance data (cont) | 3 | 3 | 830
30 | 3 | Performance data (cont) | 3 | 4 | 800
30 | 3 | Performance data (cont) | 3 | 5 | 775
30 | 3 | Performance data (cont) | 3 | 6 | 750
30 | 3 | Performance data (cont) | 3 | 7 | 725
30 | 3 | Performance data (cont) | 3 | 8 | 700
30 | 3 | Performance data (cont) | 3 | 9 | 675
30 | 3 | Performance data (cont) | 3 | 10 | 650
30 | 3 | Performance data (cont) | 4 | 1 | 900
30 | 3 | Performance data (cont) | 4 | 2 | 875
30 | 3 | Performance data (cont) | 4 | 3 | 855
30 | 3 | Performance data (cont) | 4 | 4 | 835
30 | 3 | Performance data (cont) | 4 | 5 | 815
30 | 3 | Performance data (cont) | 4 | 6 | 795
30 | 3 | Performance data (cont) | 4 | 7 | 775
30 | 3 | Performance data (cont) | 4 | 8 | 755
30 | 3 | Performance data (cont) | 4 | 9 | 735
30 | 3 | Performance data (cont) | 4 | 10 | 715
30 | 3 | Performance data (cont) | 5 | 1 | 890
30 | 3 | Performance data (cont) | 5 | 2 | 875
30 | 3 | Performance data (cont) | 5 | 3 | 855
30 | 3 | Performance data (cont) | 5 | 4 | 835
30 | 3 | Performance data (cont) | 5 | 5 | 820
30 | 3 | Performance data (cont) | 5 | 6 | 800
30 | 3 | Performance data (cont) | 5 | 7 | 785
30 | 3 | Performance data (cont) | 5 | 8 | 765
30 | 3 | Performance data (cont) | 5 | 9 | 750
30 | 3 | Performance data (cont) | 5 | 10 | 730
31 | 1 | DURABLADE ECONOMIZER | 1 | 1 | DURABLADE ECONOMIZER BAROMETRIC RELIEF DAMPER CHARACTERISTICS — 50TFF007 DURABLADE ECONOMIZER BAROMETRIC RELIEF DAMPER CHARACTERISTICS — 50TFF008-014
32 | 1 | Performance data (cont) | 1 | 1 | ECONOMI$ER BAROMETRIC FLOW 0.25 )gw 0.20 .ni( ERUSSERP 0.15 0.10 CITATS 0.05 0.00 0 500 1000 1500 2000 FLOW (CFM) SIZE 007 SIZES 008-014
32 | 1 | Performance data (cont) | 2 | 2 | 0.25 )gw 0.20 .ni( ERUSSERP 0.15 0.10 CITATS 0.05 0.00 0 500 1000 1500 2000 FLOW (CFM) SIZE 007 SIZES 008-014
32 | 1 | Performance data (cont) | 4 | 1 | ECONOMI$ER RETURN-AIR PRESSURE DROP 0.35 )gw 0.30 .ni( 0.25 ERUSSERP 0.20 0.15 0.10 CITATS 0.05 0.00 1200 2000 2800 3600 4400 FLOW (CFM) SIZE 007 SIZES 008-014
32 | 1 | Performance data (cont) | 4 | 2 | ECONOMI$ER RETURN-AIR PRESSURE DROP 0.35 )gw 0.30 .ni( 0.25 ERUSSERP 0.20 0.15
32 | 1 | Performance data (cont) | 5 | 2 | 0.35 )gw 0.30 .ni( 0.25 ERUSSERP 0.20 0.15
32 | 1 | Performance data (cont) | 10 | 2 | 0.10 CITATS 0.05 0.00 1200 2000 2800 3600 4400 FLOW (CFM) SIZE 007 SIZES 008-014
32 | 1 | Performance data (cont) | 13 | 2 | SIZE 007 SIZES 008-014
32 | 5 | Performance data (cont) | 1 | 1 | 50 40 )MFC( 30 WOLF 20 10 0 0 0.25 0.5 0.75 1 SIZE 007 STATIC PRESSURE (in. wg) SIZES 008-014
32 | 5 | Performance data (cont) | 2 | 1 | SIZE 007 SIZES 008-014
33 | 1 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 1 | 1 | 700
33 | 1 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 1 | 2 | 800
33 | 1 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 1 | 3 | 900
33 | 1 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 1 | 4 | 1000
33 | 1 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 1 | 5 | 1100
33 | 1 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 2 | 1 | 20
33 | 1 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 2 | 2 | 22
33 | 1 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 2 | 3 | 25
33 | 1 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 2 | 4 | 27
33 | 1 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 2 | 5 | 30
33 | 1 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 3 | 1 | 41
33 | 1 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 3 | 2 | 42
33 | 1 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 3 | 3 | 42
33 | 1 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 3 | 4 | 43
33 | 1 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 3 | 5 | 44
33 | 1 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4 | 1 | 12
33 | 1 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4 | 2 | 12
33 | 1 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4 | 3 | 12
33 | 1 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4 | 4 | 12
33 | 1 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4 | 5 | 12
33 | 1 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 5 | 1 | 32
33 | 1 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 5 | 2 | 40
33 | 1 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 5 | 3 | 50
33 | 1 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 5 | 4 | 63
33 | 1 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 5 | 5 | 77
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 1 | 1 | 800
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 1 | 2 | 900
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 1 | 3 | 1000
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 1 | 4 | 1100
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 1 | 5 | 1200
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 1 | 6 | 1300
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 1 | 7 | 1400
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 1 | 8 | 1500
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 1 | 9 | 1600
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 1 | 10 | 1700
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 1 | 11 | 1800
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 1 | 12 | 1900
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 1 | 13 | 2000
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 1 | 14 | 2100
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 1 | 15 | 2200
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 1 | 16 | 2300
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 2 | 1 | 1
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 2 | 2 | 2
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 2 | 3 | 4
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 2 | 4 | 6
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 2 | 5 | 8
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 2 | 6 | 10
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 2 | 7 | 12
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 2 | 8 | 14
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 2 | 9 | 16
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 2 | 10 | 18
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 2 | 11 | 19
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 2 | 12 | 21
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 2 | 13 | 23
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 2 | 14 | 25
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 2 | 15 | 27
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 2 | 16 | 29
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 3 | 1 | 5
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 3 | 2 | 7
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 3 | 3 | 9
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 3 | 4 | 10
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 3 | 5 | 12
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 3 | 6 | 15
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 3 | 7 | 17
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 3 | 8 | 20
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 3 | 9 | 22
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 3 | 10 | 25
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 3 | 11 | 27
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 3 | 12 | 29
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 3 | 13 | 32
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 3 | 14 | 34
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 3 | 15 | 37
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 3 | 16 | 39
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4 | 1 | 2
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4 | 2 | 3
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4 | 3 | 4
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4 | 4 | 5
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4 | 5 | 6
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4 | 6 | 7
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4 | 7 | 8
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4 | 8 | 9
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4 | 9 | 10
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4 | 10 | 11
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4 | 11 | 12
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4 | 12 | 13
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4 | 13 | 14
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4 | 14 | 15
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4 | 15 | 16
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4 | 16 | 17
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 5 | 1
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 5 | 2
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 5 | 3
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 5 | 4
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 5 | 5
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 5 | 6
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 5 | 7 | 31
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 5 | 8 | 35
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 5 | 9 | 41
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 5 | 10 | 50
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 5 | 11 | 59
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 5 | 12 | 67
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 5 | 13 | 75
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 5 | 14 | 84
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 5 | 15 | 90
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 5 | 16 | 97
33 | 3 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 1 | 1 | 1500
33 | 3 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 1 | 2 | 1600
33 | 3 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 1 | 3 | 1800
33 | 3 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 1 | 4 | 2000
33 | 3 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 1 | 5 | 2200
33 | 3 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 1 | 6 | 2400
33 | 3 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 2 | 1 | 0.09
33 | 3 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 2 | 2 | 0.09
33 | 3 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 2 | 3 | 0.1
33 | 3 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 2 | 4 | 0.11
33 | 3 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 2 | 5 | 0.11
33 | 3 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 2 | 6 | 0.12
33 | 3 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 3 | 1 | 0.16
33 | 3 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 3 | 2 | 0.16
33 | 3 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 3 | 3 | 0.17
33 | 3 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 3 | 4 | 0.17
33 | 3 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 3 | 5 | 0.17
33 | 3 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 3 | 6 | 0.18
33 | 3 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4 | 1 | 0.05
33 | 3 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4 | 2 | 0.05
33 | 3 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4 | 3 | 0.05
33 | 3 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4 | 4 | 0.05
33 | 3 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4 | 5 | 0.05
33 | 3 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4 | 6 | 0.05
33 | 3 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 5 | 1 | 0.13
33 | 3 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 5 | 2 | 0.15
33 | 3 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 5 | 3 | 0.19
33 | 3 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 5 | 4 | 0.24
33 | 3 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 5 | 5 | 0.29
33 | 3 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 5 | 6 | 0.35
33 | 4 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 1 | 1 | 1900
33 | 4 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 1 | 2 | 2200
33 | 4 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 1 | 3 | 2500
33 | 4 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 1 | 4 | 3000
33 | 4 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 1 | 5 | 3500
33 | 4 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 1 | 6 | 4000
33 | 4 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 1 | 7 | 4500
33 | 4 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 1 | 8 | 5000
33 | 4 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 2 | 1 | 0.01
33 | 4 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 2 | 2 | 0.02
33 | 4 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 2 | 3 | 0.03
33 | 4 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 2 | 4 | 0.05
33 | 4 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 2 | 5 | 0.07
33 | 4 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 2 | 6 | 0.08
33 | 4 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 2 | 7 | 0.1
33 | 4 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 2 | 8 | 0.12
33 | 4 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 3 | 1 | 0.02
33 | 4 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 3 | 2 | 0.03
33 | 4 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 3 | 3 | 0.05
33 | 4 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 3 | 4 | 0.07
33 | 4 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 3 | 5 | 0.09
33 | 4 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 3 | 6 | 0.12
33 | 4 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 3 | 7 | 0.14
33 | 4 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 3 | 8 | 0.16
33 | 4 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4 | 1 | 0.02
33 | 4 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4 | 2 | 0.02
33 | 4 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4 | 3 | 0.02
33 | 4 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4 | 4 | 0.03
33 | 4 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4 | 5 | 0.04
33 | 4 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4 | 6 | 0.05
33 | 4 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4 | 7 | 0.06
33 | 4 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4 | 8 | 0.07
33 | 4 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 5 | 1
33 | 4 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 5 | 2
33 | 4 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 5 | 3
33 | 4 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 5 | 4 | 0.125
33 | 4 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 5 | 5 | 0.18
33 | 4 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 5 | 6 | 0.27
33 | 4 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 5 | 7 | 0.34
33 | 4 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 5 | 8 | 0.4
33 | 5 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 1 | 1 | UNIT ELECTRICAL CHARACTERISTICS
33 | 5 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 1 | 2 | ACCESSORY kW
33 | 5 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 2 | 1 | 400-3-50
33 | 5 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 2 | 2 | 4.2 8.0 9.7 16.0* 17.7*
33 | 5 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 3 | 1 | 400-3-50
33 | 5 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 3 | 2 | 9.7 11.5 19.3 22.9 29.0*
33 | 5 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4 | 1 | 400-3-50
33 | 5 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4 | 2 | 9.7 11.5 19.3 22.9 29.0*
33 | 5 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 5 | 1 | 400-3-50
33 | 5 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 5 | 2 | 9.7† 11.5** 19.3 22.9 29.0 34.7*
34 | 1 | Electrical data | 1 | 1 | NOMINAL VOLTAGE (50 Hz)
34 | 1 | Electrical data | 1 | 2 | VOLTAGE RANGE
34 | 1 | Electrical data | 1 | 4 | COMPR (ea)
34 | 1 | Electrical data | 1 | 6 | OFM (ea)
34 | 1 | Electrical data | 1 | 7 | IFM
34 | 1 | Electrical data | 1 | 8 | ELECTRIC HEAT*
34 | 1 | Electrical data | 1 | 10 | POWER SUPPLY
34 | 1 | Electrical data | 2 | 2 | Min
34 | 1 | Electrical data | 2 | 3 | Max
34 | 1 | Electrical data | 2 | 4 | RLA
34 | 1 | Electrical data | 2 | 5 | LRA
34 | 1 | Electrical data | 2 | 6 | FLA
34 | 1 | Electrical data | 2 | 7 | FLA
34 | 1 | Electrical data | 2 | 8 | Nominal kW†
34 | 1 | Electrical data | 2 | 9 | FLA
34 | 1 | Electrical data | 2 | 10 | MCA
34 | 1 | Electrical data | 2 | 11 | MOCP**
34 | 1 | Electrical data | 2 | 12 | FLA
34 | 1 | Electrical data | 3 | 1 | 400 (3 phase)
34 | 1 | Electrical data | 3 | 2 | 360
34 | 1 | Electrical data | 3 | 3 | 440
34 | 1 | Electrical data | 3 | 4 | 9.9
34 | 1 | Electrical data | 3 | 5 | 72
34 | 1 | Electrical data | 3 | 6 | 0.6
34 | 1 | Electrical data | 3 | 7 | 2.6
34 | 1 | Electrical data | 3 | 8 | — 4.2 8.0 9.7 16.0 17.7
34 | 1 | Electrical data | 3 | 9 | — 7.2 13.8 16.8 27.8 30.7
34 | 1 | Electrical data | 3 | 10 | 18.4 18.4 18.4 20.8 32.1 34.6
34 | 1 | Electrical data | 3 | 11 | 25 25 25 25 35 35
34 | 1 | Electrical data | 3 | 12 | 18 18 18 19 30 32
34 | 1 | Electrical data | 4 | 1 | 400 (3 phase)
34 | 1 | Electrical data | 4 | 2 | 360
34 | 1 | Electrical data | 4 | 3 | 440
34 | 1 | Electrical data | 4 | 4 | 8.9
34 | 1 | Electrical data | 4 | 5 | 42
34 | 1 | Electrical data | 4 | 6 | 0.6
34 | 1 | Electrical data | 4 | 7 | 2.6
34 | 1 | Electrical data | 4 | 8 | — 9.7 11.5 19.3 22.9 29.0
34 | 1 | Electrical data | 4 | 9 | — 13.9 16.5 27.8 33.1 41.8
34 | 1 | Electrical data | 4 | 10 | 23.8 23.8 23.9 38.1 44.6 55.5
34 | 1 | Electrical data | 4 | 11 | 30 30 25 40 45 60
34 | 1 | Electrical data | 4 | 12 | 25 25 25 35 41 51
34 | 1 | Electrical data | 5 | 1 | 400 (3 phase)
34 | 1 | Electrical data | 5 | 2 | 360
34 | 1 | Electrical data | 5 | 3 | 440
34 | 1 | Electrical data | 5 | 4 | 8.3
34 | 1 | Electrical data | 5 | 5 | 69
34 | 1 | Electrical data | 5 | 6 | 0.6
34 | 1 | Electrical data | 5 | 7 | 2.6
34 | 1 | Electrical data | 5 | 8 | — 9.7 11.5 19.3 22.9 29.0
34 | 1 | Electrical data | 5 | 9 | — 13.9 16.5 27.8 33.1 41.8
34 | 1 | Electrical data | 5 | 10 | 22.5 22.5 23.9 38.1 44.6 55.5
34 | 1 | Electrical data | 5 | 11 | 25 25 25 40 45 60
34 | 1 | Electrical data | 5 | 12 | 23 23 23 35 41 51
34 | 1 | Electrical data | 6 | 1 | 400 (3 phase)
34 | 1 | Electrical data | 6 | 2 | 360
34 | 1 | Electrical data | 6 | 3 | 440
34 | 1 | Electrical data | 6 | 4 | 8.9
34 | 1 | Electrical data | 6 | 5 | 64
34 | 1 | Electrical data | 6 | 6 | 0.6
34 | 1 | Electrical data | 6 | 7 | 2.6
34 | 1 | Electrical data | 6 | 8 | — 9.7 19.3 22.9 29.0 34.7
34 | 1 | Electrical data | 6 | 9 | — 16.5 27.8 33.1 41.8 50.1
34 | 1 | Electrical data | 6 | 10 | 23.8 23.9 38.1 44.6 55.5 65.9
34 | 1 | Electrical data | 6 | 11 | 30 30 40 45 60 70††
34 | 1 | Electrical data | 6 | 12 | 25 25 35 41 51 61
34 | 1 | Electrical data | 7 | 1 | 400 (3 phase)
34 | 1 | Electrical data | 7 | 2 | 360
34 | 1 | Electrical data | 7 | 3 | 440
34 | 1 | Electrical data | 7 | 4 | 10.4
34 | 1 | Electrical data | 7 | 5 | 73
34 | 1 | Electrical data | 7 | 6 | 0.6
34 | 1 | Electrical data | 7 | 7 | 4.8
34 | 1 | Electrical data | 7 | 8 | — 11.5 19.3 22.9 29.0 34.7
34 | 1 | Electrical data | 7 | 9 | — 16.5 27.8 33.1 41.8 50.1
34 | 1 | Electrical data | 7 | 10 | 29.4 29.4 40.8 47.3 58.2 68.6
34 | 1 | Electrical data | 7 | 11 | 35 35 45 50 60 70††
34 | 1 | Electrical data | 7 | 12 | 31 31 38 44 54 63

## Performance_Tables
source_page | table_no | page_title | row_no | column_no | cell_value
15 | 1 | Performance data | 1 | 1 | 700/0.05
15 | 1 | Performance data | 1 | 2 | 950/0.07
15 | 2 | Performance data | 1 | 2 | 13
15 | 2 | Performance data | 1 | 3 | 16
15 | 2 | Performance data | 1 | 4 | 19
15 | 2 | Performance data | 1 | 5 | 22
15 | 2 | Performance data | 1 | 6 | 13
15 | 2 | Performance data | 1 | 7 | 16
15 | 2 | Performance data | 1 | 8 | 19
15 | 2 | Performance data | 1 | 9 | 22
15 | 2 | Performance data | 1 | 10 | 13
15 | 2 | Performance data | 1 | 11 | 16
15 | 2 | Performance data | 1 | 12 | 19
15 | 2 | Performance data | 2 | 1 | TC SHC kW
15 | 2 | Performance data | 2 | 2 | 15.8 15.8 3.98
15 | 2 | Performance data | 2 | 3 | 17.7 15.5 4.11
15 | 2 | Performance data | 2 | 4 | 19.6 13.1 4.25
15 | 2 | Performance data | 2 | 5 | 21.5 10.4 4.39
15 | 2 | Performance data | 2 | 6 | 16.8 16.8 4.08
15 | 2 | Performance data | 2 | 7 | 18.7 18.1 4.21
15 | 2 | Performance data | 2 | 8 | 20.7 14.9 4.35
15 | 2 | Performance data | 2 | 9 | 22.6 11.6 4.49
15 | 2 | Performance data | 2 | 10 | 17.4 17.4 4.12
15 | 2 | Performance data | 2 | 11 | 19.3 19.3 4.27
15 | 2 | Performance data | 2 | 12 | 21.3 16.6 4.41
15 | 2 | Performance data | 3 | 1 | TC SHC kW
15 | 2 | Performance data | 3 | 2 | 15.2 15.2 4.26
15 | 2 | Performance data | 3 | 3 | 17.1 15.3 4.41
15 | 2 | Performance data | 3 | 4 | 19.0 12.8 4.56
15 | 2 | Performance data | 3 | 5 | 20.6 10.2 4.71
15 | 2 | Performance data | 3 | 6 | 16.2 16.2 4.38
15 | 2 | Performance data | 3 | 7 | 18.1 17.9 4.51
15 | 2 | Performance data | 3 | 8 | 20.1 14.7 4.66
15 | 2 | Performance data | 3 | 9 | 22.0 11.4 4.82
15 | 2 | Performance data | 3 | 10 | 17.0 17.0 4.43
15 | 2 | Performance data | 3 | 11 | 18.8 18.8 4.58
15 | 2 | Performance data | 3 | 12 | 20.7 16.4 4.73
15 | 2 | Performance data | 4 | 1 | TC SHC kW
15 | 2 | Performance data | 4 | 2 | 14.7 14.7 4.54
15 | 2 | Performance data | 4 | 3 | 16.5 15.0 4.70
15 | 2 | Performance data | 4 | 4 | 18.4 12.6 4.87
15 | 2 | Performance data | 4 | 5 | 20.3 10.0 5.04
15 | 2 | Performance data | 4 | 6 | 15.6 15.6 4.66
15 | 2 | Performance data | 4 | 7 | 17.5 17.5 4.82
15 | 2 | Performance data | 4 | 8 | 19.4 14.5 4.98
15 | 2 | Performance data | 4 | 9 | 21.3 11.2 5.15
15 | 2 | Performance data | 4 | 10 | 16.6 16.6 4.74
15 | 2 | Performance data | 4 | 11 | 18.2 18.2 4.89
15 | 2 | Performance data | 4 | 12 | 20.0 16.1 5.05
15 | 2 | Performance data | 5 | 1 | TC SHC kW
15 | 2 | Performance data | 5 | 2 | 14.1 14.1 4.81
15 | 2 | Performance data | 5 | 3 | 15.9 14.7 4.99
15 | 2 | Performance data | 5 | 4 | 17.8 12.3 5.17
15 | 2 | Performance data | 5 | 5 | 19.7 9.8 5.36
15 | 2 | Performance data | 5 | 6 | 15.0 15.0 4.92
15 | 2 | Performance data | 5 | 7 | 16.9 16.9 5.10
15 | 2 | Performance data | 5 | 8 | 18.8 14.3 5.29
15 | 2 | Performance data | 5 | 9 | 20.7 11.0 5.48
15 | 2 | Performance data | 5 | 10 | 16.2 16.2 5.05
15 | 2 | Performance data | 5 | 11 | 17.7 17.7 5.20
15 | 2 | Performance data | 5 | 12 | 19.4 15.8 5.37
15 | 2 | Performance data | 6 | 1 | TC SHC kW
15 | 2 | Performance data | 6 | 2 | 13.7 13.7 5.01
15 | 2 | Performance data | 6 | 3 | 15.5 14.5 5.20
15 | 2 | Performance data | 6 | 4 | 17.3 12.2 5.39
15 | 2 | Performance data | 6 | 5 | 19.3 9.6 5.60
15 | 2 | Performance data | 6 | 6 | 14.5 14.5 5.12
15 | 2 | Performance data | 6 | 7 | 16.4 16.4 5.31
15 | 2 | Performance data | 6 | 8 | 18.2 14.1 5.52
15 | 2 | Performance data | 6 | 9 | 20.2 10.9 5.73
15 | 2 | Performance data | 6 | 10 | 15.8 15.8 5.28
15 | 2 | Performance data | 6 | 11 | 17.3 17.3 5.61
15 | 2 | Performance data | 6 | 12 | 18.8 15.6 5.61
15 | 2 | Performance data | 7 | 1 | TC SHC kW
15 | 2 | Performance data | 7 | 2 | 12.7 12.7 5.33
15 | 2 | Performance data | 7 | 3 | 14.6 14.1 5.54
15 | 2 | Performance data | 7 | 4 | 16.5 11.8 5.76
15 | 2 | Performance data | 7 | 5 | 18.3 9.3 5.99
15 | 2 | Performance data | 7 | 6 | 14.0 14.0 5.46
15 | 2 | Performance data | 7 | 7 | 15.6 15.6 5.68
15 | 2 | Performance data | 7 | 8 | 17.3 13.7 5.90
15 | 2 | Performance data | 7 | 9 | 19.2 10.6 6.13
15 | 2 | Performance data | 7 | 10 | 15.4 15.4 5.68
15 | 2 | Performance data | 7 | 11 | 16.6 16.6 5.83
15 | 2 | Performance data | 7 | 12 | 17.9 15.2 5.99
15 | 2 | Performance data | 8 | 1 | TC SHC kW
15 | 2 | Performance data | 8 | 2 | 12.0 12.0 5.60
15 | 2 | Performance data | 8 | 3 | 13.8 13.8 5.82
15 | 2 | Performance data | 8 | 4 | 15.8 11.5 6.05
15 | 2 | Performance data | 8 | 5 | 17.6 9.1 6.29
15 | 2 | Performance data | 8 | 6 | 13.5 13.5 5.75
15 | 2 | Performance data | 8 | 7 | 15.1 15.1 5.97
15 | 2 | Performance data | 8 | 8 | 16.7 13.4 6.20
15 | 2 | Performance data | 8 | 9 | 18.5 10.3 6.45
15 | 2 | Performance data | 8 | 10 | 15.1 15.1 5.99
15 | 2 | Performance data | 8 | 11 | 16.1 16.1 6.14
15 | 2 | Performance data | 8 | 12 | 17.2 14.8 6.31
15 | 2 | Performance data | 9 | 1 | TC SHC kW
15 | 2 | Performance data | 9 | 2 | 11.2 11.2 5.85
15 | 2 | Performance data | 9 | 3 | 13.1 13.1 6.09
15 | 2 | Performance data | 9 | 4 | 15.1 11.2 6.34
15 | 2 | Performance data | 9 | 5 | 16.9 8.8 6.60
15 | 2 | Performance data | 9 | 6 | 13.0 13.0 6.04
15 | 2 | Performance data | 9 | 7 | 14.5 14.5 6.26
15 | 2 | Performance data | 9 | 8 | 15.9 13.1 6.50
15 | 2 | Performance data | 9 | 9 | 17.7 10.0 6.76
15 | 2 | Performance data | 9 | 10 | 14.8 14.8 6.31
15 | 2 | Performance data | 9 | 11 | 15.5 15.5 6.46
15 | 2 | Performance data | 9 | 12 | 16.5 14.4 6.61
15 | 2 | Performance data | 10 | 1 | TC SHC kW
15 | 2 | Performance data | 10 | 2 | 10.5 10.5 6.11
15 | 2 | Performance data | 10 | 3 | 12.4 12.4 6.36
15 | 2 | Performance data | 10 | 4 | 14.4 11.0 6.63
15 | 2 | Performance data | 10 | 5 | 16.2 8.6 6.91
15 | 2 | Performance data | 10 | 6 | 12.7 12.7 6.31
15 | 2 | Performance data | 10 | 7 | 13.9 13.9 6.56
15 | 2 | Performance data | 10 | 8 | 15.3 12.8 6.81
15 | 2 | Performance data | 10 | 9 | 16.9 9.8 7.08
15 | 2 | Performance data | 10 | 10 | 14.4 14.4 6.62
15 | 2 | Performance data | 10 | 11 | 15.0 15.0 6.77
15 | 2 | Performance data | 10 | 12 | 15.7 14.1 6.92
16 | 1 | Performance data (cont) | 1 | 2 | 14
16 | 1 | Performance data (cont) | 1 | 3 | 16
16 | 1 | Performance data (cont) | 1 | 4 | 18
16 | 1 | Performance data (cont) | 1 | 5 | 20
16 | 1 | Performance data (cont) | 1 | 6 | 22
16 | 1 | Performance data (cont) | 1 | 7 | 14
16 | 1 | Performance data (cont) | 1 | 8 | 16
16 | 1 | Performance data (cont) | 1 | 9 | 18
16 | 1 | Performance data (cont) | 1 | 10 | 20
16 | 1 | Performance data (cont) | 2 | 1 | TC SHC kW
16 | 1 | Performance data (cont) | 2 | 2 | 19.5 19.4 5.02
16 | 1 | Performance data (cont) | 2 | 3 | 20.9 18.0 5.16
16 | 1 | Performance data (cont) | 2 | 4 | 22.5 16.2 5.34
16 | 1 | Performance data (cont) | 2 | 5 | 24.3 14.3 5.54
16 | 1 | Performance data (cont) | 2 | 6 | 26.0 12.3 5.72
16 | 1 | Performance data (cont) | 2 | 7 | 21.6 21.4 5.28
16 | 1 | Performance data (cont) | 2 | 8 | 22.3 20.5 5.37
16 | 1 | Performance data (cont) | 2 | 9 | 23.7 18.5 5.52
16 | 1 | Performance data (cont) | 2 | 10 | 25.3 16.1 5.70
16 | 1 | Performance data (cont) | 3 | 1 | TC SHC kW
16 | 1 | Performance data (cont) | 3 | 2 | 19.1 18.9 5.25
16 | 1 | Performance data (cont) | 3 | 3 | 20.4 17.7 5.38
16 | 1 | Performance data (cont) | 3 | 4 | 21.9 16.0 5.56
16 | 1 | Performance data (cont) | 3 | 5 | 23.7 14.1 5.76
16 | 1 | Performance data (cont) | 3 | 6 | 25.4 12.1 5.96
16 | 1 | Performance data (cont) | 3 | 7 | 21.0 21.0 5.51
16 | 1 | Performance data (cont) | 3 | 8 | 21.7 20.2 5.58
16 | 1 | Performance data (cont) | 3 | 9 | 23.1 18.3 5.74
16 | 1 | Performance data (cont) | 3 | 10 | 24.7 15.9 5.92
16 | 1 | Performance data (cont) | 4 | 1 | TC SHC kW
16 | 1 | Performance data (cont) | 4 | 2 | 18.6 18.4 5.49
16 | 1 | Performance data (cont) | 4 | 3 | 19.8 17.3 5.61
16 | 1 | Performance data (cont) | 4 | 4 | 21.3 15.7 5.78
16 | 1 | Performance data (cont) | 4 | 5 | 23.0 13.9 5.98
16 | 1 | Performance data (cont) | 4 | 6 | 24.8 11.9 6.19
16 | 1 | Performance data (cont) | 4 | 7 | 20.5 20.5 5.74
16 | 1 | Performance data (cont) | 4 | 8 | 21.1 19.8 5.8
16 | 1 | Performance data (cont) | 4 | 9 | 22.4 18.0 5.96
16 | 1 | Performance data (cont) | 4 | 10 | 24.1 15.7 6.15
16 | 1 | Performance data (cont) | 5 | 1 | TC SHC kW
16 | 1 | Performance data (cont) | 5 | 2 | 18.0 17.8 5.77
16 | 1 | Performance data (cont) | 5 | 3 | 19.1 16.9 5.88
16 | 1 | Performance data (cont) | 5 | 4 | 20.6 15.4 6.04
16 | 1 | Performance data (cont) | 5 | 5 | 22.2 13.6 6.25
16 | 1 | Performance data (cont) | 5 | 6 | 23.9 11.6 6.47
16 | 1 | Performance data (cont) | 5 | 7 | 19.9 19.8 6.03
16 | 1 | Performance data (cont) | 5 | 8 | 20.3 19.4 6.07
16 | 1 | Performance data (cont) | 5 | 9 | 21.5 17.7 6.22
16 | 1 | Performance data (cont) | 5 | 10 | 23.2 15.4 6.43
16 | 1 | Performance data (cont) | 6 | 1 | TC SHC kW
16 | 1 | Performance data (cont) | 6 | 2 | 17.3 17.2 6.09
16 | 1 | Performance data (cont) | 6 | 3 | 18.2 16.4 6.18
16 | 1 | Performance data (cont) | 6 | 4 | 19.63 15.0 6.34
16 | 1 | Performance data (cont) | 6 | 5 | 21.3 13.2 6.55
16 | 1 | Performance data (cont) | 6 | 6 | 23.0 11.3 6.77
16 | 1 | Performance data (cont) | 6 | 7 | 18.2 19.1 6.33
16 | 1 | Performance data (cont) | 6 | 8 | 19.4 18.9 6.37
16 | 1 | Performance data (cont) | 6 | 9 | 20.6 17.3 6.61
16 | 1 | Performance data (cont) | 6 | 10 | 22.3 15.0 6.73
16 | 1 | Performance data (cont) | 7 | 1 | TC SHC kW
16 | 1 | Performance data (cont) | 7 | 2 | 16.6 16.6 6.40
16 | 1 | Performance data (cont) | 7 | 3 | 18.3 15.9 6.48
16 | 1 | Performance data (cont) | 7 | 4 | 18.7 14.6 6.63
16 | 1 | Performance data (cont) | 7 | 5 | 20.3 12.8 6.84
16 | 1 | Performance data (cont) | 7 | 6 | 22.0 10.9 7.07
16 | 1 | Performance data (cont) | 7 | 7 | 18.4 18.4 6.65
16 | 1 | Performance data (cont) | 7 | 8 | 18.6 18.3 6.67
16 | 1 | Performance data (cont) | 7 | 9 | 19.6 16.9 6.81
16 | 1 | Performance data (cont) | 7 | 10 | 21.3 14.7 7.02
16 | 1 | Performance data (cont) | 8 | 1 | TC SHC kW
16 | 1 | Performance data (cont) | 8 | 2 | 15.9 15.9 6.71
16 | 1 | Performance data (cont) | 8 | 3 | 16.4 15.4 6.77
16 | 1 | Performance data (cont) | 8 | 4 | 17.7 14.2 6.92
16 | 1 | Performance data (cont) | 8 | 5 | 19.4 12.5 7.13
16 | 1 | Performance data (cont) | 8 | 6 | 21.0 10.6 7.36
16 | 1 | Performance data (cont) | 8 | 7 | 17.7 17.7 6.97
16 | 1 | Performance data (cont) | 8 | 8 | 17.7 17.6 6.97
16 | 1 | Performance data (cont) | 8 | 9 | 18.7 16.4 7.10
16 | 1 | Performance data (cont) | 8 | 10 | 20.2 14.3 7.30
16 | 1 | Performance data (cont) | 9 | 1 | TC SHC kW
16 | 1 | Performance data (cont) | 9 | 2 | 15.2 15.2 7.02
16 | 1 | Performance data (cont) | 9 | 3 | 15.5 14.9 7.05
16 | 1 | Performance data (cont) | 9 | 4 | 16.7 13.8 7.20
16 | 1 | Performance data (cont) | 9 | 5 | 18.3 12.1 7.41
16 | 1 | Performance data (cont) | 9 | 6 | 19.9 10.2 7.64
16 | 1 | Performance data (cont) | 9 | 7 | 16.9 16.9 7.27
16 | 1 | Performance data (cont) | 9 | 8 | 16.9 16.9 7.27
16 | 1 | Performance data (cont) | 9 | 9 | 17.7 15.8 7.39
16 | 1 | Performance data (cont) | 9 | 10 | 19.1 13.9 7.57
16 | 1 | Performance data (cont) | 10 | 1 | TC SHC kW
16 | 1 | Performance data (cont) | 10 | 2 | 14.4 14.4 7.33
16 | 1 | Performance data (cont) | 10 | 3 | 14.5 14.3 7.33
16 | 1 | Performance data (cont) | 10 | 4 | 15.6 13.3 7.47
16 | 1 | Performance data (cont) | 10 | 5 | 17.3 11.7 7.67
16 | 1 | Performance data (cont) | 10 | 6 | 18.8 9.9 7.91
16 | 1 | Performance data (cont) | 10 | 7 | 16.1 16.1 7.56
16 | 1 | Performance data (cont) | 10 | 8 | 16.1 16.1 7.57
16 | 1 | Performance data (cont) | 10 | 9 | 16.8 15.2 7.67
16 | 1 | Performance data (cont) | 10 | 10 | 18.0 13.5 7.85
16 | 2 | Performance data (cont) | 1 | 2 | 14
16 | 2 | Performance data (cont) | 1 | 3 | 16
16 | 2 | Performance data (cont) | 1 | 4 | 18
16 | 2 | Performance data (cont) | 1 | 5 | 20
16 | 2 | Performance data (cont) | 1 | 6 | 22
16 | 2 | Performance data (cont) | 1 | 7 | 14
16 | 2 | Performance data (cont) | 1 | 8 | 16
16 | 2 | Performance data (cont) | 1 | 9 | 18
16 | 2 | Performance data (cont) | 1 | 10 | 20
16 | 2 | Performance data (cont) | 2 | 1 | TC SHC kW
16 | 2 | Performance data (cont) | 2 | 2 | 21.8 21.8 5.33
16 | 2 | Performance data (cont) | 2 | 3 | 22.5 20.9 5.41
16 | 2 | Performance data (cont) | 2 | 4 | 23.9 18.9 5.55
16 | 2 | Performance data (cont) | 2 | 5 | 25.5 16.4 5.73
16 | 2 | Performance data (cont) | 2 | 6 | 27.1 13.6 5.91
16 | 2 | Performance data (cont) | 2 | 7 | 22.9 22.8 5.49
16 | 2 | Performance data (cont) | 2 | 8 | 23.1 22.4 5.51
16 | 2 | Performance data (cont) | 2 | 9 | 24.3 20.5 5.65
16 | 2 | Performance data (cont) | 2 | 10 | 26.1 17.7 5.83
16 | 2 | Performance data (cont) | 3 | 1 | TC SHC kW
16 | 2 | Performance data (cont) | 3 | 2 | 21.3 21.2 5.55
16 | 2 | Performance data (cont) | 3 | 3 | 21.9 20.6 5.62
16 | 2 | Performance data (cont) | 3 | 4 | 23.3 18.7 5.77
16 | 2 | Performance data (cont) | 3 | 5 | 24.9 16.2 5.96
16 | 2 | Performance data (cont) | 3 | 6 | 26.5 13.5 6.14
16 | 2 | Performance data (cont) | 3 | 7 | 22.4 22.3 5.72
16 | 2 | Performance data (cont) | 3 | 8 | 22.5 22.0 5.73
16 | 2 | Performance data (cont) | 3 | 9 | 23.7 20.2 5.86
16 | 2 | Performance data (cont) | 3 | 10 | 25.4 17.5 6.05
16 | 2 | Performance data (cont) | 4 | 1 | TC SHC kW
16 | 2 | Performance data (cont) | 4 | 2 | 20.8 20.7 5.78
16 | 2 | Performance data (cont) | 4 | 3 | 21.2 20.2 5.84
16 | 2 | Performance data (cont) | 4 | 4 | 22.5 18.4 5.98
16 | 2 | Performance data (cont) | 4 | 5 | 24.2 16.0 6.17
16 | 2 | Performance data (cont) | 4 | 6 | 25.9 13.3 6.38
16 | 2 | Performance data (cont) | 4 | 7 | 21.8 21.8 5.94
16 | 2 | Performance data (cont) | 4 | 8 | 21.9 21.7 5.96
16 | 2 | Performance data (cont) | 4 | 9 | 23.1 20.0 6.08
16 | 2 | Performance data (cont) | 4 | 10 | 24.7 17.3 6.28
16 | 2 | Performance data (cont) | 5 | 1 | TC SHC kW
16 | 2 | Performance data (cont) | 5 | 2 | 20.2 20.2 6.07
16 | 2 | Performance data (cont) | 5 | 3 | 20.5 19.8 6.11
16 | 2 | Performance data (cont) | 5 | 4 | 21.7 18.1 6.25
16 | 2 | Performance data (cont) | 5 | 5 | 23.4 15.7 6.45
16 | 2 | Performance data (cont) | 5 | 6 | 25.2 13.0 6.66
16 | 2 | Performance data (cont) | 5 | 7 | 21.2 21.2 6.23
16 | 2 | Performance data (cont) | 5 | 8 | 21.2 21.0 6.23
16 | 2 | Performance data (cont) | 5 | 9 | 22.2 19.5 6.36
16 | 2 | Performance data (cont) | 5 | 10 | 23.8 17.0 6.54
16 | 2 | Performance data (cont) | 6 | 1 | TC SHC kW
16 | 2 | Performance data (cont) | 6 | 2 | 19.5 19.4 6.39
16 | 2 | Performance data (cont) | 6 | 3 | 19.6 19.2 6.41
16 | 2 | Performance data (cont) | 6 | 4 | 20.7 17.7 6.55
16 | 2 | Performance data (cont) | 6 | 5 | 22.4 15.3 6.75
16 | 2 | Performance data (cont) | 6 | 6 | 24.1 12.7 6.96
16 | 2 | Performance data (cont) | 6 | 7 | 20.4 20.4 6.54
16 | 2 | Performance data (cont) | 6 | 8 | 20.4 20.4 6.54
16 | 2 | Performance data (cont) | 6 | 9 | 20.7 19.0 6.66
16 | 2 | Performance data (cont) | 6 | 10 | 22.8 16.6 6.84
16 | 2 | Performance data (cont) | 7 | 1 | TC SHC kW
16 | 2 | Performance data (cont) | 7 | 2 | 18.7 18.7 6.69
16 | 2 | Performance data (cont) | 7 | 3 | 18.7 18.6 6.70
16 | 2 | Performance data (cont) | 7 | 4 | 19.8 17.2 6.83
16 | 2 | Performance data (cont) | 7 | 5 | 21.3 15.0 7.04
16 | 2 | Performance data (cont) | 7 | 6 | 23.1 12.4 7.26
16 | 2 | Performance data (cont) | 7 | 7 | 19.6 19.6 6.86
16 | 2 | Performance data (cont) | 7 | 8 | 19.6 19.6 6.86
16 | 2 | Performance data (cont) | 7 | 9 | 20.4 18.4 6.95
16 | 2 | Performance data (cont) | 7 | 10 | 21.7 16.3 7.12
16 | 2 | Performance data (cont) | 8 | 1 | TC SHC kW
16 | 2 | Performance data (cont) | 8 | 2 | 17.9 17.9 7.01
16 | 2 | Performance data (cont) | 8 | 3 | 17.9 17.9 7.01
16 | 2 | Performance data (cont) | 8 | 4 | 18.8 16.7 7.13
16 | 2 | Performance data (cont) | 8 | 5 | 20.3 14.6 7.33
16 | 2 | Performance data (cont) | 8 | 6 | 22.0 12.1 7.55
16 | 2 | Performance data (cont) | 8 | 7 | 18.8 18.8 7.16
16 | 2 | Performance data (cont) | 8 | 8 | 18.8 18.8 7.16
16 | 2 | Performance data (cont) | 8 | 9 | 19.4 17.8 7.25
16 | 2 | Performance data (cont) | 8 | 10 | 20.6 15.9 7.41
16 | 2 | Performance data (cont) | 9 | 1 | TC SHC kW
16 | 2 | Performance data (cont) | 9 | 2 | 17.1 17.1 7.31
16 | 2 | Performance data (cont) | 9 | 3 | 17.1 17.1 7.31
16 | 2 | Performance data (cont) | 9 | 4 | 17.9 16.1 7.42
16 | 2 | Performance data (cont) | 9 | 5 | 19.2 14.2 7.59
16 | 2 | Performance data (cont) | 9 | 6 | 20.8 11.7 7.83
16 | 2 | Performance data (cont) | 9 | 7 | 17.9 17.9 7.46
16 | 2 | Performance data (cont) | 9 | 8 | 17.9 17.9 7.47
16 | 2 | Performance data (cont) | 9 | 9 | 18.5 17.2 7.54
16 | 2 | Performance data (cont) | 9 | 10 | 19.5 15.5 7.69
16 | 2 | Performance data (cont) | 10 | 1 | TC SHC kW
16 | 2 | Performance data (cont) | 10 | 2 | 16.3 16.3 7.61
16 | 2 | Performance data (cont) | 10 | 3 | 16.3 16.3 7.61
16 | 2 | Performance data (cont) | 10 | 4 | 16.9 15.4 7.70
16 | 2 | Performance data (cont) | 10 | 5 | 18.0 13.9 7.87
16 | 2 | Performance data (cont) | 10 | 6 | 19.6 11.4 8.1
16 | 2 | Performance data (cont) | 10 | 7 | 17.1 17.1 7.76
16 | 2 | Performance data (cont) | 10 | 8 | 17.1 17.1 7.77
16 | 2 | Performance data (cont) | 10 | 9 | 17.4 16.5 7.82
16 | 2 | Performance data (cont) | 10 | 10 | 18.3 15.1 7.95
17 | 1 | COOLING CAPACITIES — SI (cont) | 1 | 1 | 1200/0.07
17 | 1 | COOLING CAPACITIES — SI (cont) | 1 | 2 | 1400/.08
17 | 2 | COOLING CAPACITIES — SI (cont) | 1 | 2 | 13
17 | 2 | COOLING CAPACITIES — SI (cont) | 1 | 3 | 16
17 | 2 | COOLING CAPACITIES — SI (cont) | 1 | 4 | 19
17 | 2 | COOLING CAPACITIES — SI (cont) | 1 | 5 | 22
17 | 2 | COOLING CAPACITIES — SI (cont) | 1 | 6 | 13
17 | 2 | COOLING CAPACITIES — SI (cont) | 1 | 7 | 16
17 | 2 | COOLING CAPACITIES — SI (cont) | 1 | 8 | 19
17 | 2 | COOLING CAPACITIES — SI (cont) | 1 | 9 | 22
17 | 2 | COOLING CAPACITIES — SI (cont) | 1 | 10 | 13
17 | 2 | COOLING CAPACITIES — SI (cont) | 1 | 11 | 16
17 | 2 | COOLING CAPACITIES — SI (cont) | 1 | 12 | 19
17 | 2 | COOLING CAPACITIES — SI (cont) | 2 | 1 | TC SHC kW
17 | 2 | COOLING CAPACITIES — SI (cont) | 2 | 2 | 24.7 24.1 6.25
17 | 2 | COOLING CAPACITIES — SI (cont) | 2 | 3 | 25.2 23.2 6.38
17 | 2 | COOLING CAPACITIES — SI (cont) | 2 | 4 | 28.4 19.3 6.60
17 | 2 | COOLING CAPACITIES — SI (cont) | 2 | 5 | 30.8 15.0 6.70
17 | 2 | COOLING CAPACITIES — SI (cont) | 2 | 6 | 26.0 25.2 6.60
17 | 2 | COOLING CAPACITIES — SI (cont) | 2 | 7 | 26.2 24.6 6.68
17 | 2 | COOLING CAPACITIES — SI (cont) | 2 | 8 | 29.1 20.5 6.97
17 | 2 | COOLING CAPACITIES — SI (cont) | 2 | 9 | 31.5 15.5 7.06
17 | 2 | COOLING CAPACITIES — SI (cont) | 2 | 10 | 27.9 26.5 7.25
17 | 2 | COOLING CAPACITIES — SI (cont) | 2 | 11 | 27.9 26.5 7.25
17 | 2 | COOLING CAPACITIES — SI (cont) | 2 | 12 | 29.9 22.0 7.66
17 | 2 | COOLING CAPACITIES — SI (cont) | 3 | 1 | TC SHC kW
17 | 2 | COOLING CAPACITIES — SI (cont) | 3 | 2 | 24.0 23.4 6.61
17 | 2 | COOLING CAPACITIES — SI (cont) | 3 | 3 | 24.3 22.8 6.69
17 | 2 | COOLING CAPACITIES — SI (cont) | 3 | 4 | 27.5 19.0 6.96
17 | 2 | COOLING CAPACITIES — SI (cont) | 3 | 5 | 30.3 14.8 7.09
17 | 2 | COOLING CAPACITIES — SI (cont) | 3 | 6 | 25.5 24.6 6.97
17 | 2 | COOLING CAPACITIES — SI (cont) | 3 | 7 | 25.5 24.3 7.02
17 | 2 | COOLING CAPACITIES — SI (cont) | 3 | 8 | 28.4 20.4 7.35
17 | 2 | COOLING CAPACITIES — SI (cont) | 3 | 9 | 30.9 15.4 7.46
17 | 2 | COOLING CAPACITIES — SI (cont) | 3 | 10 | 27.1 25.7 7.61
17 | 2 | COOLING CAPACITIES — SI (cont) | 3 | 11 | 27.1 25.8 7.60
17 | 2 | COOLING CAPACITIES — SI (cont) | 3 | 12 | 29.3 22.0 8.04
17 | 2 | COOLING CAPACITIES — SI (cont) | 4 | 1 | TC SHC kW
17 | 2 | COOLING CAPACITIES — SI (cont) | 4 | 2 | 23.0 22.5 7.00
17 | 2 | COOLING CAPACITIES — SI (cont) | 4 | 3 | 23.2 22.0 7.06
17 | 2 | COOLING CAPACITIES — SI (cont) | 4 | 4 | 26.5 18.7 7.33
17 | 2 | COOLING CAPACITIES — SI (cont) | 4 | 5 | 29.6 14.6 7.48
17 | 2 | COOLING CAPACITIES — SI (cont) | 4 | 6 | 24.7 23.9 7.34
17 | 2 | COOLING CAPACITIES — SI (cont) | 4 | 7 | 24.7 23.9 7.34
17 | 2 | COOLING CAPACITIES — SI (cont) | 4 | 8 | 27.5 20.1 7.71
17 | 2 | COOLING CAPACITIES — SI (cont) | 4 | 9 | 30.3 15.2 7.86
17 | 2 | COOLING CAPACITIES — SI (cont) | 4 | 10 | 26.4 25.0 7.98
17 | 2 | COOLING CAPACITIES — SI (cont) | 4 | 11 | 26.4 25.0 7.97
17 | 2 | COOLING CAPACITIES — SI (cont) | 4 | 12 | 28.4 21.8 8.42
17 | 2 | COOLING CAPACITIES — SI (cont) | 5 | 1 | TC SHC kW
17 | 2 | COOLING CAPACITIES — SI (cont) | 5 | 2 | 22.3 21.7 7.32
17 | 2 | COOLING CAPACITIES — SI (cont) | 5 | 3 | 22.4 21.4 7.36
17 | 2 | COOLING CAPACITIES — SI (cont) | 5 | 4 | 25.5 18.4 7.71
17 | 2 | COOLING CAPACITIES — SI (cont) | 5 | 5 | 28.7 14.3 7.87
17 | 2 | COOLING CAPACITIES — SI (cont) | 5 | 6 | 23.7 22.8 7.72
17 | 2 | COOLING CAPACITIES — SI (cont) | 5 | 7 | 23.7 22.8 7.72
17 | 2 | COOLING CAPACITIES — SI (cont) | 5 | 8 | 26.3 19.7 8.09
17 | 2 | COOLING CAPACITIES — SI (cont) | 5 | 9 | 29.4 15.0 8.25
17 | 2 | COOLING CAPACITIES — SI (cont) | 5 | 10 | 25.6 24.2 8.37
17 | 2 | COOLING CAPACITIES — SI (cont) | 5 | 11 | 25.6 24.2 8.36
17 | 2 | COOLING CAPACITIES — SI (cont) | 5 | 12 | 27.3 21.5 8.77
17 | 2 | COOLING CAPACITIES — SI (cont) | 6 | 1 | TC SHC kW
17 | 2 | COOLING CAPACITIES — SI (cont) | 6 | 2 | 21.7 21.1 7.56
17 | 2 | COOLING CAPACITIES — SI (cont) | 6 | 3 | 21.7 20.9 7.59
17 | 2 | COOLING CAPACITIES — SI (cont) | 6 | 4 | 24.6 17.9 8.01
17 | 2 | COOLING CAPACITIES — SI (cont) | 6 | 5 | 28.0 14.1 8.17
17 | 2 | COOLING CAPACITIES — SI (cont) | 6 | 6 | 23.1 22.2 8.00
17 | 2 | COOLING CAPACITIES — SI (cont) | 6 | 7 | 23.0 22.2 7.99
17 | 2 | COOLING CAPACITIES — SI (cont) | 6 | 8 | 25.6 19.5 8.37
17 | 2 | COOLING CAPACITIES — SI (cont) | 6 | 9 | 28.7 14.8 8.57
17 | 2 | COOLING CAPACITIES — SI (cont) | 6 | 10 | 25.0 23.6 8.66
17 | 2 | COOLING CAPACITIES — SI (cont) | 6 | 11 | 25.0 23.6 8.65
17 | 2 | COOLING CAPACITIES — SI (cont) | 6 | 12 | 26.4 21.2 9.03
17 | 2 | COOLING CAPACITIES — SI (cont) | 7 | 1 | TC SHC kW
17 | 2 | COOLING CAPACITIES — SI (cont) | 7 | 2 | 20.7 20.1 7.96
17 | 2 | COOLING CAPACITIES — SI (cont) | 7 | 3 | 20.7 20.1 7.96
17 | 2 | COOLING CAPACITIES — SI (cont) | 7 | 4 | 23.1 17.4 8.44
17 | 2 | COOLING CAPACITIES — SI (cont) | 7 | 5 | 26.7 13.6 8.66
17 | 2 | COOLING CAPACITIES — SI (cont) | 7 | 6 | 22.0 21.2 8.42
17 | 2 | COOLING CAPACITIES — SI (cont) | 7 | 7 | 22.0 21.2 8.41
17 | 2 | COOLING CAPACITIES — SI (cont) | 7 | 8 | 23.9 18.8 8.82
17 | 2 | COOLING CAPACITIES — SI (cont) | 7 | 9 | 27.4 14.3 9.06
17 | 2 | COOLING CAPACITIES — SI (cont) | 7 | 10 | 23.6 22.2 9.15
17 | 2 | COOLING CAPACITIES — SI (cont) | 7 | 11 | 23.6 22.2 9.14
17 | 2 | COOLING CAPACITIES — SI (cont) | 7 | 12 | 25.0 20.7 9.47
17 | 2 | COOLING CAPACITIES — SI (cont) | 8 | 1 | TC SHC kW
17 | 2 | COOLING CAPACITIES — SI (cont) | 8 | 2 | 19.9 19.3 8.29
17 | 2 | COOLING CAPACITIES — SI (cont) | 8 | 3 | 19.9 19.3 8.29
17 | 2 | COOLING CAPACITIES — SI (cont) | 8 | 4 | 22.0 16.9 8.78
17 | 2 | COOLING CAPACITIES — SI (cont) | 8 | 5 | 25.5 13.2 9.04
17 | 2 | COOLING CAPACITIES — SI (cont) | 8 | 6 | 21.2 20.3 8.75
17 | 2 | COOLING CAPACITIES — SI (cont) | 8 | 7 | 21.2 20.3 8.75
17 | 2 | COOLING CAPACITIES — SI (cont) | 8 | 8 | 22.7 18.3 9.15
17 | 2 | COOLING CAPACITIES — SI (cont) | 8 | 9 | 26.3 14.0 9.44
17 | 2 | COOLING CAPACITIES — SI (cont) | 8 | 10 | 22.7 21.3 9.52
17 | 2 | COOLING CAPACITIES — SI (cont) | 8 | 11 | 22.7 21.3 9.51
17 | 2 | COOLING CAPACITIES — SI (cont) | 8 | 12 | 23.7 20.2 9.80
17 | 2 | COOLING CAPACITIES — SI (cont) | 9 | 1 | TC SHC kW
17 | 2 | COOLING CAPACITIES — SI (cont) | 9 | 2 | 19.1 18.5 8.62
17 | 2 | COOLING CAPACITIES — SI (cont) | 9 | 3 | 19.1 18.5 8.62
17 | 2 | COOLING CAPACITIES — SI (cont) | 9 | 4 | 20.8 16.4 9.05
17 | 2 | COOLING CAPACITIES — SI (cont) | 9 | 5 | 24.3 12.8 9.42
17 | 2 | COOLING CAPACITIES — SI (cont) | 9 | 6 | 20.3 19.4 9.08
17 | 2 | COOLING CAPACITIES — SI (cont) | 9 | 7 | 20.3 19.4 9.08
17 | 2 | COOLING CAPACITIES — SI (cont) | 9 | 8 | 21.5 17.8 9.48
17 | 2 | COOLING CAPACITIES — SI (cont) | 9 | 9 | 25.0 13.5 9.83
17 | 2 | COOLING CAPACITIES — SI (cont) | 9 | 10 | 21.8 20.4 9.88
17 | 2 | COOLING CAPACITIES — SI (cont) | 9 | 11 | 21.8 20.4 9.87
17 | 2 | COOLING CAPACITIES — SI (cont) | 9 | 12 | 22.3 19.5 10.10
18 | 1 | Performance data (cont) | 1 | 2 | 14
18 | 1 | Performance data (cont) | 1 | 3 | 16
18 | 1 | Performance data (cont) | 1 | 4 | 18
18 | 1 | Performance data (cont) | 1 | 5 | 20
18 | 1 | Performance data (cont) | 1 | 6 | 22
18 | 1 | Performance data (cont) | 1 | 7 | 14
18 | 1 | Performance data (cont) | 1 | 8 | 16
18 | 1 | Performance data (cont) | 1 | 9 | 18
18 | 1 | Performance data (cont) | 1 | 10 | 20
18 | 1 | Performance data (cont) | 2 | 1 | TC SHC kW
18 | 1 | Performance data (cont) | 2 | 2 | 26.6 26.4 6.82
18 | 1 | Performance data (cont) | 2 | 3 | 28.2 24.8 6.98
18 | 1 | Performance data (cont) | 2 | 4 | 30.5 22.8 7.17
18 | 1 | Performance data (cont) | 2 | 5 | 33.1 20.3 7.35
18 | 1 | Performance data (cont) | 2 | 6 | 34.7 17.3 7.42
18 | 1 | Performance data (cont) | 2 | 7 | 30.5 30.4 7.09
18 | 1 | Performance data (cont) | 2 | 8 | 31.4 29.3 7.17
18 | 1 | Performance data (cont) | 2 | 9 | 32.7 26.2 7.27
18 | 1 | Performance data (cont) | 2 | 10 | 34.3 22.2 7.39
18 | 1 | Performance data (cont) | 3 | 1 | TC SHC kW
18 | 1 | Performance data (cont) | 3 | 2 | 25.8 25.6 7.20
18 | 1 | Performance data (cont) | 3 | 3 | 27.0 24.2 7.34
18 | 1 | Performance data (cont) | 3 | 4 | 29.4 22.3 7.54
18 | 1 | Performance data (cont) | 3 | 5 | 32.1 19.9 7.73
18 | 1 | Performance data (cont) | 3 | 6 | 33.8 16.8 7.82
18 | 1 | Performance data (cont) | 3 | 7 | 29.6 29.5 7.47
18 | 1 | Performance data (cont) | 3 | 8 | 30.4 28.7 7.53
18 | 1 | Performance data (cont) | 3 | 9 | 31.8 25.9 7.65
18 | 1 | Performance data (cont) | 3 | 10 | 33.5 22.2 7.80
18 | 1 | Performance data (cont) | 4 | 1 | TC SHC kW
18 | 1 | Performance data (cont) | 4 | 2 | 24.7 24.6 7.61
18 | 1 | Performance data (cont) | 4 | 3 | 25.8 23.5 7.93
18 | 1 | Performance data (cont) | 4 | 4 | 28.2 21.7 8.11
18 | 1 | Performance data (cont) | 4 | 5 | 30.8 19.4 8.32
18 | 1 | Performance data (cont) | 4 | 6 | 32.8 16.4 8.45
18 | 1 | Performance data (cont) | 4 | 7 | 28.5 28.5 8.09
18 | 1 | Performance data (cont) | 4 | 8 | 29.1 27.9 8.12
18 | 1 | Performance data (cont) | 4 | 9 | 30.7 25.4 8.26
18 | 1 | Performance data (cont) | 4 | 10 | 32.6 21.9 8.46
18 | 1 | Performance data (cont) | 5 | 1 | TC SHC kW
18 | 1 | Performance data (cont) | 5 | 2 | 23.6 23.5 8.03
18 | 1 | Performance data (cont) | 5 | 3 | 24.5 22.7 8.13
18 | 1 | Performance data (cont) | 5 | 4 | 26.6 21.1 8.31
18 | 1 | Performance data (cont) | 5 | 5 | 29.4 18.8 8.53
18 | 1 | Performance data (cont) | 5 | 6 | 31.8 16.1 8.67
18 | 1 | Performance data (cont) | 5 | 7 | 27.3 27.3 8.30
18 | 1 | Performance data (cont) | 5 | 8 | 27.7 27.0 8.32
18 | 1 | Performance data (cont) | 5 | 9 | 29.4 24.8 8.47
18 | 1 | Performance data (cont) | 5 | 10 | 31.5 21.6 8.67
18 | 1 | Performance data (cont) | 6 | 1 | TC SHC kW
18 | 1 | Performance data (cont) | 6 | 2 | 22.4 22.3 8.47
18 | 1 | Performance data (cont) | 6 | 3 | 23.0 21.8 8.53
18 | 1 | Performance data (cont) | 6 | 4 | 25.0 20.3 8.73
18 | 1 | Performance data (cont) | 6 | 5 | 27.9 18.2 8.96
18 | 1 | Performance data (cont) | 6 | 6 | 30.7 17.8 9.15
18 | 1 | Performance data (cont) | 6 | 7 | 26.1 26.0 8.74
18 | 1 | Performance data (cont) | 6 | 8 | 26.3 26.0 8.74
18 | 1 | Performance data (cont) | 6 | 9 | 27.9 24.1 8.89
18 | 1 | Performance data (cont) | 6 | 10 | 30.1 21.2 9.11
18 | 1 | Performance data (cont) | 7 | 1 | TC SHC kW
18 | 1 | Performance data (cont) | 7 | 2 | 21.1 21.1 8.95
18 | 1 | Performance data (cont) | 7 | 3 | 21.5 20.9 8.97
18 | 1 | Performance data (cont) | 7 | 4 | 23.4 19.6 9.15
18 | 1 | Performance data (cont) | 7 | 5 | 26.2 17.5 9.40
18 | 1 | Performance data (cont) | 7 | 6 | 29.5 15.3 9.64
18 | 1 | Performance data (cont) | 7 | 7 | 24.7 24.7 9.20
18 | 1 | Performance data (cont) | 7 | 8 | 24.7 24.7 9.20
18 | 1 | Performance data (cont) | 7 | 9 | 26.4 23.3 9.34
18 | 1 | Performance data (cont) | 7 | 10 | 28.7 20.7 9.56
18 | 1 | Performance data (cont) | 8 | 1 | TC SHC kW
18 | 1 | Performance data (cont) | 8 | 2 | 20.0 20.0 9.40
18 | 1 | Performance data (cont) | 8 | 3 | 20.1 19.9 9.40
18 | 1 | Performance data (cont) | 8 | 4 | 21.7 18.7 9.60
18 | 1 | Performance data (cont) | 8 | 5 | 24.4 16.8 9.86
18 | 1 | Performance data (cont) | 8 | 6 | 27.9 14.8 10.11
18 | 1 | Performance data (cont) | 8 | 7 | 23.1 23.1 9.70
18 | 1 | Performance data (cont) | 8 | 8 | 23.1 23.1 9.71
18 | 1 | Performance data (cont) | 8 | 9 | 24.4 22.0 9.82
18 | 1 | Performance data (cont) | 8 | 10 | 26.6 20.0 10.03
18 | 1 | Performance data (cont) | 9 | 1 | TC SHC kW
18 | 1 | Performance data (cont) | 9 | 2 | 19.1 10.1 9.89
18 | 1 | Performance data (cont) | 9 | 3 | 19.1 19.1 9.89
18 | 1 | Performance data (cont) | 9 | 4 | 20.3 17.9 10.06
18 | 1 | Performance data (cont) | 9 | 5 | 22.6 16.2 10.32
18 | 1 | Performance data (cont) | 9 | 6 | 26.0 14.2 10.59
18 | 1 | Performance data (cont) | 9 | 7 | 21.5 21.5 10.22
18 | 1 | Performance data (cont) | 9 | 8 | 21.5 21.5 10.22
18 | 1 | Performance data (cont) | 9 | 9 | 22.4 20.7 10.31
18 | 1 | Performance data (cont) | 9 | 10 | 24.3 19.1 10.50
18 | 1 | Performance data (cont) | 10 | 1 | TC SHC kW
18 | 1 | Performance data (cont) | 10 | 2 | 18.3 18.3 10.37
18 | 1 | Performance data (cont) | 10 | 3 | 18.3 18.3 10.37
18 | 1 | Performance data (cont) | 10 | 4 | 19.1 17.2 10.52
18 | 1 | Performance data (cont) | 10 | 5 | 20.9 15.5 10.77
18 | 1 | Performance data (cont) | 10 | 6 | 24.0 13.5 11.07
18 | 1 | Performance data (cont) | 10 | 7 | 20.0 20.0 10.74
18 | 1 | Performance data (cont) | 10 | 8 | 20.0 20.0 10.74
18 | 1 | Performance data (cont) | 10 | 9 | 20.4 18.4 10.81
18 | 1 | Performance data (cont) | 10 | 10 | 21.9 18.1 10.98
18 | 2 | Performance data (cont) | 1 | 2 | 14
18 | 2 | Performance data (cont) | 1 | 3 | 16
18 | 2 | Performance data (cont) | 1 | 4 | 18
18 | 2 | Performance data (cont) | 1 | 5 | 20
18 | 2 | Performance data (cont) | 1 | 6 | 22
18 | 2 | Performance data (cont) | 1 | 7 | 14
18 | 2 | Performance data (cont) | 1 | 8 | 16
18 | 2 | Performance data (cont) | 1 | 9 | 18
18 | 2 | Performance data (cont) | 1 | 10 | 20
18 | 2 | Performance data (cont) | 2 | 1 | TC SHC kW
18 | 2 | Performance data (cont) | 2 | 2 | 31.5 31.4 7.12
18 | 2 | Performance data (cont) | 2 | 3 | 31.9 30.6 7.16
18 | 2 | Performance data (cont) | 2 | 4 | 33.3 27.8 7.30
18 | 2 | Performance data (cont) | 2 | 5 | 35.3 24.0 7.50
18 | 2 | Performance data (cont) | 2 | 6 | 37.2 19.9 7.70
18 | 2 | Performance data (cont) | 2 | 7 | 31.7 31.7 7.15
18 | 2 | Performance data (cont) | 2 | 8 | 23.1 31.1 7.18
18 | 2 | Performance data (cont) | 2 | 9 | 33.5 28.3 7.32
18 | 2 | Performance data (cont) | 2 | 10 | 35.3 24.4 7.51
18 | 2 | Performance data (cont) | 3 | 1 | TC SHC kW
18 | 2 | Performance data (cont) | 3 | 2 | 30.8 30.8 7.53
18 | 2 | Performance data (cont) | 3 | 3 | 31.0 30.1 7.54
18 | 2 | Performance data (cont) | 3 | 4 | 32.4 27.4 7.68
18 | 2 | Performance data (cont) | 3 | 5 | 34.2 23.6 7.88
18 | 2 | Performance data (cont) | 3 | 6 | 36.2 19.6 8.10
18 | 2 | Performance data (cont) | 3 | 7 | 31.0 31.0 7.54
18 | 2 | Performance data (cont) | 3 | 8 | 31.2 30.5 7.57
18 | 2 | Performance data (cont) | 3 | 9 | 32.5 27.9 7.71
18 | 2 | Performance data (cont) | 3 | 10 | 34.4 24.0 7.90
18 | 2 | Performance data (cont) | 4 | 1 | TC SHC kW
18 | 2 | Performance data (cont) | 4 | 2 | 30.0 30.0 7.95
18 | 2 | Performance data (cont) | 4 | 3 | 30.1 29.6 7.97
18 | 2 | Performance data (cont) | 4 | 4 | 31.4 27.2 8.11
18 | 2 | Performance data (cont) | 4 | 5 | 33.2 23.4 8.30
18 | 2 | Performance data (cont) | 4 | 6 | 35.2 19.3 8.51
18 | 2 | Performance data (cont) | 4 | 7 | 30.3 30.2 7.99
18 | 2 | Performance data (cont) | 4 | 8 | 30.4 30.1 7.99
18 | 2 | Performance data (cont) | 4 | 9 | 31.6 27.6 8.13
18 | 2 | Performance data (cont) | 4 | 10 | 33.3 23.7 8.31
18 | 2 | Performance data (cont) | 5 | 1 | TC SHC kW
18 | 2 | Performance data (cont) | 5 | 2 | 29.1 29.1 8.40
18 | 2 | Performance data (cont) | 5 | 3 | 29.1 29.0 8.41
18 | 2 | Performance data (cont) | 5 | 4 | 30.3 26.7 8.54
18 | 2 | Performance data (cont) | 5 | 5 | 32.1 23.1 8.73
18 | 2 | Performance data (cont) | 5 | 6 | 34.0 18.9 8.95
18 | 2 | Performance data (cont) | 5 | 7 | 29.4 29.4 8.44
18 | 2 | Performance data (cont) | 5 | 8 | 29.4 29.4 8.44
18 | 2 | Performance data (cont) | 5 | 9 | 30.5 27.1 8.56
18 | 2 | Performance data (cont) | 5 | 10 | 32.2 23.5 8.75
18 | 2 | Performance data (cont) | 6 | 1 | TC SHC kW
18 | 2 | Performance data (cont) | 6 | 2 | 28.1 27.9 8.87
18 | 2 | Performance data (cont) | 6 | 3 | 28.0 28.0 8.87
18 | 2 | Performance data (cont) | 6 | 4 | 29.1 26.1 8.89
18 | 2 | Performance data (cont) | 6 | 5 | 30.8 22.8 9.17
18 | 2 | Performance data (cont) | 6 | 6 | 32.8 18.5 9.40
18 | 2 | Performance data (cont) | 6 | 7 | 28.3 28.3 8.91
18 | 2 | Performance data (cont) | 6 | 8 | 28.3 28.3 8.91
18 | 2 | Performance data (cont) | 6 | 9 | 29.3 26.5 9.01
18 | 2 | Performance data (cont) | 6 | 10 | 31.0 23.3 9.19
18 | 2 | Performance data (cont) | 7 | 1 | TC SHC kW
18 | 2 | Performance data (cont) | 7 | 2 | 26.5 14.7 9.37
18 | 2 | Performance data (cont) | 7 | 3 | 26.5 26.5 9.36
18 | 2 | Performance data (cont) | 7 | 4 | 27.7 25.1 9.46
18 | 2 | Performance data (cont) | 7 | 5 | 29.5 22.5 9.64
18 | 2 | Performance data (cont) | 7 | 6 | 31.5 18.3 9.88
18 | 2 | Performance data (cont) | 7 | 7 | 27.0 26.9 9.41
18 | 2 | Performance data (cont) | 7 | 8 | 27.0 27.0 9.40
18 | 2 | Performance data (cont) | 7 | 9 | 28.0 25.6 9.50
18 | 2 | Performance data (cont) | 7 | 10 | 29.7 23.0 9.66
18 | 2 | Performance data (cont) | 8 | 1 | TC SHC kW
18 | 2 | Performance data (cont) | 8 | 2 | 24.8 24.8 9.87
18 | 2 | Performance data (cont) | 8 | 3 | 24.8 24.8 9.87
18 | 2 | Performance data (cont) | 8 | 4 | 25.7 23.8 9.96
18 | 2 | Performance data (cont) | 8 | 5 | 27.5 21.8 10.12
18 | 2 | Performance data (cont) | 8 | 6 | 30.0 18.0 10.36
18 | 2 | Performance data (cont) | 8 | 7 | 25.2 25.2 9.92
18 | 2 | Performance data (cont) | 8 | 8 | 25.2 25.2 9.92
18 | 2 | Performance data (cont) | 8 | 9 | 26.1 24.4 9.99
18 | 2 | Performance data (cont) | 8 | 10 | 27.7 22.3 10.13
18 | 2 | Performance data (cont) | 9 | 1 | TC SHC kW
18 | 2 | Performance data (cont) | 9 | 2 | 23.0 23.0 10.39
18 | 2 | Performance data (cont) | 9 | 3 | 23.0 23.0 10.39
18 | 2 | Performance data (cont) | 9 | 4 | 23.7 22.4 10.45
18 | 2 | Performance data (cont) | 9 | 5 | 25.3 20.9 10.59
18 | 2 | Performance data (cont) | 9 | 6 | 28.3 17.5 10.86
18 | 2 | Performance data (cont) | 9 | 7 | 23.4 23.4 10.43
18 | 2 | Performance data (cont) | 9 | 8 | 23.4 23.4 10.43
18 | 2 | Performance data (cont) | 9 | 9 | 24.0 23.0 10.49
18 | 2 | Performance data (cont) | 9 | 10 | 25.5 21.4 10.61
18 | 2 | Performance data (cont) | 10 | 1 | TC SHC kW
18 | 2 | Performance data (cont) | 10 | 2 | 21.3 21.3 10.93
18 | 2 | Performance data (cont) | 10 | 3 | 21.3 21.3 10.93
18 | 2 | Performance data (cont) | 10 | 4 | 21.6 21.0 10.95
18 | 2 | Performance data (cont) | 10 | 5 | 22.8 19.9 11.07
18 | 2 | Performance data (cont) | 10 | 6 | 26.5 17.0 11.38
18 | 2 | Performance data (cont) | 10 | 7 | 21.6 21.6 10.97
18 | 2 | Performance data (cont) | 10 | 8 | 21.6 21.6 10.97
18 | 2 | Performance data (cont) | 10 | 9 | 21.8 21.4 10.99
18 | 2 | Performance data (cont) | 10 | 10 | 23.0 20.4 11.10
19 | 1 | COOLING CAPACITIES — SI (cont) | 1 | 1 | 1500/0.13
19 | 1 | COOLING CAPACITIES — SI (cont) | 1 | 2 | 2000/0.17
19 | 2 | COOLING CAPACITIES — SI (cont) | 1 | 2 | 13
19 | 2 | COOLING CAPACITIES — SI (cont) | 1 | 3 | 16
19 | 2 | COOLING CAPACITIES — SI (cont) | 1 | 4 | 19
19 | 2 | COOLING CAPACITIES — SI (cont) | 1 | 5 | 22
19 | 2 | COOLING CAPACITIES — SI (cont) | 1 | 6 | 13
19 | 2 | COOLING CAPACITIES — SI (cont) | 1 | 7 | 16
19 | 2 | COOLING CAPACITIES — SI (cont) | 1 | 8 | 19
19 | 2 | COOLING CAPACITIES — SI (cont) | 1 | 9 | 22
19 | 2 | COOLING CAPACITIES — SI (cont) | 1 | 10 | 13
19 | 2 | COOLING CAPACITIES — SI (cont) | 1 | 11 | 16
19 | 2 | COOLING CAPACITIES — SI (cont) | 1 | 12 | 19
19 | 2 | COOLING CAPACITIES — SI (cont) | 2 | 1 | TC SHC kW
19 | 2 | COOLING CAPACITIES — SI (cont) | 2 | 2 | 34.7 34.7 8.92
19 | 2 | COOLING CAPACITIES — SI (cont) | 2 | 3 | 38.0 33.8 8.99
19 | 2 | COOLING CAPACITIES — SI (cont) | 2 | 4 | 41.4 28.1 9.08
19 | 2 | COOLING CAPACITIES — SI (cont) | 2 | 5 | 44.4 22.0 9.13
19 | 2 | COOLING CAPACITIES — SI (cont) | 2 | 6 | 37.0 37.0 9.00
19 | 2 | COOLING CAPACITIES — SI (cont) | 2 | 7 | 40.0 39.9 9.06
19 | 2 | COOLING CAPACITIES — SI (cont) | 2 | 8 | 43.2 31.7 9.13
19 | 2 | COOLING CAPACITIES — SI (cont) | 2 | 9 | 46.3 24.0 9.22
19 | 2 | COOLING CAPACITIES — SI (cont) | 2 | 10 | 36.6 36.6 9.05
19 | 2 | COOLING CAPACITIES — SI (cont) | 2 | 11 | 40.1 40.1 9.10
19 | 2 | COOLING CAPACITIES — SI (cont) | 2 | 12 | 43.6 33.5 9.15
19 | 2 | COOLING CAPACITIES — SI (cont) | 3 | 1 | TC SHC kW
19 | 2 | COOLING CAPACITIES — SI (cont) | 3 | 2 | 32.1 32.1 9.34
19 | 2 | COOLING CAPACITIES — SI (cont) | 3 | 3 | 35.8 32.8 9.46
19 | 2 | COOLING CAPACITIES — SI (cont) | 3 | 4 | 39.6 27.4 9.60
19 | 2 | COOLING CAPACITIES — SI (cont) | 3 | 5 | 43.0 21.6 9.70
19 | 2 | COOLING CAPACITIES — SI (cont) | 3 | 6 | 34.8 34.8 9.47
19 | 2 | COOLING CAPACITIES — SI (cont) | 3 | 7 | 38.2 38.2 9.57
19 | 2 | COOLING CAPACITIES — SI (cont) | 3 | 8 | 41.6 31.1 9.68
19 | 2 | COOLING CAPACITIES — SI (cont) | 3 | 9 | 44.9 23.7 9.80
19 | 2 | COOLING CAPACITIES — SI (cont) | 3 | 10 | 35.5 35.5 9.60
19 | 2 | COOLING CAPACITIES — SI (cont) | 3 | 11 | 38.7 38.7 9.63
19 | 2 | COOLING CAPACITIES — SI (cont) | 3 | 12 | 42.1 32.4 9.74
19 | 2 | COOLING CAPACITIES — SI (cont) | 4 | 1 | TC SHC kW
19 | 2 | COOLING CAPACITIES — SI (cont) | 4 | 2 | 29.4 29.4 9.78
19 | 2 | COOLING CAPACITIES — SI (cont) | 4 | 3 | 33.6 31.9 9.94
19 | 2 | COOLING CAPACITIES — SI (cont) | 4 | 4 | 37.9 26.7 10.12
19 | 2 | COOLING CAPACITIES — SI (cont) | 4 | 5 | 41.6 21.1 10.27
19 | 2 | COOLING CAPACITIES — SI (cont) | 4 | 6 | 32.9 32.9 9.95
19 | 2 | COOLING CAPACITIES — SI (cont) | 4 | 7 | 36.3 36.3 10.08
19 | 2 | COOLING CAPACITIES — SI (cont) | 4 | 8 | 40.0 30.5 10.22
19 | 2 | COOLING CAPACITIES — SI (cont) | 4 | 9 | 43.4 23.3 10.39
19 | 2 | COOLING CAPACITIES — SI (cont) | 4 | 10 | 34.4 34.4 10.15
19 | 2 | COOLING CAPACITIES — SI (cont) | 4 | 11 | 37.4 37.4 10.10
19 | 2 | COOLING CAPACITIES — SI (cont) | 4 | 12 | 40.6 32.5 10.25
19 | 2 | COOLING CAPACITIES — SI (cont) | 5 | 1 | TC SHC kW
19 | 2 | COOLING CAPACITIES — SI (cont) | 5 | 2 | 26.7 26.7 10.20
19 | 2 | COOLING CAPACITIES — SI (cont) | 5 | 3 | 31.5 30.9 10.42
19 | 2 | COOLING CAPACITIES — SI (cont) | 5 | 4 | 36.2 26.0 10.64
19 | 2 | COOLING CAPACITIES — SI (cont) | 5 | 5 | 40.2 20.7 10.85
19 | 2 | COOLING CAPACITIES — SI (cont) | 5 | 6 | 30.8 30.8 10.40
19 | 2 | COOLING CAPACITIES — SI (cont) | 5 | 7 | 34.5 34.5 10.59
19 | 2 | COOLING CAPACITIES — SI (cont) | 5 | 8 | 38.3 29.9 10.76
19 | 2 | COOLING CAPACITIES — SI (cont) | 5 | 9 | 42.0 22.9 10.96
19 | 2 | COOLING CAPACITIES — SI (cont) | 5 | 10 | 33.0 33.0 10.49
19 | 2 | COOLING CAPACITIES — SI (cont) | 5 | 11 | 36.0 36.0 10.65
19 | 2 | COOLING CAPACITIES — SI (cont) | 5 | 12 | 39.1 31.9 10.82
19 | 2 | COOLING CAPACITIES — SI (cont) | 6 | 1 | TC SHC kW
19 | 2 | COOLING CAPACITIES — SI (cont) | 6 | 2 | 24.7 24.7 10.52
19 | 2 | COOLING CAPACITIES — SI (cont) | 6 | 3 | 29.9 29.7 10.80
19 | 2 | COOLING CAPACITIES — SI (cont) | 6 | 4 | 34.9 25.5 11.03
19 | 2 | COOLING CAPACITIES — SI (cont) | 6 | 5 | 39.1 20.3 11.30
19 | 2 | COOLING CAPACITIES — SI (cont) | 6 | 6 | 29.2 29.2 10.77
19 | 2 | COOLING CAPACITIES — SI (cont) | 6 | 7 | 33.1 33.1 11.00
19 | 2 | COOLING CAPACITIES — SI (cont) | 6 | 8 | 37.0 29.4 11.18
19 | 2 | COOLING CAPACITIES — SI (cont) | 6 | 9 | 40.9 22.7 11.40
19 | 2 | COOLING CAPACITIES — SI (cont) | 6 | 10 | 31.4 31.4 10.40
19 | 2 | COOLING CAPACITIES — SI (cont) | 6 | 11 | 35.0 35.0 11.07
19 | 2 | COOLING CAPACITIES — SI (cont) | 6 | 12 | 38.0 31.5 11.25
19 | 2 | COOLING CAPACITIES — SI (cont) | 7 | 1 | TC SHC kW
19 | 2 | COOLING CAPACITIES — SI (cont) | 7 | 2 | 21.1 21.1 11.10
19 | 2 | COOLING CAPACITIES — SI (cont) | 7 | 3 | 26.8 26.8 11.40
19 | 2 | COOLING CAPACITIES — SI (cont) | 7 | 4 | 32.3 24.4 11.71
19 | 2 | COOLING CAPACITIES — SI (cont) | 7 | 5 | 37.1 19.7 12.00
19 | 2 | COOLING CAPACITIES — SI (cont) | 7 | 6 | 26.9 26.9 11.42
19 | 2 | COOLING CAPACITIES — SI (cont) | 7 | 7 | 30.8 30.8 11.64
19 | 2 | COOLING CAPACITIES — SI (cont) | 7 | 8 | 34.7 28.3 11.88
19 | 2 | COOLING CAPACITIES — SI (cont) | 7 | 9 | 38.8 22.1 12.13
19 | 2 | COOLING CAPACITIES — SI (cont) | 7 | 10 | 30.5 30.5 11.64
19 | 2 | COOLING CAPACITIES — SI (cont) | 7 | 11 | 53.1 33.1 11.79
19 | 2 | COOLING CAPACITIES — SI (cont) | 7 | 12 | 35.8 30.6 11.96
19 | 2 | COOLING CAPACITIES — SI (cont) | 8 | 1 | TC SHC kW
19 | 2 | COOLING CAPACITIES — SI (cont) | 8 | 2 | 20.5 20.5 11.62
19 | 2 | COOLING CAPACITIES — SI (cont) | 8 | 3 | 25.3 25.3 11.93
19 | 2 | COOLING CAPACITIES — SI (cont) | 8 | 4 | 30.2 23.5 12.25
19 | 2 | COOLING CAPACITIES — SI (cont) | 8 | 5 | 35.2 19.1 12.58
19 | 2 | COOLING CAPACITIES — SI (cont) | 8 | 6 | 25.7 25.7 12.05
19 | 2 | COOLING CAPACITIES — SI (cont) | 8 | 7 | 28.8 28.8 12.24
19 | 2 | COOLING CAPACITIES — SI (cont) | 8 | 8 | 32.2 27.1 12.44
19 | 2 | COOLING CAPACITIES — SI (cont) | 8 | 9 | 36.9 21.5 12.73
19 | 2 | COOLING CAPACITIES — SI (cont) | 8 | 10 | 29.1 29.1 12.26
19 | 2 | COOLING CAPACITIES — SI (cont) | 8 | 11 | 31.0 31.0 12.38
19 | 2 | COOLING CAPACITIES — SI (cont) | 8 | 12 | 33.4 29.4 12.52
19 | 2 | COOLING CAPACITIES — SI (cont) | 9 | 1 | TC SHC kW
19 | 2 | COOLING CAPACITIES — SI (cont) | 9 | 2 | 20.4 20.4 12.15
19 | 2 | COOLING CAPACITIES — SI (cont) | 9 | 3 | 24.1 24.1 12.45
19 | 2 | COOLING CAPACITIES — SI (cont) | 9 | 4 | 27.9 27.9 12.78
19 | 2 | COOLING CAPACITIES — SI (cont) | 9 | 5 | 33.2 33.2 13.17
19 | 2 | COOLING CAPACITIES — SI (cont) | 9 | 6 | 24.5 24.5 12.68
19 | 2 | COOLING CAPACITIES — SI (cont) | 9 | 7 | 26.9 26.9 12.84
19 | 2 | COOLING CAPACITIES — SI (cont) | 9 | 8 | 29.6 25.8 13.00
19 | 2 | COOLING CAPACITIES — SI (cont) | 9 | 9 | 34.9 21.0 13.33
19 | 2 | COOLING CAPACITIES — SI (cont) | 9 | 10 | 27.7 27.7 12.88
19 | 2 | COOLING CAPACITIES — SI (cont) | 9 | 11 | 29.0 29.0 12.97
19 | 2 | COOLING CAPACITIES — SI (cont) | 9 | 12 | 30.8 28.1 13.10
19 | 2 | COOLING CAPACITIES — SI (cont) | 10 | 1 | TC SHC kW
19 | 2 | COOLING CAPACITIES — SI (cont) | 10 | 2 | 20.1 20.1 12.67
19 | 2 | COOLING CAPACITIES — SI (cont) | 10 | 3 | 22.8 22.8 12.98
19 | 2 | COOLING CAPACITIES — SI (cont) | 10 | 4 | 25.8 21.4 13.31
19 | 2 | COOLING CAPACITIES — SI (cont) | 10 | 5 | 31.3 17.8 13.75
19 | 2 | COOLING CAPACITIES — SI (cont) | 10 | 6 | 23.3 23.3 13.34
19 | 2 | COOLING CAPACITIES — SI (cont) | 10 | 7 | 24.9 24.9 13.43
19 | 2 | COOLING CAPACITIES — SI (cont) | 10 | 8 | 27.0 24.5 13.56
19 | 2 | COOLING CAPACITIES — SI (cont) | 10 | 9 | 33.1 20.3 13.93
19 | 2 | COOLING CAPACITIES — SI (cont) | 10 | 10 | 26.2 26.0 13.49
19 | 2 | COOLING CAPACITIES — SI (cont) | 10 | 11 | 26.9 26.8 13.57
19 | 2 | COOLING CAPACITIES — SI (cont) | 10 | 12 | 28.2 26.7 13.67
20 | 1 | Performance data (cont) | 1 | 1 | 1500/0.05
20 | 1 | Performance data (cont) | 1 | 2 | 2000/0.07
20 | 2 | Performance data (cont) | 1 | 2 | 62
20 | 2 | Performance data (cont) | 1 | 3 | 67
20 | 2 | Performance data (cont) | 1 | 4 | 72
20 | 2 | Performance data (cont) | 1 | 5 | 62
20 | 2 | Performance data (cont) | 1 | 6 | 67
20 | 2 | Performance data (cont) | 1 | 7 | 72
20 | 2 | Performance data (cont) | 1 | 8 | 62
20 | 2 | Performance data (cont) | 1 | 9 | 67
20 | 2 | Performance data (cont) | 2 | 1 | TC SHC kW
20 | 2 | Performance data (cont) | 2 | 2 | 60.0 50.5 4.44
20 | 2 | Performance data (cont) | 2 | 3 | 66.0 42.6 4.57
20 | 2 | Performance data (cont) | 2 | 4 | 72.1 34.5 4.71
20 | 2 | Performance data (cont) | 2 | 5 | 63.0 58.2 4.52
20 | 2 | Performance data (cont) | 2 | 6 | 69.2 48.5 4.66
20 | 2 | Performance data (cont) | 2 | 7 | 76.1 38.3 4.84
20 | 2 | Performance data (cont) | 2 | 8 | 65.2 64.3 4.58
20 | 2 | Performance data (cont) | 2 | 9 | 71.5 54.0 4.74
20 | 2 | Performance data (cont) | 3 | 1 | TC SHC kW
20 | 2 | Performance data (cont) | 3 | 2 | 57.2 49.4 4.85
20 | 2 | Performance data (cont) | 3 | 3 | 63.2 41.6 5.00
20 | 2 | Performance data (cont) | 3 | 4 | 69.4 33.5 5.17
20 | 2 | Performance data (cont) | 3 | 5 | 60.3 57.3 4.96
20 | 2 | Performance data (cont) | 3 | 6 | 66.3 47.5 5.11
20 | 2 | Performance data (cont) | 3 | 7 | 72.4 37.1 5.28
20 | 2 | Performance data (cont) | 3 | 8 | 62.6 62.6 5.03
20 | 2 | Performance data (cont) | 3 | 9 | 68.0 52.8 5.18
20 | 2 | Performance data (cont) | 4 | 1 | TC SHC kW
20 | 2 | Performance data (cont) | 4 | 2 | 54.4 48.1 5.25
20 | 2 | Performance data (cont) | 4 | 3 | 60.2 40.4 5.43
20 | 2 | Performance data (cont) | 4 | 4 | 66.3 32.4 5.62
20 | 2 | Performance data (cont) | 4 | 5 | 57.1 55.6 5.35
20 | 2 | Performance data (cont) | 4 | 6 | 62.9 46.4 5.54
20 | 2 | Performance data (cont) | 4 | 7 | 69.4 36.2 5.75
20 | 2 | Performance data (cont) | 4 | 8 | 60.0 60.0 5.47
20 | 2 | Performance data (cont) | 4 | 9 | 64.7 52.0 5.62
20 | 2 | Performance data (cont) | 5 | 1 | TC SHC kW
20 | 2 | Performance data (cont) | 5 | 2 | 51.0 46.5 5.64
20 | 2 | Performance data (cont) | 5 | 3 | 56.9 39.1 5.83
20 | 2 | Performance data (cont) | 5 | 4 | 62.9 31.2 6.05
20 | 2 | Performance data (cont) | 5 | 5 | 54.2 53.5 5.76
20 | 2 | Performance data (cont) | 5 | 6 | 59.5 45.2 5.97
20 | 2 | Performance data (cont) | 5 | 7 | 65.7 35.0 6.19
20 | 2 | Performance data (cont) | 5 | 8 | 57.2 57.2 5.90
20 | 2 | Performance data (cont) | 5 | 9 | 61.1 50.7 6.05
20 | 2 | Performance data (cont) | 6 | 1 | TC SHC kW
20 | 2 | Performance data (cont) | 6 | 2 | 47.6 45.0 6.02
20 | 2 | Performance data (cont) | 6 | 3 | 53.7 37.8 6.24
20 | 2 | Performance data (cont) | 6 | 4 | 59.5 30.0 6.48
20 | 2 | Performance data (cont) | 6 | 5 | 51.4 51.3 6.17
20 | 2 | Performance data (cont) | 6 | 6 | 56.0 44.0 6.39
20 | 2 | Performance data (cont) | 6 | 7 | 62.0 33.8 6.63
20 | 2 | Performance data (cont) | 6 | 8 | 54.4 54.4 6.33
20 | 2 | Performance data (cont) | 6 | 9 | 57.4 49.4 6.48
20 | 2 | Performance data (cont) | 7 | 1 | TC SHC kW
20 | 2 | Performance data (cont) | 7 | 2 | 44.7 43.5 6.39
20 | 2 | Performance data (cont) | 7 | 3 | 50.3 36.6 6.65
20 | 2 | Performance data (cont) | 7 | 4 | 55.8 28.8 6.90
20 | 2 | Performance data (cont) | 7 | 5 | 48.7 48.7 6.61
20 | 2 | Performance data (cont) | 7 | 6 | 52.3 42.5 6.77
20 | 2 | Performance data (cont) | 7 | 7 | 58.0 32.4 7.03
20 | 2 | Performance data (cont) | 7 | 8 | 51.6 51.6 6.79
20 | 2 | Performance data (cont) | 7 | 9 | 53.5 47.7 6.87
20 | 3 | Performance data (cont) | 1 | 1 | 1950/0.06
20 | 3 | Performance data (cont) | 1 | 2 | 2400/0.075
20 | 3 | Performance data (cont) | 1 | 3 | 2500/0.075
20 | 4 | Performance data (cont) | 1 | 2 | 62
20 | 4 | Performance data (cont) | 1 | 3 | 67
20 | 4 | Performance data (cont) | 1 | 4 | 72
20 | 4 | Performance data (cont) | 1 | 5 | 62
20 | 4 | Performance data (cont) | 1 | 6 | 67
20 | 4 | Performance data (cont) | 1 | 7 | 72
20 | 4 | Performance data (cont) | 1 | 8 | 62
20 | 4 | Performance data (cont) | 1 | 9 | 67
20 | 4 | Performance data (cont) | 1 | 10 | 72
20 | 4 | Performance data (cont) | 1 | 11 | 62
20 | 4 | Performance data (cont) | 1 | 12 | 67
20 | 4 | Performance data (cont) | 2 | 1 | TC SHC kW
20 | 4 | Performance data (cont) | 2 | 2 | 71.9 56.3 5.47
20 | 4 | Performance data (cont) | 2 | 3 | 80.1 46.6 5.73
20 | 4 | Performance data (cont) | 2 | 4 | 88.3 55.1 6.02
20 | 4 | Performance data (cont) | 2 | 5 | 74.9 62.3 5.60
20 | 4 | Performance data (cont) | 2 | 6 | 83.0 50.5 5.86
20 | 4 | Performance data (cont) | 2 | 7 | 90.9 57.0 6.14
20 | 4 | Performance data (cont) | 2 | 8 | 75.3 63.6 5.64
20 | 4 | Performance data (cont) | 2 | 9 | 83.6 51.2 5.90
20 | 4 | Performance data (cont) | 2 | 10 | 91.3 60.4 6.14
20 | 4 | Performance data (cont) | 2 | 11 | 77.4 69.1 5.74
20 | 4 | Performance data (cont) | 2 | 12 | 85.2 55.3 6.00
20 | 4 | Performance data (cont) | 3 | 1 | TC SHC kW
20 | 4 | Performance data (cont) | 3 | 2 | 69.0 59.7 5.77
20 | 4 | Performance data (cont) | 3 | 3 | 77.1 50.5 6.04
20 | 4 | Performance data (cont) | 3 | 4 | 85.4 40.6 6.34
20 | 4 | Performance data (cont) | 3 | 5 | 71.7 66.6 5.90
20 | 4 | Performance data (cont) | 3 | 6 | 79.8 55.6 6.17
20 | 4 | Performance data (cont) | 3 | 7 | 88.2 43.6 6.47
20 | 4 | Performance data (cont) | 3 | 8 | 72.2 68.0 5.93
20 | 4 | Performance data (cont) | 3 | 9 | 80.2 56.6 6.19
20 | 4 | Performance data (cont) | 3 | 10 | 88.5 44.1 6.49
20 | 4 | Performance data (cont) | 3 | 11 | 74.3 73.8 6.05
20 | 4 | Performance data (cont) | 3 | 12 | 82.0 62.0 6.31
20 | 4 | Performance data (cont) | 4 | 1 | TC SHC kW
20 | 4 | Performance data (cont) | 4 | 2 | 64.9 57.9 6.32
20 | 4 | Performance data (cont) | 4 | 3 | 72.7 48.8 6.61
20 | 4 | Performance data (cont) | 4 | 4 | 80.8 39.1 6.54
20 | 4 | Performance data (cont) | 4 | 5 | 67.4 64.6 6.45
20 | 4 | Performance data (cont) | 4 | 6 | 75.2 54.0 6.75
20 | 4 | Performance data (cont) | 4 | 7 | 83.5 42.1 6.60
20 | 4 | Performance data (cont) | 4 | 8 | 67.8 65.8 6.48
20 | 4 | Performance data (cont) | 4 | 9 | 75.6 55.1 6.76
20 | 4 | Performance data (cont) | 4 | 10 | 83.8 42.7 6.69
20 | 4 | Performance data (cont) | 4 | 11 | 70.7 70.5 6.60
20 | 4 | Performance data (cont) | 4 | 12 | 77.1 60.2 6.86
20 | 4 | Performance data (cont) | 5 | 1 | TC SHC kW
20 | 4 | Performance data (cont) | 5 | 2 | 60.4 55.7 6.59
20 | 4 | Performance data (cont) | 5 | 3 | 68.1 47.2 6.86
20 | 4 | Performance data (cont) | 5 | 4 | 76.2 37.5 7.19
20 | 4 | Performance data (cont) | 5 | 5 | 63.0 62.2 6.71
20 | 4 | Performance data (cont) | 5 | 6 | 70.4 52.4 7.00
20 | 4 | Performance data (cont) | 5 | 7 | 78.6 40.8 7.32
20 | 4 | Performance data (cont) | 5 | 8 | 63.5 63.2 6.74
20 | 4 | Performance data (cont) | 5 | 9 | 70.8 53.4 7.02
20 | 4 | Performance data (cont) | 5 | 10 | 78.8 41.3 7.34
20 | 4 | Performance data (cont) | 5 | 11 | 66.7 66.7 6.90
20 | 4 | Performance data (cont) | 5 | 12 | 72.0 58.6 7.11
20 | 4 | Performance data (cont) | 6 | 1 | TC SHC kW
20 | 4 | Performance data (cont) | 6 | 2 | 55.9 53.2 6.99
20 | 4 | Performance data (cont) | 6 | 3 | 63.4 45.4 7.26
20 | 4 | Performance data (cont) | 6 | 4 | 71.1 35.9 7.58
20 | 4 | Performance data (cont) | 6 | 5 | 59.0 59.0 7.13
20 | 4 | Performance data (cont) | 6 | 6 | 65.4 50.6 7.39
20 | 4 | Performance data (cont) | 6 | 7 | 73.2 39.0 7.71
20 | 4 | Performance data (cont) | 6 | 8 | 59.7 59.7 7.17
20 | 4 | Performance data (cont) | 6 | 9 | 65.6 51.6 7.41
20 | 4 | Performance data (cont) | 6 | 10 | 73.5 39.6 7.72
20 | 4 | Performance data (cont) | 6 | 11 | 62.5 62.7 7.34
20 | 4 | Performance data (cont) | 6 | 12 | 66.8 56.8 7.49
20 | 4 | Performance data (cont) | 7 | 1 | TC SHC kW
20 | 4 | Performance data (cont) | 7 | 2 | 51.1 50.4 7.37
20 | 4 | Performance data (cont) | 7 | 3 | 58.4 43.5 7.63
20 | 4 | Performance data (cont) | 7 | 4 | 65.8 34.1 7.95
20 | 4 | Performance data (cont) | 7 | 5 | 55.1 55.0 7.54
20 | 4 | Performance data (cont) | 7 | 6 | 60.0 48.6 7.75
20 | 4 | Performance data (cont) | 7 | 7 | 67.7 37.3 8.08
20 | 4 | Performance data (cont) | 7 | 8 | 55.8 55.8 7.58
20 | 4 | Performance data (cont) | 7 | 9 | 60.3 49.8 6.77
20 | 4 | Performance data (cont) | 7 | 10 | 57.9 37.9 8.10
20 | 4 | Performance data (cont) | 7 | 11 | 58.7 58.6 7.75
20 | 4 | Performance data (cont) | 7 | 12 | 61.3 54.8 7.87
20 | 5 | Performance data (cont) | 1 | 1 | 2000/0.07
20 | 5 | Performance data (cont) | 1 | 2 | 2500/.08
20 | 5 | Performance data (cont) | 1 | 3 | 3000/0.10
20 | 6 | Performance data (cont) | 1 | 2 | 62
20 | 6 | Performance data (cont) | 1 | 3 | 67
20 | 6 | Performance data (cont) | 1 | 4 | 72
20 | 6 | Performance data (cont) | 1 | 5 | 62
20 | 6 | Performance data (cont) | 1 | 6 | 67
20 | 6 | Performance data (cont) | 1 | 7 | 72
20 | 6 | Performance data (cont) | 1 | 8 | 62
20 | 6 | Performance data (cont) | 1 | 9 | 67
20 | 6 | Performance data (cont) | 1 | 10 | 72
20 | 6 | Performance data (cont) | 1 | 11 | 62
20 | 6 | Performance data (cont) | 1 | 12 | 67
20 | 6 | Performance data (cont) | 2 | 1 | TC SHC kW
20 | 6 | Performance data (cont) | 2 | 2 | 79.2 65.7 6.44
20 | 6 | Performance data (cont) | 2 | 3 | 90.1 56.4 6.56
20 | 6 | Performance data (cont) | 2 | 4 | 99.5 46.2 6.68
20 | 6 | Performance data (cont) | 2 | 5 | 85.0 74.9 6.76
20 | 6 | Performance data (cont) | 2 | 6 | 95.2 62.5 6.93
20 | 6 | Performance data (cont) | 2 | 7 | 103.7 49.2 7.06
20 | 6 | Performance data (cont) | 2 | 8 | 88.9 81.9 7.12
20 | 6 | Performance data (cont) | 2 | 9 | 98.5 67.3 7.39
20 | 6 | Performance data (cont) | 2 | 10 | 106.4 51.4 7.49
20 | 6 | Performance data (cont) | 2 | 11 | 92.3 86.0 7.56
20 | 6 | Performance data (cont) | 2 | 12 | 100.9 71.2 7.93
20 | 6 | Performance data (cont) | 3 | 1 | TC SHC kW
20 | 6 | Performance data (cont) | 3 | 2 | 74.6 63.7 6.85
20 | 6 | Performance data (cont) | 3 | 3 | 85.8 54.8 7.06
20 | 6 | Performance data (cont) | 3 | 4 | 96.0 44.9 7.21
20 | 6 | Performance data (cont) | 3 | 5 | 79.4 72.2 7.25
20 | 6 | Performance data (cont) | 3 | 6 | 90.6 60.8 7.46
20 | 6 | Performance data (cont) | 3 | 7 | 100.2 48.1 7.59
20 | 6 | Performance data (cont) | 3 | 8 | 84.4 78.9 7.59
20 | 6 | Performance data (cont) | 3 | 9 | 94.3 66.0 7.90
20 | 6 | Performance data (cont) | 3 | 10 | 103.0 50.5 8.04
20 | 6 | Performance data (cont) | 3 | 11 | 88.3 83.9 8.01
20 | 6 | Performance data (cont) | 3 | 12 | 96.7 70.3 8.45
20 | 6 | Performance data (cont) | 4 | 1 | TC SHC kW
20 | 6 | Performance data (cont) | 4 | 2 | 70.2 61.6 7.26
20 | 6 | Performance data (cont) | 4 | 3 | 80.4 52.5 7.58
20 | 6 | Performance data (cont) | 4 | 4 | 91.4 43.2 7.75
20 | 6 | Performance data (cont) | 4 | 5 | 74.7 69.6 7.62
20 | 6 | Performance data (cont) | 4 | 6 | 82.9 59.2 7.98
20 | 6 | Performance data (cont) | 4 | 7 | 96.1 46.8 8.15
20 | 6 | Performance data (cont) | 4 | 8 | 79.1 75.3 8.08
20 | 6 | Performance data (cont) | 4 | 9 | 84.1 64.4 8.43
20 | 6 | Performance data (cont) | 4 | 10 | 98.9 49.3 8.60
20 | 6 | Performance data (cont) | 4 | 11 | 84.5 80.1 8.53
20 | 6 | Performance data (cont) | 4 | 12 | 91.5 68.7 8.99
20 | 6 | Performance data (cont) | 5 | 1 | TC SHC kW
20 | 6 | Performance data (cont) | 5 | 2 | 65.5 59.3 7.64
20 | 6 | Performance data (cont) | 5 | 3 | 75.6 50.5 8.05
20 | 6 | Performance data (cont) | 5 | 4 | 86.8 41.6 8.28
20 | 6 | Performance data (cont) | 5 | 5 | 70.4 55.4 8.03
20 | 6 | Performance data (cont) | 5 | 6 | 79.9 56.7 8.50
20 | 6 | Performance data (cont) | 5 | 7 | 91.0 45.0 8.69
20 | 6 | Performance data (cont) | 5 | 8 | 75.1 72.2 8.50
20 | 6 | Performance data (cont) | 5 | 9 | 83.0 61.8 8.98
20 | 6 | Performance data (cont) | 5 | 10 | 93.9 47.7 9.16
20 | 6 | Performance data (cont) | 5 | 11 | 79.3 75.0 9.07
20 | 6 | Performance data (cont) | 5 | 12 | 85.9 67.0 9.48
20 | 6 | Performance data (cont) | 6 | 1 | TC SHC kW
20 | 6 | Performance data (cont) | 6 | 2 | 60.7 56.5 8.01
20 | 6 | Performance data (cont) | 6 | 3 | 70.5 48.5 8.47
20 | 6 | Performance data (cont) | 6 | 4 | 81.7 39.8 8.81
20 | 6 | Performance data (cont) | 6 | 5 | 66.0 63.5 8.45
20 | 6 | Performance data (cont) | 6 | 6 | 74.4 54.5 8.96
20 | 6 | Performance data (cont) | 6 | 7 | 85.6 43.2 9.21
20 | 6 | Performance data (cont) | 6 | 8 | 70.9 68.0 8.96
20 | 6 | Performance data (cont) | 6 | 9 | 77.3 59.8 9.44
20 | 6 | Performance data (cont) | 6 | 10 | 88.4 45.9 9.69
20 | 6 | Performance data (cont) | 6 | 11 | 75.0 70.6 9.57
20 | 6 | Performance data (cont) | 6 | 12 | 79.5 64.3 10.00
20 | 6 | Performance data (cont) | 7 | 1 | TC SHC kW
20 | 6 | Performance data (cont) | 7 | 2 | 45.4 53.6 8.43
20 | 6 | Performance data (cont) | 7 | 3 | 65.1 46.3 8.90
20 | 6 | Performance data (cont) | 7 | 4 | 75.7 37.5 9.35
20 | 6 | Performance data (cont) | 7 | 5 | 61.8 60.0 8.88
20 | 6 | Performance data (cont) | 7 | 6 | 68.7 52.4 9.39
20 | 6 | Performance data (cont) | 7 | 7 | 79.9 41.3 9.77
20 | 6 | Performance data (cont) | 7 | 8 | 66.6 63.7 9.43
20 | 6 | Performance data (cont) | 7 | 9 | 71.3 57.6 9.88
20 | 6 | Performance data (cont) | 7 | 10 | 82.6 44.0 10.26
20 | 6 | Performance data (cont) | 7 | 11 | 70.6 66.2 10.06
20 | 6 | Performance data (cont) | 7 | 12 | 73.3 61.9 10.41
21 | 1 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 1 | 2500/0.09
21 | 1 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 2 | 3200/0.105
21 | 1 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 3 | 3800/0.12
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 2 | 62
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 3 | 67
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 4 | 72
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 5 | 62
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 6 | 67
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 7 | 72
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 8 | 62
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 9 | 67
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 10 | 72
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 11 | 62
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 12 | 67
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 2 | 1 | TC SHC kW
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 2 | 2 | 95.1 77.4 7.39
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 2 | 3 | 108.3 64.2 7.69
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 2 | 4 | 116.7 77.2 7.83
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 2 | 5 | 104.5 87.6 7.55
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 2 | 6 | 112.8 70.1 7.74
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 2 | 7 | 121.4 82.0 8.00
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 2 | 8 | 106.2 101.9 7.5
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 2 | 9 | 114.9 74.6 7.81
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 2 | 10 | 124.4 84.7 8.10
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 2 | 11 | 107.0 95.0 7.56
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 2 | 12 | 115.8 75.9 7.84
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 3 | 1 | TC SHC kW
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 3 | 2 | 88.9 79.9 7.91
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 3 | 3 | 102.3 69.3 8.24
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 3 | 4 | 112.0 55.1 8.42
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 3 | 5 | 98.5 93.5 8.08
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 3 | 6 | 108.3 77.7 8.34
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 3 | 7 | 116.9 60.0 8.60
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 3 | 8 | 101.8 100.3 8.10
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 3 | 9 | 110.3 83.4 8.39
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 3 | 10 | 119.2 63.7 8.69
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 3 | 11 | 102.7 102.2 8.15
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 3 | 12 | 110.8 85.1 8.41
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 4 | 1 | TC SHC kW
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 4 | 2 | 81.8 76.4 8.64
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 4 | 3 | 94.7 66.2 8.94
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 4 | 4 | 107.2 53.8 8.85
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 4 | 5 | 91.2 89.5 8.77
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 4 | 6 | 102.5 76.0 9.08
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 4 | 7 | 110.9 58.1 8.96
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 4 | 8 | 96.8 96.7 8.8
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 4 | 9 | 104.4 82.1 9.15
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 4 | 10 | 113.7 61.4 9.03
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 4 | 11 | 98.0 98.0 8.91
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 4 | 12 | 105.0 83.9 9.17
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 5 | 1 | TC SHC kW
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 5 | 2 | 74.2 72.1 9.06
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 5 | 3 | 86.4 62.8 9.42
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 5 | 4 | 101.8 51.8 9.74
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 5 | 5 | 83.4 83.4 9.26
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 5 | 6 | 95.2 73.4 9.56
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 5 | 7 | 105.3 56.9 9.88
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 5 | 8 | 89.7 89.7 9.4
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 5 | 9 | 98.2 80.5 9.65
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 5 | 10 | 107.6 60.8 9.96
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 5 | 11 | 91.3 91.3 9.48
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 5 | 12 | 98.7 82.6 9.66
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 6 | 1 | TC SHC kW
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 6 | 2 | 67.4 67.3 9.71
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 6 | 3 | 77.2 59.1 10.04
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 6 | 4 | 94.2 49.5 10.42
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 6 | 5 | 75.6 75.6 9.97
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 6 | 6 | 83.8 68.9 10.19
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 6 | 7 | 99.0 55.1 10.59
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 6 | 8 | 81.3 81.2 10.1
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 6 | 9 | 87.4 76.3 10.28
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 6 | 10 | 100.6 59.0 10.66
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 6 | 11 | 82.8 82.7 10.19
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 6 | 12 | 88.4 78.7 10.31
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 7 | 1 | TC SHC kW
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 7 | 2 | 63.2 63.2 10.37
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 7 | 3 | 69.2 56.0 10.68
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 7 | 4 | 84.4 46.0 11.09
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 7 | 5 | 68.5 68.5 10.69
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 7 | 6 | 71.8 64.3 10.85
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 7 | 7 | 88.8 51.9 11.27
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 7 | 8 | 73.1 73.0 10.9
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 7 | 9 | 75.0 70.9 10.95
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 7 | 10 | 92.3 56.9 11.37
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 7 | 11 | 74.2 74.2 10.93
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 7 | 12 | 76.0 73.0 10.97
21 | 3 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 1 | 3150/0.13
21 | 3 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 2 | 4200/0.17
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 2 | 62
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 3 | 67
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 4 | 72
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 5 | 62
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 6 | 67
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 7 | 72
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 8 | 62
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 9 | 67
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 2 | 1 | TC SHC kW
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 2 | 2 | 125.1 107.5 9.48
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 2 | 3 | 137.3 90.6 9.60
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 2 | 4 | 147.5 71.7 9.69
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 2 | 5 | 133.0 125.8 9.58
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 2 | 6 | 143.5 101.9 9.67
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 2 | 7 | 154.1 78.7 9.79
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 2 | 8 | 135.1 134.0 9.59
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 2 | 9 | 145.6 109.7 9.69
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 3 | 1 | TC SHC kW
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 3 | 2 | 115.4 103.1 10.15
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 3 | 3 | 129.6 87.7 10.33
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 3 | 4 | 140.9 69.8 10.49
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 3 | 5 | 124.4 120.8 10.29
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 3 | 6 | 135.9 99.8 10.43
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 3 | 7 | 147.3 77.0 10.61
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 3 | 8 | 128.9 128.3 10.34
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 3 | 9 | 138.6 108.6 10.48
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 4 | 1 | TC SHC kW
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 4 | 2 | 105.5 98.9 10.83
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 4 | 3 | 122.0 84.8 11.06
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 4 | 4 | 134.4 67.8 11.30
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 4 | 5 | 115.8 115.7 11.01
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 4 | 6 | 128.2 97.8 11.20
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 4 | 7 | 140.4 75.3 11.41
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 4 | 8 | 122.7 122.7 11.11
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 4 | 9 | 131.5 107.6 11.27
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 5 | 1 | TC SHC kW
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 5 | 2 | 94.1 92.7 11.54
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 5 | 3 | 112.2 81.2 11.83
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 5 | 4 | 126.9 65.3 12.10
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 5 | 5 | 106.5 106.5 11.76
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 5 | 6 | 118.9 94.8 11.98
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 5 | 7 | 132.4 73.2 12.22
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 5 | 8 | 115.2 115.2 11.92
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 5 | 9 | 122.6 105.6 12.06
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 6 | 1 | TC SHC kW
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 6 | 2 | 86.9 86.8 12.26
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 6 | 3 | 100.4 76.4 12.55
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 6 | 4 | 117.9 62.5 12.91
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 6 | 5 | 96.5 96.5 12.58
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 6 | 6 | 105.3 89.8 12.74
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 6 | 7 | 123.7 70.5 13.07
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 6 | 8 | 104.6 104.6 12.73
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 6 | 9 | 109.2 100.4 12.83
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 7 | 1 | TC SHC kW
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 7 | 2 | 79.9 79.9 13.00
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 7 | 3 | 88.5 71.7 13.29
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 7 | 4 | 108.8 59.6 13.72
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 7 | 5 | 86.4 86.3 13.40
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 7 | 6 | 91.7 84.8 13.49
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 7 | 7 | 115.0 67.8 13.91
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 7 | 8 | 94.1 99.1 13.55
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 7 | 9 | 96.0 94.6 13.62
22 | 1 | Performance data (cont) | 1 | 1 | 25
22 | 1 | Performance data (cont) | 1 | 3 | 50
22 | 1 | Performance data (cont) | 1 | 5 | 100
22 | 1 | Performance data (cont) | 1 | 7 | 150
22 | 1 | Performance data (cont) | 1 | 9 | 200
22 | 1 | Performance data (cont) | 1 | 11 | 250
22 | 1 | Performance data (cont) | 1 | 13 | 300
22 | 1 | Performance data (cont) | 1 | 15 | 350
22 | 1 | Performance data (cont) | 2 | 1 | R/s
22 | 1 | Performance data (cont) | 2 | 2 | kW
22 | 1 | Performance data (cont) | 2 | 3 | R/s
22 | 1 | Performance data (cont) | 2 | 4 | kW
22 | 1 | Performance data (cont) | 2 | 5 | R/s
22 | 1 | Performance data (cont) | 2 | 6 | kW
22 | 1 | Performance data (cont) | 2 | 7 | R/s
22 | 1 | Performance data (cont) | 2 | 8 | kW
22 | 1 | Performance data (cont) | 2 | 9 | R/s
22 | 1 | Performance data (cont) | 2 | 10 | kW
22 | 1 | Performance data (cont) | 2 | 11 | R/s
22 | 1 | Performance data (cont) | 2 | 12 | kW
22 | 1 | Performance data (cont) | 2 | 13 | R/s
22 | 1 | Performance data (cont) | 2 | 14 | kW
22 | 1 | Performance data (cont) | 2 | 15 | R/s
22 | 1 | Performance data (cont) | 2 | 16 | kW
22 | 1 | Performance data (cont) | 2 | 17 | R/s
22 | 1 | Performance data (cont) | 3 | 1 | 12.1 12.8 13.5 14.2 14.9 15.7 16.4 17.2 18.0 18.7 19.4
22 | 1 | Performance data (cont) | 3 | 2 | 0.30 0.36 0.42 0.56 0.63 0.72 0.81 0.92 1.03 1.17 1.23
22 | 1 | Performance data (cont) | 3 | 3 | 13.1 13.7 14.4 15.1 15.8 16.5 17.2 17.9 18.6 19.2 19.8
22 | 1 | Performance data (cont) | 3 | 4 | 0.36 0.42 0.49 0.61 0.70 0.78 0.88 0.99 1.10 1.23 1.36
22 | 1 | Performance data (cont) | 3 | 5 | 14.8 15.5 16.1 16.7 17.3 17.9 18.6 19.2 19.9 20.6 21.3
22 | 1 | Performance data (cont) | 3 | 6 | 0.48 0.56 0.63 0.74 0.82 0.91 1.02 1.13 1.26 1.41 1.55
22 | 1 | Performance data (cont) | 3 | 7 | 16.4 17.0 17.5 18.1 18.7 19.3 19.9 20.6 21.2 21.8 22.4
22 | 1 | Performance data (cont) | 3 | 8 | 0.61 0.68 0.77 0.85 0.95 1.06 1.18 1.30 1.44 1.58 1.72
22 | 1 | Performance data (cont) | 3 | 9 | 17.8 18.4 18.9 19.4 19.9 20.5 21.1 21.7 22.3 23.0 23.6
22 | 1 | Performance data (cont) | 3 | 10 | 0.75 0.84 0.93 1.00 1.10 1.21 1.34 1.48 1.63 1.78 1.92
22 | 1 | Performance data (cont) | 3 | 11 | 18.7 19.5 20.1 20.6 21.1 21.7 22.2 22.8 23.4 24.0 24.6
22 | 1 | Performance data (cont) | 3 | 12 | 0.85 0.98 1.09 1.15 1.26 1.37 1.50 1.64 1.79 1.97 2.12
22 | 1 | Performance data (cont) | 3 | 13 | 18.7 20.1 21.1 21.7 22.2 22.8 23.3 23.8 24.4
22 | 1 | Performance data (cont) | 3 | 14 | 0.83 1.05 1.22 1.31 1.42 1.55 1.69 1.83 1.98
22 | 1 | Performance data (cont) | 3 | 15 | 17.8 20.0 21.5 22.9 23.3 23.8 24.3 24.9
22 | 1 | Performance data (cont) | 3 | 16 | 0.67 1.23 1.28 1.50 1.62 1.73 1.86 2.01
22 | 1 | Performance data (cont) | 3 | 17 | 16.0 19.1 21.3 23.9 24.4 24.8 25.2
22 | 1 | Performance data (cont) | 4 | 17 | 25.7
22 | 1 | Performance data (cont) | 4 | 18 | 2.21
22 | 1 | Performance data (cont) | 5 | 15 | 25.4
22 | 1 | Performance data (cont) | 5 | 16 | 2.18
22 | 1 | Performance data (cont) | 5 | 17 | 26.3
22 | 1 | Performance data (cont) | 5 | 18 | 2.38
22 | 1 | Performance data (cont) | 6 | 13 | 24.9
22 | 1 | Performance data (cont) | 6 | 14 | 2.14
22 | 1 | Performance data (cont) | 6 | 15 | 25.9
22 | 1 | Performance data (cont) | 6 | 16 | 2.34
22 | 1 | Performance data (cont) | 6 | 17 | — —
22 | 1 | Performance data (cont) | 7 | 13 | 25.5
22 | 1 | Performance data (cont) | 7 | 14 | 2.29
22 | 1 | Performance data (cont) | 7 | 15
22 | 1 | Performance data (cont) | 7 | 16
22 | 2 | Performance data (cont) | 1 | 1 | 50
22 | 2 | Performance data (cont) | 1 | 3 | 100
22 | 2 | Performance data (cont) | 1 | 5 | 150
22 | 2 | Performance data (cont) | 1 | 7 | 200
22 | 2 | Performance data (cont) | 1 | 9 | 250
22 | 2 | Performance data (cont) | 1 | 11 | 300
22 | 2 | Performance data (cont) | 1 | 13 | 350
22 | 2 | Performance data (cont) | 1 | 15 | 400
22 | 2 | Performance data (cont) | 1 | 17 | 450
22 | 2 | Performance data (cont) | 2 | 1 | R/s
22 | 2 | Performance data (cont) | 2 | 2 | kW
22 | 2 | Performance data (cont) | 2 | 3 | R/s
22 | 2 | Performance data (cont) | 2 | 4 | kW
22 | 2 | Performance data (cont) | 2 | 5 | R/s
22 | 2 | Performance data (cont) | 2 | 6 | kW
22 | 2 | Performance data (cont) | 2 | 7 | R/s
22 | 2 | Performance data (cont) | 2 | 8 | kW
22 | 2 | Performance data (cont) | 2 | 9 | R/s
22 | 2 | Performance data (cont) | 2 | 10 | kW
22 | 2 | Performance data (cont) | 2 | 11 | R/s
22 | 2 | Performance data (cont) | 2 | 12 | kW
22 | 2 | Performance data (cont) | 2 | 13 | R/s
22 | 2 | Performance data (cont) | 2 | 14 | kW
22 | 2 | Performance data (cont) | 2 | 15 | R/s
22 | 2 | Performance data (cont) | 2 | 16 | kW
22 | 2 | Performance data (cont) | 2 | 17 | R/s
22 | 2 | Performance data (cont) | 2 | 18 | kW
22 | 2 | Performance data (cont) | 2 | 19 | R/s
22 | 2 | Performance data (cont) | 3 | 1 | 7.0 7.5 8.1 8.7 9.3 9.8 10.4 11.0
22 | 2 | Performance data (cont) | 3 | 2 | 0.27 0.37 0.47 0.57 0.67 0.80 0.94 1.11
22 | 2 | Performance data (cont) | 3 | 3 | 9.0 9.3 9.7 10.1 10.5 11.0 11.5 12.0
22 | 2 | Performance data (cont) | 3 | 4 | 0.45 0.55 0.65 0.75 0.85 0.99 1.13 1.31
22 | 2 | Performance data (cont) | 3 | 5 | 9.6 10.1 10.6 11.1 11.6 12.1 12.6 13.0
22 | 2 | Performance data (cont) | 3 | 6 | 0.53 0.66 0.79 0.92 1.05 1.21 1.38 1.58
22 | 2 | Performance data (cont) | 3 | 7 | 11.0 11.4 11.8 12.2 12.6 13.0 13.5 13.9
22 | 2 | Performance data (cont) | 3 | 8 | 0.70 0.84 0.98 1.12 1.26 1.43 1.63 1.85
22 | 2 | Performance data (cont) | 3 | 9 | 12.0 12.3 12.7 13.1 13.5 13.9 14.3 14.7
22 | 2 | Performance data (cont) | 3 | 10 | 1.86 1.02 1.18 1.34 1.50 1.67 1.87 2.11
22 | 2 | Performance data (cont) | 3 | 11 | 13.1 13.4 13.7 14.0 14.3 14.7
22 | 2 | Performance data (cont) | 3 | 12 | 1.03 1.19 1.37 1.55 1.73 1.93
22 | 2 | Performance data (cont) | 3 | 13 | 13.9 14.2 14.5 14.8 15.1
22 | 2 | Performance data (cont) | 3 | 14 | 1.25 1.43 1.61 1.79 1.97
22 | 2 | Performance data (cont) | 3 | 15 | 15.0 15.3 15.5 15.7
22 | 2 | Performance data (cont) | 3 | 16 | 1.74 1.86 1.98 2.10
22 | 2 | Performance data (cont) | 3 | 17 | 15.5 15.8
22 | 2 | Performance data (cont) | 3 | 18 | 1.96 2.10
22 | 2 | Performance data (cont) | 3 | 19 | 16.6
22 | 2 | Performance data (cont) | 3 | 20 | 2.45
22 | 2 | Performance data (cont) | 4 | 19 | 16.8
22 | 2 | Performance data (cont) | 4 | 20 | 2.55
22 | 2 | Performance data (cont) | 5 | 17 | 16.1
22 | 2 | Performance data (cont) | 5 | 18 | 2.24
22 | 2 | Performance data (cont) | 5 | 19 | 17
22 | 2 | Performance data (cont) | 5 | 20 | 2.65
22 | 2 | Performance data (cont) | 6 | 17 | 16.4
22 | 2 | Performance data (cont) | 6 | 18 | 2.38
22 | 2 | Performance data (cont) | 6 | 19 | 17.2
22 | 2 | Performance data (cont) | 6 | 20 | 2.75
22 | 2 | Performance data (cont) | 7 | 15 | 15.9
22 | 2 | Performance data (cont) | 7 | 16 | 2.22
22 | 2 | Performance data (cont) | 7 | 17 | 16.7
22 | 2 | Performance data (cont) | 7 | 18 | 2.52
22 | 2 | Performance data (cont) | 7 | 19 | 17.4
22 | 2 | Performance data (cont) | 7 | 20 | 2.85
22 | 2 | Performance data (cont) | 8 | 13 | 15.5
22 | 2 | Performance data (cont) | 8 | 14 | 2.18
22 | 2 | Performance data (cont) | 8 | 15 | 16.2
22 | 2 | Performance data (cont) | 8 | 16 | 2.34
22 | 2 | Performance data (cont) | 8 | 17 | 16.9
22 | 2 | Performance data (cont) | 8 | 18 | 2.69
22 | 2 | Performance data (cont) | 8 | 19 | 17.6
22 | 2 | Performance data (cont) | 8 | 20 | 2.97
22 | 2 | Performance data (cont) | 9 | 11 | 15.1
22 | 2 | Performance data (cont) | 9 | 12 | 2.13
22 | 2 | Performance data (cont) | 9 | 13 | 15.9
22 | 2 | Performance data (cont) | 9 | 14 | 2.41
22 | 2 | Performance data (cont) | 9 | 15 | 16.6
22 | 2 | Performance data (cont) | 9 | 16 | 2.66
22 | 2 | Performance data (cont) | 9 | 17 | 17.3
22 | 2 | Performance data (cont) | 9 | 18 | 2.92
22 | 2 | Performance data (cont) | 9 | 19 | — —
22 | 2 | Performance data (cont) | 10 | 11 | 15.5
22 | 2 | Performance data (cont) | 10 | 12 | 2.36
22 | 2 | Performance data (cont) | 10 | 13 | 16.3
22 | 2 | Performance data (cont) | 10 | 14 | 2.64
22 | 2 | Performance data (cont) | 10 | 15 | 17
22 | 2 | Performance data (cont) | 10 | 16 | 2.91
22 | 2 | Performance data (cont) | 10 | 17
22 | 2 | Performance data (cont) | 10 | 18
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 1 | 1 | 50
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 1 | 3 | 100
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 1 | 5 | 150
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 1 | 7 | 200
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 1 | 9 | 250
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 1 | 11 | 300
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 1 | 13 | 350
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 1 | 15 | 400
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 1 | 17 | 450
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 1 | R/s
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 2 | kW
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 3 | R/s
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 4 | kW
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 5 | R/s
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 6 | kW
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 7 | R/s
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 8 | kW
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 9 | R/s
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 10 | kW
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 11 | R/s
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 12 | kW
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 13 | R/s
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 14 | kW
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 15 | R/s
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 16 | kW
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 17 | R/s
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 18 | kW
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 19 | R/s
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 1 | 7.6 7.9 8.2 8.4 8.8 9.2 9.7 10.2 10.6 11.1
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 2 | 0.36 0.39 0.42 0.56 0.66 0.74 0.85 0.96 1.09 1.24
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 3 | 9.2 9.3 9.5 9.6 10.0 10.4 10.8 11.2 11.7 12.1
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 4 | 0.46 0.51 0.55 0.78 0.86 0.95 1.07 1.19 1.34 1.49
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 5 | 10.2 10.4 10.6 10.8 11.1 11.5 11.8 12.2 12.6 13.0
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 6 | 0.56 0.63 0.69 0.88 0.98 1.09 1.22 1.35 1.51 1.67
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 7 | 11.3 11.4 11.5 11.7 12.0 12.4 12.8 13.1 13.5 13.9
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 8 | 0.70 0.75 0.80 0.96 1.10 1.23 1.37 1.51 1.67 1.86
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 9 | 12.7 12.8 12.9 12.6 12.9 13.2 13.6 13.9 14.3 14.7
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 10 | 0.74 0.86 1.92 1.09 1.22 1.35 1.49 1.66 1.85 2.04
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 11 | 12.9 13.0 13.1 13.3 13.7 14.0 14.4 14.7 15.0
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 12 | 0.80 0.90 1.02 1.18 1.33 1.49 1.65 1.81 2.01
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 13 | 13.6 13.9 14.2 14.3 14.5 14.8 15.1 15.4
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 14 | 0.90 1.02 1.14 1.34 1.47 1.57 1.79 1.98
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 15 | 14.4 14.6 14.8 15.1 15.4 15.6 15.8
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 16 | 1.09 1.13 1.38 1.58 1.67 1.77 1.94
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 17 | 15.2 15.4 15.6 15.9 16.2 16.4 16.5
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 18 | 1.20 1.38 1.65 1.81 1.90 1.97 2.09
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 19 | 16.2 16.3 16.5 16.7 16.8
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 4 | 19 | 17.1
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 4 | 20 | 2.21
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 5 | 19 | 17.3
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 5 | 20 | 2.31
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 6 | 15 | 16.1
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 6 | 16 | 2.13
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 6 | 17 | 16.7
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 6 | 18 | 2.29
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 6 | 19 | 17.4
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 6 | 20 | 2.46
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 7 | 13 | 15.7
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 7 | 14 | 2.18
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 7 | 15 | 16.4
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 7 | 16 | 2.36
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 7 | 17 | 17.1
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 7 | 18 | 2.54
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 7 | 19 | 17.7
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 7 | 20 | 2.71
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 8 | 11 | 15.4
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 8 | 12 | 2.23
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 8 | 13 | 16.1
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 8 | 14 | 2.4
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 8 | 15 | 16.8
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 8 | 16 | 2.59
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 8 | 17 | 17.4
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 8 | 18 | 2.8
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 8 | 19 | 18
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 8 | 20 | 2.99
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 1 | 1 | 50
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 1 | 3 | 100
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 1 | 5 | 150
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 1 | 7 | 200
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 1 | 9 | 250
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 1 | 11 | 300
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 1 | 13 | 350
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 1 | 15 | 400
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 1 | 17 | 450
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 1 | R/s
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 2 | kW
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 3 | R/s
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 4 | kW
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 5 | R/s
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 6 | kW
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 7 | R/s
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 8 | kW
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 9 | R/s
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 10 | kW
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 11 | R/s
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 12 | kW
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 13 | R/s
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 14 | kW
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 15 | R/s
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 16 | kW
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 17 | R/s
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 18 | kW
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | 19 | R/s
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 1 | 9.7 9.9 10.2 10.4 10.7 10.9 11.1 11.4 11.6 11.9 12.1 12.4 12.6 12.8 13.1 13.3 13.6 13.8
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 2 | 0.66 0.72 0.78 0.85 0.91 1.07 1.12 1.19 1.26 1.34 1.42 1.51 1.60 1.70 1.79 1.91 2.01 2.13
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 3 | 10.8 11.0 11.2 11.5 11.7 11.9 12.1 12.4 12.6 12.8 13.0 13.2 13.5 13.7 13.9 14.2 14.4 14.6
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 4 | 0.84 0.89 0.95 1.01 1.08 1.22 1.29 1.36 1.45 1.53 1.62 1.71 1.81 1.92 2.02 2.14 2.26 2.38
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 5 | 11.7 11.9 12.1 12.4 12.6 12.8 13.0 13.2 13.4 13.7 13.9 14.1 14.3 14.5 14.7 15.0 15.2 15.4
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 6 | 0.91 1.01 1.10 1.20 1.29 1.37 1.45 1.54 1.62 1.71 1.80 1.89 2.00 2.12 2.22 2.34 2.47 2.60
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 7 | 12.6 12.8 13.0 13.2 13.4 13.6 13.8 14.0 14.2 14.4 14.6 14.8 15.0 15.3 15.5 15.7 15.9 16.1
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 8 | 1.09 1.15 1.22 1.29 1.38 1.52 1.60 1.69 1.78 1.88 1.99 2.09 2.21 2.33 2.45 2.57 2.69 2.82
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 9 | 13.5 13.7 13.8 14.0 14.2 14.4 14.6 14.7 14.9 15.1 15.3 15.5 15.7 15.9 16.1 16.4 16.6 16.8
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 10 | 1.27 1.34 1.41 1.48 1.55 1.67 1.75 1.84 1.93 2.03 2.15 2.26 2.39 2.51 2.64 2.77 2.92 3.07
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 11 | 14.3 14.5 14.6 14.8 15.0 15.1 15.3 15.5 15.6 15.8 16.0 16.2 16.4 16.6 16.8 17.0 17.2 17.4
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 12 | 1.32 1.46 1.58 1.67 1.76 1.86 1.95 2.03 2.12 2.22 2.32 2.42 2.54 2.68 2.82 2.97 3.12 3.26
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 13 | 15.1 15.2 15.4 15.5 15.7 15.8 16.0 16.2 16.3 16.5 16.7 16.9 17.0 17.2 17.4 17.6 17.8
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 14 | 1.44 1.38 1.71 1.76 1.92 2.02 2.12 2.22 2.33 2.44 2.54 2.64 2.76 2.88 3.01 3.14 3.30
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 15 | 16.0 16.1 16.2 16.3 16.4 16.5 16.7 16.8 17.0 17.2 17.3 17.5 17.7 17.8 18.0
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 16 | 1.55 1.71 1.79 1.89 2.01 2.20 2.29 2.40 2.52 2.64 2.76 2.88 3.01 3.14 3.25
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 17 | 16.9 17.0 17.0 17.1 17.1 17.2 17.3 17.5 17.7 17.8 18.0 18.1 18.3
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 18 | 1.66 1.79 1.92 2.06 2.18 2.36 2.47 2.59 2.71 2.83 2.96 3.09 3.23
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 19 | 17.5 17.5 17.6 17.6 17.7 17.7 17.9 18.1 18.3 18.4 18.6 17.7
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 4 | 19 | 18.9
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 4 | 20 | 3.44
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 5 | 17 | 18.5
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 5 | 18 | 3.36
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 5 | 19 | 19.1
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 5 | 20 | 3.59
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 6 | 17 | 18.6
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 6 | 18 | 3.51
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 6 | 19 | 19.2
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 6 | 20 | 3.75
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 7 | 15 | 18.2
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 7 | 16 | 3.39
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 7 | 17 | 18.8
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 7 | 18 | 3.65
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 7 | 19 | 19.4
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 7 | 20 | 3.9
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 8 | 15 | 18.4
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 8 | 16 | 3.52
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 8 | 17 | 19
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 8 | 18 | 3.8
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 8 | 19 | 19.5
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 8 | 20 | 4.06
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 9 | 13 | 18
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 9 | 14 | 3.47
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 9 | 15 | 18.6
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 9 | 16 | 3.67
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 9 | 17 | 19.2
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 9 | 18 | 3.93
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 9 | 19 | 19.7
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 9 | 20 | 4.22
24 | 1 | Performance data (cont) | 1 | 1 | 25
24 | 1 | Performance data (cont) | 1 | 3 | 50
24 | 1 | Performance data (cont) | 1 | 5 | 100
24 | 1 | Performance data (cont) | 1 | 7 | 150
24 | 1 | Performance data (cont) | 1 | 9 | 200
24 | 1 | Performance data (cont) | 1 | 11 | 250
24 | 1 | Performance data (cont) | 1 | 13 | 300
24 | 1 | Performance data (cont) | 1 | 15 | 350
24 | 1 | Performance data (cont) | 2 | 1 | R/s
24 | 1 | Performance data (cont) | 2 | 2 | kW
24 | 1 | Performance data (cont) | 2 | 3 | R/s
24 | 1 | Performance data (cont) | 2 | 4 | kW
24 | 1 | Performance data (cont) | 2 | 5 | R/s
24 | 1 | Performance data (cont) | 2 | 6 | kW
24 | 1 | Performance data (cont) | 2 | 7 | R/s
24 | 1 | Performance data (cont) | 2 | 8 | kW
24 | 1 | Performance data (cont) | 2 | 9 | R/s
24 | 1 | Performance data (cont) | 2 | 10 | kW
24 | 1 | Performance data (cont) | 2 | 11 | R/s
24 | 1 | Performance data (cont) | 2 | 12 | kW
24 | 1 | Performance data (cont) | 2 | 13 | R/s
24 | 1 | Performance data (cont) | 2 | 14 | kW
24 | 1 | Performance data (cont) | 2 | 15 | R/s
24 | 1 | Performance data (cont) | 2 | 16 | kW
24 | 1 | Performance data (cont) | 2 | 17 | R/s
24 | 1 | Performance data (cont) | 3 | 1 | 10.8 11.5 12.1 12.8 13.4 14.1 14.7 15.4 16.1 16.8 17.5
24 | 1 | Performance data (cont) | 3 | 2 | 0.25 0.30 0.35 0.49 0.54 0.61 0.67 0.75 0.85 0.95 1.05
24 | 1 | Performance data (cont) | 3 | 3 | 12.0 12.5 13.1 13.7 14.3 14.9 15.5 16.1 16.7 17.4 18.1
24 | 1 | Performance data (cont) | 3 | 4 | 0.30 0.35 0.41 0.53 0.59 0.65 0.73 0.82 0.91 1.01 1.10
24 | 1 | Performance data (cont) | 3 | 5 | 13.9 14.4 14.9 15.4 15.9 16.5 17.0 17.6 18.2 18.7 19.6
24 | 1 | Performance data (cont) | 3 | 6 | 0.41 0.47 0.53 0.64 0.71 0.78 0.85 0.95 1.05 1.17 1.25
24 | 1 | Performance data (cont) | 3 | 7 | 15.6 16.1 16.5 17.0 17.5 17.9 18.4 18.9 19.5 20.0 20.5
24 | 1 | Performance data (cont) | 3 | 8 | 0.53 0.60 0.67 0.76 0.84 0.92 1.00 1.10 1.21 1.31 1.41
24 | 1 | Performance data (cont) | 3 | 9 | 17.0 17.5 17.9 18.3 18.8 19.3 19.8 20.3 20.8 21.2 21.8
24 | 1 | Performance data (cont) | 3 | 10 | 0.67 0.74 0.81 0.89 0.97 1.06 1.15 1.27 1.37 1.49 1.61
24 | 1 | Performance data (cont) | 3 | 11 | 18.4 18.8 19.2 19.6 20.0 20.5 21.0 21.5 22.0 22.4 22.8
24 | 1 | Performance data (cont) | 3 | 12 | 0.83 0.88 0.96 1.03 1.11 1.20 1.31 1.43 1.56 1.69 1.77
24 | 1 | Performance data (cont) | 3 | 13 | 19.8 20.1 20.4 20.8 21.3 21.7 22.1 22.5 23.0 23.5 24.1
24 | 1 | Performance data (cont) | 3 | 14 | 1.04 1.09 1.12 1.19 1.28 1.37 1.48 1.60 1.73 1.87 2.01
24 | 1 | Performance data (cont) | 3 | 15 | 21.2 21.5 21.7 21.9 22.3 22.8 23.2 23.6 24.0 24.5
24 | 1 | Performance data (cont) | 3 | 16 | 1.27 1.31 1.36 1.35 1.44 1.55 1.66 1.78 1.91 2.05
24 | 1 | Performance data (cont) | 3 | 17 | 21.9 22.3 22.6 23.0 23.4 23.8 24.2 24.6 25.1
24 | 1 | Performance data (cont) | 4 | 17 | 25.5
24 | 1 | Performance data (cont) | 4 | 18 | 2.23
24 | 1 | Performance data (cont) | 5 | 15 | 25
24 | 1 | Performance data (cont) | 5 | 16 | 2.2
24 | 1 | Performance data (cont) | 5 | 17 | 26
24 | 1 | Performance data (cont) | 5 | 18 | 2.39
24 | 2 | Performance data (cont) | 1 | 1 | 50
24 | 2 | Performance data (cont) | 1 | 3 | 100
24 | 2 | Performance data (cont) | 1 | 5 | 150
24 | 2 | Performance data (cont) | 1 | 7 | 200
24 | 2 | Performance data (cont) | 1 | 9 | 250
24 | 2 | Performance data (cont) | 1 | 11 | 300
24 | 2 | Performance data (cont) | 1 | 13 | 350
24 | 2 | Performance data (cont) | 1 | 15 | 400
24 | 2 | Performance data (cont) | 1 | 17 | 450
24 | 2 | Performance data (cont) | 2 | 1 | R/s
24 | 2 | Performance data (cont) | 2 | 2 | kW
24 | 2 | Performance data (cont) | 2 | 3 | R/s
24 | 2 | Performance data (cont) | 2 | 4 | kW
24 | 2 | Performance data (cont) | 2 | 5 | R/s
24 | 2 | Performance data (cont) | 2 | 6 | kW
24 | 2 | Performance data (cont) | 2 | 7 | R/s
24 | 2 | Performance data (cont) | 2 | 8 | kW
24 | 2 | Performance data (cont) | 2 | 9 | R/s
24 | 2 | Performance data (cont) | 2 | 10 | kW
24 | 2 | Performance data (cont) | 2 | 11 | R/s
24 | 2 | Performance data (cont) | 2 | 12 | kW
24 | 2 | Performance data (cont) | 2 | 13 | R/s
24 | 2 | Performance data (cont) | 2 | 14 | kW
24 | 2 | Performance data (cont) | 2 | 15 | R/s
24 | 2 | Performance data (cont) | 2 | 16 | kW
24 | 2 | Performance data (cont) | 2 | 17 | R/s
24 | 2 | Performance data (cont) | 2 | 18 | kW
24 | 2 | Performance data (cont) | 2 | 19 | R/s
24 | 2 | Performance data (cont) | 3 | 1 | 6.5 7.1 7.5 7.9 8.3 8.8 9.2 9.7
24 | 2 | Performance data (cont) | 3 | 2 | 0.29 0.36 0.43 0.50 0.57 0.66 0.76 0.88
24 | 2 | Performance data (cont) | 3 | 3 | 8.2 8.6 9.0 9.4 9.8 10.2 10.6 11.0
24 | 2 | Performance data (cont) | 3 | 4 | 0.35 0.45 0.55 0.65 0.75 0.85 0.97 1.10
24 | 2 | Performance data (cont) | 3 | 5 | 9.4 9.8 10.2 10.6 11.0 11.3 11.7 12.1
24 | 2 | Performance data (cont) | 3 | 6 | 0.53 0.62 0.73 0.84 0.95 1.06 1.19 1.34
24 | 2 | Performance data (cont) | 3 | 7 | 10.8 11.1 11.4 11.7 12.0 12.4 12.7 13.0
24 | 2 | Performance data (cont) | 3 | 8 | 0.71 0.81 0.92 1.03 1.14 1.29 1.45 1.60
24 | 2 | Performance data (cont) | 3 | 9 | 11.9 12.1 12.4 12.7 13.0 13.3 13.7 14.0
24 | 2 | Performance data (cont) | 3 | 10 | 0.86 0.95 1.09 1.23 1.37 1.52 1.69 1.88
24 | 2 | Performance data (cont) | 3 | 11 | 12.7 13.0 13.3 13.6 13.9 14.2 14.5
24 | 2 | Performance data (cont) | 3 | 12 | 1.10 1.23 1.36 1.49 1.62 1.77 1.93
24 | 2 | Performance data (cont) | 3 | 13 | 13.3 13.6 13.9 14.4 14.8 15.0
24 | 2 | Performance data (cont) | 3 | 14 | 1.31 1.45 1.59 1.73 1.87 2.04
24 | 2 | Performance data (cont) | 3 | 15 | 13.3 13.7 14.1 14.9
24 | 2 | Performance data (cont) | 3 | 16 | 1.55 1.70 1.85 2.00
24 | 2 | Performance data (cont) | 3 | 17 | 13.5 13.9 14.3
24 | 2 | Performance data (cont) | 3 | 18 | 1.80 1.95 2.11
24 | 2 | Performance data (cont) | 3 | 19 | 13.8
24 | 2 | Performance data (cont) | 4 | 19 | 14.2
24 | 2 | Performance data (cont) | 4 | 20 | 2.19
24 | 2 | Performance data (cont) | 5 | 19 | 14.6
24 | 2 | Performance data (cont) | 5 | 20 | 2.35
24 | 2 | Performance data (cont) | 6 | 17 | 15.1
24 | 2 | Performance data (cont) | 6 | 18 | 2.27
24 | 2 | Performance data (cont) | 6 | 19 | 15
24 | 2 | Performance data (cont) | 6 | 20 | 2.53
24 | 2 | Performance data (cont) | 7 | 15 | 15.5
24 | 2 | Performance data (cont) | 7 | 16 | 2.15
24 | 2 | Performance data (cont) | 7 | 17 | 16
24 | 2 | Performance data (cont) | 7 | 18 | 2.43
24 | 2 | Performance data (cont) | 7 | 19 | 16.4
24 | 2 | Performance data (cont) | 7 | 20 | 2.71
24 | 2 | Performance data (cont) | 8 | 15 | 15.8
24 | 2 | Performance data (cont) | 8 | 16 | 2.32
24 | 2 | Performance data (cont) | 8 | 17 | 16.5
24 | 2 | Performance data (cont) | 8 | 18 | 2.6
24 | 2 | Performance data (cont) | 8 | 19 | 17.1
24 | 2 | Performance data (cont) | 8 | 20 | 2.88
24 | 2 | Performance data (cont) | 9 | 13 | 15.3
24 | 2 | Performance data (cont) | 9 | 14 | 2.21
24 | 2 | Performance data (cont) | 9 | 15 | 16.1
24 | 2 | Performance data (cont) | 9 | 16 | 2.5
24 | 2 | Performance data (cont) | 9 | 17 | 16.9
24 | 2 | Performance data (cont) | 9 | 18 | 2.78
24 | 2 | Performance data (cont) | 9 | 19 | — —
24 | 2 | Performance data (cont) | 10 | 11 | 14.8
24 | 2 | Performance data (cont) | 10 | 12 | 2.14
24 | 2 | Performance data (cont) | 10 | 13 | 15.6
24 | 2 | Performance data (cont) | 10 | 14 | 2.41
24 | 2 | Performance data (cont) | 10 | 15 | 16.4
24 | 2 | Performance data (cont) | 10 | 16 | 2.7
24 | 2 | Performance data (cont) | 10 | 17
24 | 2 | Performance data (cont) | 10 | 18
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 1 | 50
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 3 | 100
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 5 | 150
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 7 | 200
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 9 | 250
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 11 | 300
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 13 | 350
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 15 | 400
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 17 | 450
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 1 | R/s
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 2 | kW
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 3 | R/s
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 4 | kW
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 5 | R/s
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 6 | kW
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 7 | R/s
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 8 | kW
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 9 | R/s
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 10 | kW
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 11 | R/s
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 12 | kW
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 13 | R/s
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 14 | kW
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 15 | R/s
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 16 | kW
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 17 | R/s
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 18 | kW
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 19 | R/s
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 1 | 7.3 7.4 7.6 7.6 8.0 8.4 8.8 9.1 9.5 9.9
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 2 | 0.30 0.35 0.39 0.56 0.66 0.74 0.85 0.96 1.09 1.24
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 3 | 8.6 8.7 8.8 8.9 9.3 9.6 10.0 10.3 10.7 11.0
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 4 | 0.43 0.46 0.49 0.67 0.78 0.87 0.96 1.06 1.18 1.31
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 5 | 9.8 9.9 10.0 10.2 10.5 10.7 11.1 11.3 11.7 12.0
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 6 | 0.47 0.58 0.69 0.83 0.91 0.99 1.10 1.22 1.34 1.48
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 7 | 10.8 11.0 11.1 11.1 11.4 11.8 12.1 12.3 12.6 12.9
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 8 | 0.60 0.72 0.77 0.91 1.03 1.14 1.25 1.37 1.51 1.66
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 9 | 11.8 11.9 12.0 12.1 12.4 12.7 12.9 13.2 13.5 13.8
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 10 | 0.72 0.80 0.88 1.05 1.16 1.28 1.40 1.53 1.68 1.84
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 11 | 12.8 12.9 13.0 13.1 13.3 13.5 13.8 14.0 14.3 14.6
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 12 | 0.85 0.86 0.87 1.21 1.30 1.42 1.55 1.69 1.86 2.04
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 13 | 13.6 13.7 13.8 13.9 14.1 14.3 14.5 14.8 15.0
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 14 | 0.90 0.96 1.02 1.22 1.41 1.57 1.70 1.86 2.03
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 15 | 13.6 13.8 13.9 14.0 14.6 15.1 15.3 15.5
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 16 | 0.95 1.02 1.08 0.79 1.25 1.67 1.88 2.02
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 17 | 14.2 14.4 14.6 15.0 15.4 15.7 16.0
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 18 | 0.98 1.08 1.20 1.43 1.64 1.83 2.00
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 19 | 14.4 14.7 15.0 15.6 16.0 16.4 16.7
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 4 | 17 | 16.3
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 4 | 18 | 2.23
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 4 | 19 | 17
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 4 | 20 | 2.36
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 5 | 15 | 15.8
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 5 | 16 | 2.21
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 5 | 17 | 16.4
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 5 | 18 | 2.4
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 5 | 19 | 17.2
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 5 | 20 | 2.62
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 6 | 13 | 15.3
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 6 | 14 | 2.21
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 6 | 15 | 16
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 6 | 16 | 2.42
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 6 | 17 | 16.7
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 6 | 18 | 2.61
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 6 | 19 | 17.3
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 6 | 20 | 2.82
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 1 | 50
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 3 | 100
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 5 | 150
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 7 | 200
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 9 | 250
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 11 | 300
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 13 | 350
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 15 | 400
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 17 | 450
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 1 | R/s
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 2 | kW
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 3 | R/s
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 4 | kW R/s
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 6 | kW
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 7 | R/s
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 8 | kW
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 9 | R/s
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 10 | kW
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 11 | R/s
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 12 | kW
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 13 | R/s
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 14 | kW
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 15 | R/s
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 16 | kW
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 17 | R/s
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 18 | kW
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 19 | R/s
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 1 | 9.0 9.2 9.4 9.7 9.9 10.1 10.4 10.6 10.8 11.1 11.3 11.6 11.9 12.0 12.4 12.6 12.9 13.2
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 2 | 0.58 0.62 0.67 0.73 0.79 0.94 1.01 1.07 1.13 1.21 1.29 1.36 1.45 1.54 1.64 1.75 1.85 1.95
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 3 | 10.2 10.4 10.6 10.8 11.0 11.2 11.4 11.6 11.8 12.0 12.1 12.3 12.5 12.7 12.9 13.1 13.3 13.5
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 4 | 0.73 0.79 0.84 0.89 0.96 1.11 1.17 1.22 1.29 1.35 1.43 1.51 1.58 1.67 1.76 1.85 1.95 2.06
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 5 | 11.3 11.5 11.7 11.9 12.1 12.2 12.4 12.5 12.7 12.9 13.1 13.2 13.4 13.6 13.8 14.0 14.2 14.4
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 6 | 0.88 0.94 1.01 1.08 1.14 1.26 1.33 1.40 1.46 1.55 1.63 1.71 1.81 1.89 1.99 2.08 2.19 2.29
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 7 | 12.1 12.3 12.5 12.7 12.9 13.0 13.3 13.5 13.7 13.8 14.0 14.1 14.3 14.5 14.6 14.8 15.0 15.2
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 8 | 1.00 1.06 1.14 1.21 1.29 1.42 1.51 1.59 1.68 1.76 1.84 1.92 2.00 2.09 2.19 2.30 2.42 2.54
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 9 | 13.2 13.2 13.3 13.5 13.6 13.9 14.0 14.2 14.4 14.5 14.7 14.9 15.1 15.3 15.5 15.6 15.8 16.0
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 10 | 1.21 1.24 1.28 1.35 1.44 1.56 1.64 1.72 1.81 1.91 2.01 2.12 2.23 2.34 2.45 2.56 2.65 2.77
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 11 | 14.2 14.3 14.4 14.5 14.6 14.7 14.8 15.0 15.1 15.3 15.4 15.6 15.8 15.9 16.1 16.3 16.5 16.7
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 12 | 1.24 1.29 1.38 1.48 1.64 1.75 1.81 1.89 1.98 2.07 2.17 2.28 2.39 2.51 2.64 2.77 2.91 3.04
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 13 | 15.1 15.1 15.2 15.3 15.4 15.5 15.6 15.7 15.8 16.0 16.2 16.3 16.5 16.6 16.8 16.9 17.1
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 14 | 1.28 1.41 1.54 1.67 1.82 1.94 2.02 2.10 2.19 2.27 2.36 2.47 2.58 2.69 2.82 2.94 3.08
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 15 | 16.0 16.0 16.1 16.1 16.2 16.2 16.3 16.5 16.6 16.7 16.8 17.0 17.1 17.3 17.4 17.6 17.7
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 16 | 1.44 1.59 1.73 1.86 1.94 2.12 2.21 2.32 2.40 2.51 2.60 2.70 2.80 2.90 3.02 3.14 3.29
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 17 | 16.5 16.6 16.6 16.7 16.8 16.9 17.0 17.2 17.3 17.4 17.5 17.6 17.8 17.9 18.1
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 18 | 1.68 1.81 1.94 2.02 2.13 2.29 2.40 2.51 2.60 2.71 2.82 2.93 3.04 3.16 3.28
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 19 | 17.3 17.3 17.4 17.4 17.5 17.4 17.6 17.8 18.0 18.1 18.2 18.3 18.4
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 4 | 19 | 18.6
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 4 | 20 | 3.41
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 5 | 19 | 18.7
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 5 | 20 | 3.55
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 6 | 17 | 18.2
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 6 | 18 | 3.4
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 6 | 19 | 18.8
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 6 | 20 | 3.67
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 7 | 17 | 18.4
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 7 | 18 | 3.51
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 7 | 19 | 19
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 7 | 20 | 3.8
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 8 | 13 | 17.3
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 8 | 14 | 3.23
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 8 | 15 | 17.9
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 8 | 16 | 3.44
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 8 | 17 | 18.5
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 8 | 18 | 3.65
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 8 | 19 | 19.1
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 8 | 20 | 3.92
26 | 1 | Performance data (cont) | 1 | 1 | 0.1
26 | 1 | Performance data (cont) | 1 | 3 | 0.2
26 | 1 | Performance data (cont) | 1 | 5 | 0.4
26 | 1 | Performance data (cont) | 1 | 7 | 0.6
26 | 1 | Performance data (cont) | 1 | 9 | 0.8
26 | 1 | Performance data (cont) | 1 | 11 | 1
26 | 1 | Performance data (cont) | 1 | 13 | 1.2
26 | 1 | Performance data (cont) | 1 | 15 | 1.4
26 | 1 | Performance data (cont) | 2 | 1 | Rpm
26 | 1 | Performance data (cont) | 2 | 2 | Watts
26 | 1 | Performance data (cont) | 2 | 3 | Rpm
26 | 1 | Performance data (cont) | 2 | 4 | Watts
26 | 1 | Performance data (cont) | 2 | 5 | Rpm
26 | 1 | Performance data (cont) | 2 | 6 | Watts
26 | 1 | Performance data (cont) | 2 | 7 | Rpm
26 | 1 | Performance data (cont) | 2 | 8 | Watts
26 | 1 | Performance data (cont) | 2 | 9 | Rpm
26 | 1 | Performance data (cont) | 2 | 10 | Watts
26 | 1 | Performance data (cont) | 2 | 11 | Rpm
26 | 1 | Performance data (cont) | 2 | 12 | Watts
26 | 1 | Performance data (cont) | 2 | 13 | Rpm
26 | 1 | Performance data (cont) | 2 | 14 | Watts
26 | 1 | Performance data (cont) | 2 | 15 | Rpm
26 | 1 | Performance data (cont) | 2 | 16 | Watts
26 | 1 | Performance data (cont) | 2 | 17 | Rpm
26 | 1 | Performance data (cont) | 2 | 18 | Watts
26 | 1 | Performance data (cont) | 3 | 1 | 731 772 814 852 894 936 978 1021 1064 1107 1150
26 | 1 | Performance data (cont) | 3 | 2 | 304 359 424 562 630 708 795 891 998 1114 1241
26 | 1 | Performance data (cont) | 3 | 3 | 789 826 865 905 945 984 1024 1064 1104 1145 1186
26 | 1 | Performance data (cont) | 3 | 4 | 368 424 497 615 692 771 859 956 1064 1182 1318
26 | 1 | Performance data (cont) | 3 | 5 | 895 930 964 1002 1037 1072 1108 1145 1183 1222 1262
26 | 1 | Performance data (cont) | 3 | 6 | 488 562 636 739 818 899 998 1097 1216 1353 1491
26 | 1 | Performance data (cont) | 3 | 7 | 990 1019 1050 1084 1119 1154 1190 1225 1260 1296 1331
26 | 1 | Performance data (cont) | 3 | 8 | 617 691 774 859 948 1047 1156 1275 1396 1534 1674
26 | 1 | Performance data (cont) | 3 | 9 | 1074 1105 1134 1163 1194 1226 1259 1294 1330 1365 1400
26 | 1 | Performance data (cont) | 3 | 10 | 764 847 930 998 1089 1190 1310 1439 1578 1718 1875
26 | 1 | Performance data (cont) | 3 | 11 | 1130 1174 1208 1235 1266 1297 1327 1359 1392 1426 1461
26 | 1 | Performance data (cont) | 3 | 12 | 875 985 1096 1156 1250 1361 1473 1604 1744 1901 2067
26 | 1 | Performance data (cont) | 3 | 13 | 1168 1213 1265 1303 1330 1362 1393 1423 1454 1485
26 | 1 | Performance data (cont) | 3 | 14 | 921 1078 1234 1318 1413 1534 1656 1779 1927 2084
26 | 1 | Performance data (cont) | 3 | 15 | 1250 1315 1348 1371 1396 1422 1452 1483
26 | 1 | Performance data (cont) | 3 | 16 | 1059 1197 1455 1499 1604 1718 1840 1980
26 | 1 | Performance data (cont) | 3 | 17 | 1345 1401 1421 1433 1460 1485 1510
26 | 1 | Performance data (cont) | 3 | 18 | 1216 1335 1639 1638 1796 1910 2041
26 | 1 | Performance data (cont) | 4 | 17 | 1538
26 | 1 | Performance data (cont) | 4 | 18 | 2171
26 | 1 | Performance data (cont) | 5 | 15 | 1515
26 | 1 | Performance data (cont) | 5 | 16 | 2128
26 | 1 | Performance data (cont) | 5 | 17 | 1569
26 | 1 | Performance data (cont) | 5 | 18 | 2326
26 | 1 | Performance data (cont) | 6 | 15 | 1544
26 | 1 | Performance data (cont) | 6 | 16 | 2283
26 | 1 | Performance data (cont) | 6 | 17 | 1601
26 | 1 | Performance data (cont) | 6 | 18 | 2459
26 | 1 | Performance data (cont) | 7 | 13 | 1518
26 | 1 | Performance data (cont) | 7 | 14 | 2249
26 | 1 | Performance data (cont) | 7 | 15 | 1575
26 | 1 | Performance data (cont) | 7 | 16 | 2445
26 | 1 | Performance data (cont) | 7 | 17
26 | 1 | Performance data (cont) | 7 | 18
26 | 2 | Performance data (cont) | 1 | 1 | 0.2
26 | 2 | Performance data (cont) | 1 | 3 | 0.4
26 | 2 | Performance data (cont) | 1 | 5 | 0.6
26 | 2 | Performance data (cont) | 1 | 7 | 0.8
26 | 2 | Performance data (cont) | 1 | 9 | 1
26 | 2 | Performance data (cont) | 1 | 11 | 1.2
26 | 2 | Performance data (cont) | 1 | 13 | 1.4
26 | 2 | Performance data (cont) | 1 | 15 | 1.6
26 | 2 | Performance data (cont) | 1 | 17 | 1.8
26 | 2 | Performance data (cont) | 2 | 1 | Rpm
26 | 2 | Performance data (cont) | 2 | 2 | Watts
26 | 2 | Performance data (cont) | 2 | 3 | Rpm
26 | 2 | Performance data (cont) | 2 | 4 | Watts
26 | 2 | Performance data (cont) | 2 | 5 | Rpm
26 | 2 | Performance data (cont) | 2 | 6 | Watts
26 | 2 | Performance data (cont) | 2 | 7 | Rpm
26 | 2 | Performance data (cont) | 2 | 8 | Watts
26 | 2 | Performance data (cont) | 2 | 9 | Rpm
26 | 2 | Performance data (cont) | 2 | 10 | Watts
26 | 2 | Performance data (cont) | 2 | 11 | Rpm
26 | 2 | Performance data (cont) | 2 | 12 | Watts
26 | 2 | Performance data (cont) | 2 | 13 | Rpm
26 | 2 | Performance data (cont) | 2 | 14 | Watts
26 | 2 | Performance data (cont) | 2 | 15 | Rpm
26 | 2 | Performance data (cont) | 2 | 16 | Watts
26 | 2 | Performance data (cont) | 2 | 17 | Rpm
26 | 2 | Performance data (cont) | 2 | 18 | Watts
26 | 2 | Performance data (cont) | 2 | 19 | Rpm
26 | 2 | Performance data (cont) | 3 | 1 | 466 473 488 503 511 518 534 549 557 565 581 597 613 629 646 662 679 696 712
26 | 2 | Performance data (cont) | 3 | 2 | 429 448 486 524 539 562 607 653 684 708 763 827 891 965 1039 1123 1207 1301 1396
26 | 2 | Performance data (cont) | 3 | 3 | 564 571 585 585 592 599 613 627 633 639 652 665 679 694 709 724 740 756 771
26 | 2 | Performance data (cont) | 3 | 4 | 567 590 637 684 708 731 787 835 867 891 948 1014 1081 1156 1241 1335 1430 1534 1639
26 | 2 | Performance data (cont) | 3 | 5 | 623 571 641 653 659 665 677 690 697 703 717 713 745 759 772 785 798 811 824
26 | 2 | Performance data (cont) | 3 | 6 | 731 755 803 851 875 899 965 1031 1064 1097 1173 1250 1335 1413 1508 1595 1691 1788 1892
26 | 2 | Performance data (cont) | 3 | 7 | 689 694 705 716 722 727 738 750 756 761 773 786 799 812 825 840 854 868
26 | 2 | Performance data (cont) | 3 | 8 | 894 923 981 1039 1072 1097 1165 1233 1267 1301 1378 1473 1560 1665 1761 1866 1980 2093
26 | 2 | Performance data (cont) | 3 | 9 | 745 750 761 772 778 783 794 805 811 816 827 839 850 862 875
26 | 2 | Performance data (cont) | 3 | 10 | 1041 1079 1156 1233 1275 1310 1378 1456 1499 1543 1621 1709 1805 1901 2015
26 | 2 | Performance data (cont) | 3 | 11 | 799 804 814 824 829 834 844 855 861 866 878 889 900
26 | 2 | Performance data (cont) | 3 | 12 | 1250 1289 1368 1447 1491 1526 1604 1691 1735 1779 1875 1971 2067
26 | 2 | Performance data (cont) | 3 | 13 | 861 864 871 878 884 885 892 902 908 913
26 | 2 | Performance data (cont) | 3 | 14 | 1616 1638 1682 1727 1744 1770 1840 1927 1980 2023
26 | 2 | Performance data (cont) | 3 | 15 | 922 924 929 934 937 939 944
26 | 2 | Performance data (cont) | 3 | 16 | 1902 1928 1980 2032 2058 2084 2119
26 | 2 | Performance data (cont) | 3 | 17 | 759
26 | 2 | Performance data (cont) | 3 | 18 | 2219
26 | 2 | Performance data (cont) | 3 | 19 | 1004
26 | 2 | Performance data (cont) | 3 | 20 | 2640
26 | 2 | Performance data (cont) | 4 | 17 | 790
26 | 2 | Performance data (cont) | 4 | 18 | 2246
26 | 2 | Performance data (cont) | 4 | 19 | 1007
26 | 2 | Performance data (cont) | 4 | 20 | 2652
26 | 2 | Performance data (cont) | 5 | 17 | 853
26 | 2 | Performance data (cont) | 5 | 18 | 2283
26 | 2 | Performance data (cont) | 5 | 19 | 1013
26 | 2 | Performance data (cont) | 5 | 20 | 2677
26 | 2 | Performance data (cont) | 6 | 17 | 916
26 | 2 | Performance data (cont) | 6 | 18 | 2326
26 | 2 | Performance data (cont) | 6 | 19 | 1019
26 | 2 | Performance data (cont) | 6 | 20 | 2702
26 | 2 | Performance data (cont) | 7 | 17 | 947
26 | 2 | Performance data (cont) | 7 | 18 | 2343
26 | 2 | Performance data (cont) | 7 | 19 | 1022
26 | 2 | Performance data (cont) | 7 | 20 | 2710
26 | 2 | Performance data (cont) | 8 | 17 | 979
26 | 2 | Performance data (cont) | 8 | 18 | 2369
26 | 2 | Performance data (cont) | 8 | 19 | 1025
26 | 2 | Performance data (cont) | 8 | 20 | 2727
26 | 2 | Performance data (cont) | 9 | 17 | 987
26 | 2 | Performance data (cont) | 9 | 18 | 2428
26 | 2 | Performance data (cont) | 9 | 19 | 1039
26 | 2 | Performance data (cont) | 9 | 20 | 2791
26 | 2 | Performance data (cont) | 10 | 15 | 949
26 | 2 | Performance data (cont) | 10 | 16 | 2188
26 | 2 | Performance data (cont) | 10 | 17 | 1002
26 | 2 | Performance data (cont) | 10 | 18 | 2495
26 | 2 | Performance data (cont) | 10 | 19 | 1041
26 | 2 | Performance data (cont) | 10 | 20 | 2831
26 | 2 | Performance data (cont) | 11 | 15 | 953
26 | 2 | Performance data (cont) | 11 | 16 | 2232
26 | 2 | Performance data (cont) | 11 | 17 | 1003
26 | 2 | Performance data (cont) | 11 | 18 | 2521
26 | 2 | Performance data (cont) | 11 | 19 | 1045
26 | 2 | Performance data (cont) | 11 | 20 | 2854
26 | 2 | Performance data (cont) | 12 | 15 | 957
26 | 2 | Performance data (cont) | 12 | 16 | 2275
26 | 2 | Performance data (cont) | 12 | 17 | 1004
26 | 2 | Performance data (cont) | 12 | 18 | 2554
26 | 2 | Performance data (cont) | 12 | 19 | 1050
26 | 2 | Performance data (cont) | 12 | 20 | 2878
26 | 2 | Performance data (cont) | 13 | 13 | 924
26 | 2 | Performance data (cont) | 13 | 14 | 2128
26 | 2 | Performance data (cont) | 13 | 15 | 967
26 | 2 | Performance data (cont) | 13 | 16 | 2377
26 | 2 | Performance data (cont) | 13 | 17 | 1010
26 | 2 | Performance data (cont) | 13 | 18 | 2637
26 | 2 | Performance data (cont) | 13 | 19 | 1056
26 | 2 | Performance data (cont) | 13 | 20 | 2925
26 | 2 | Performance data (cont) | 14 | 13 | 935
26 | 2 | Performance data (cont) | 14 | 14 | 2223
26 | 2 | Performance data (cont) | 14 | 15 | 978
26 | 2 | Performance data (cont) | 14 | 16 | 2479
26 | 2 | Performance data (cont) | 14 | 17 | 1019
26 | 2 | Performance data (cont) | 14 | 18 | 2735
26 | 2 | Performance data (cont) | 14 | 19 | 1061
26 | 2 | Performance data (cont) | 14 | 20 | 3002
26 | 2 | Performance data (cont) | 15 | 13 | 946
26 | 2 | Performance data (cont) | 15 | 14 | 2335
26 | 2 | Performance data (cont) | 15 | 15 | 989
26 | 2 | Performance data (cont) | 15 | 16 | 2595
26 | 2 | Performance data (cont) | 15 | 17 | 1030
26 | 2 | Performance data (cont) | 15 | 18 | 2847
26 | 2 | Performance data (cont) | 15 | 19 | — — — — — — —
26 | 2 | Performance data (cont) | 16 | 11 | 911
26 | 2 | Performance data (cont) | 16 | 12 | 2171
26 | 2 | Performance data (cont) | 16 | 13 | 957
26 | 2 | Performance data (cont) | 16 | 14 | 2445
26 | 2 | Performance data (cont) | 16 | 15 | 1000
26 | 2 | Performance data (cont) | 16 | 16 | 2702
26 | 2 | Performance data (cont) | 16 | 17 | 1040
26 | 2 | Performance data (cont) | 16 | 18 | 2956
26 | 2 | Performance data (cont) | 17 | 11 | 923
26 | 2 | Performance data (cont) | 17 | 12 | 2275
26 | 2 | Performance data (cont) | 17 | 13 | 968
26 | 2 | Performance data (cont) | 17 | 14 | 2554
26 | 2 | Performance data (cont) | 17 | 15 | 1011
26 | 2 | Performance data (cont) | 17 | 16 | 2832
26 | 2 | Performance data (cont) | 17 | 17 | — — — — —
26 | 2 | Performance data (cont) | 17 | 18 | — — — — —
26 | 2 | Performance data (cont) | 18 | 9 | 887
26 | 2 | Performance data (cont) | 18 | 10 | 2128
26 | 2 | Performance data (cont) | 18 | 11 | 934
26 | 2 | Performance data (cont) | 18 | 12 | 2386
26 | 2 | Performance data (cont) | 18 | 13 | 980
26 | 2 | Performance data (cont) | 18 | 14 | 2661
26 | 2 | Performance data (cont) | 18 | 15 | 1022
26 | 2 | Performance data (cont) | 18 | 16 | 2933
26 | 2 | Performance data (cont) | 19 | 9 | 900
26 | 2 | Performance data (cont) | 19 | 10 | 2240
26 | 2 | Performance data (cont) | 19 | 11 | 946
26 | 2 | Performance data (cont) | 19 | 12 | 2504
26 | 2 | Performance data (cont) | 19 | 13 | 991
26 | 2 | Performance data (cont) | 19 | 14 | 2775
26 | 2 | Performance data (cont) | 19 | 15 | — — —
26 | 2 | Performance data (cont) | 19 | 16 | — — —
26 | 2 | Performance data (cont) | 20 | 9 | 914
26 | 2 | Performance data (cont) | 20 | 10 | 2369
26 | 2 | Performance data (cont) | 20 | 11 | 959
26 | 2 | Performance data (cont) | 20 | 12 | 2629
26 | 2 | Performance data (cont) | 20 | 13 | 1003
26 | 2 | Performance data (cont) | 20 | 14 | 2886
26 | 2 | Performance data (cont) | 21 | 7 | 881
26 | 2 | Performance data (cont) | 21 | 8 | 2206
26 | 2 | Performance data (cont) | 21 | 9 | 928
26 | 2 | Performance data (cont) | 21 | 10 | 2495
26 | 2 | Performance data (cont) | 21 | 11 | 971
26 | 2 | Performance data (cont) | 21 | 12 | 2759
26 | 2 | Performance data (cont) | 21 | 13 | 1014
26 | 2 | Performance data (cont) | 21 | 14 | 3009
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 1 | 1 | 0.2
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 1 | 3 | 0.4
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 1 | 5 | 0.6
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 1 | 7 | 0.8
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 1 | 9 | 1
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 1 | 11 | 1.2
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 1 | 13 | 1.4
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 1 | 15 | 1.6
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 1 | 17 | 1.8
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 1 | Rpm
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 2 | Watts
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 3 | Rpm
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 4 | Watts
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 5 | Rpm
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 6 | Watts
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 7 | Rpm
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 8 | Watts
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 9 | Rpm
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 10 | Watts
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 11 | Rpm
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 12 | Watts
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 13 | Rpm
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 14 | Watts
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 15 | Rpm
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 16 | Watts
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 17 | Rpm
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 18 | Watts
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 19 | Rpm
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 1 | 471 483 495 508 521 532 544 557 570 583 596 609 622 635 649 662 675 689
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 2 | 369 404 449 485 530 630 677 716 763 818 867 924 989 1047 1123 1190 1267 1353
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 3 | 552 562 573 583 594 605 616 628 639 651 663 674 686 698 713 722 734 746
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 4 | 494 530 575 620 665 763 803 859 907 965 1031 1097 1165 1241 1318 1396 1482 1569
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 5 | 617 627 638 648 659 670 680 690 700 711 721 732 744 755 767 778 790 801
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 6 | 611 656 710 755 809 891 940 998 1064 1123 1190 1267 1335 1413 1491 1578 1674 1761
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 7 | 679 685 694 704 714 725 735 746 757 767 777 787 797 808 818 829 839 851
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 8 | 719 773 827 881 944 1014 1081 1148 1216 1284 1353 1430 1508 1595 1683 1779 1875 1971
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 9 | 740 754 757 759 766 778 787 796 805 815 826 836 847 857 867 878 888
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 10 | 818 881 944 1007 1070 1148 1216 1284 1353 1430 1517 1595 1691 1779 1866 1962 2058
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 11 | 757 765 775 791 807 825 835 844 854 863 871 880 890 901 912
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 12 | 881 944 1007 1070 1150 1275 1353 1430 1508 1587 1665 1753 1849 1945 2050
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 13 | 765 775 793 808 823 874 880 888 897 907 916 926 934
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 14 | 944 1025 1088 1186 1339 1422 1491 1569 1648 1744 1831 1927 2015
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 15 | 811 825 848 887 918 926 933 934 940 947 956
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 16 | 1034 1097 1240 1357 1519 1613 1656 1718 1853 1946 2039
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 17 | 889 907 929 954 963 974 983 988 989 991
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 18 | 1321 1429 1528 1690 1834 1920 1963 1980 2031 2099
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 19 | 946 959 975 987 999
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 4 | 19 | 1012
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 4 | 20 | 2134
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 5 | 19 | 1017
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 5 | 20 | 2177
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 6 | 19 | 1025
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 6 | 20 | 2230
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 7 | 19 | 1032
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 7 | 20 | 2282
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 8 | 19 | 1038
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 8 | 20 | 2318
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 9 | 17 | 997
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 9 | 18 | 2195
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 9 | 19 | 1043
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 9 | 20 | 2380
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 10 | 15 | 966
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 10 | 16 | 2134
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 10 | 17 | 1004
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 10 | 18 | 2291
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 10 | 19 | 1045
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 10 | 20 | 2478
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 11 | 15 | 976
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 11 | 16 | 2238
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 11 | 17 | 1013
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 11 | 18 | 2397
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 11 | 19 | 1051
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 11 | 20 | 2569
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 12 | 13 | 943
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 12 | 14 | 2160
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 12 | 15 | 985
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 12 | 16 | 2344
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 12 | 17 | 1023
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 12 | 18 | 2514
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 12 | 19 | 1059
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 12 | 20 | 2688
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 13 | 13 | 952
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 13 | 14 | 2265
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 13 | 15 | 994
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 13 | 16 | 2451
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 13 | 17 | 1032
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 13 | 18 | 2633
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 13 | 19 | 1068
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 13 | 20 | 2819
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 14 | 11 | 922
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 14 | 12 | 2203
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 14 | 13 | 962
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 14 | 14 | 2371
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 14 | 15 | 1003
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 14 | 16 | 2560
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 14 | 17 | 1042
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 14 | 18 | 2763
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 14 | 19 | 1078
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 14 | 20 | 2952
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 15 | 11 | 933
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 15 | 12 | 2309
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 15 | 13 | 973
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 15 | 14 | 2496
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 15 | 15 | 1011
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 15 | 16 | 2679
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 15 | 17 | 1051
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 15 | 18 | 2895
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 15 | 19 | 1087
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 15 | 20 | 3097
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 16 | 9 | 898
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 16 | 10 | 2212
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 16 | 11 | 943
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 16 | 12 | 2424
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 16 | 13 | 983
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 16 | 14 | 2624
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 16 | 15 | 1021
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 16 | 16 | 2810
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 16 | 17 | 1060
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 16 | 18 | 3029
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 16 | 19 | 1090
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 16 | 20 | 3276
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 1 | 1 | 0.2
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 1 | 3 | 0.4
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 1 | 5 | 0.6
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 1 | 7 | 0.8
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 1 | 9 | 1
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 1 | 11 | 1.2
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 1 | 13 | 1.4
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 1 | 15 | 1.6
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 1 | 17 | 1.8
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 1 | Rpm
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 2 | Watts
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 3 | Rpm
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 4 | Watts
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 5 | Rpm
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 6 | Watts
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 7 | Rpm
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 8 | Watts
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 9 | Rpm
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 10 | Watts
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 11 | Rpm
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 12 | Watts
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 13 | Rpm
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 14 | Watts
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 15 | Rpm
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 16 | Watts
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 17 | Rpm
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 18 | Watts
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | 19 | Rpm
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 1 | 570 584 598 612 626 640 654 668 683 697 711 726 741 755 770 784 799 814 829 843 858
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 2 | 623 676 728 781 873 913 1065 1129 1194 1267 1340 1423 1506 1598 1700 1794 1905 2009 2131 2246 2378
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 3 | 636 649 662 675 688 702 714 727 741 754 767 780 794 808 821 835 849 863 877 892 906
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 4 | 799 842 904 957 1018 1080 1218 1291 1365 1448 1531 1624 1717 1819 1923 2027 2140 2254 2378 2503 2629
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 5 | 693 705 717 729 741 754 767 780 793 806 819 832 845 858 871 884 897 910 923 937 950
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 6 | 886 948 1027 1115 1202 1290 1373 1456 1540 1624 1708 1802 1897 2000 2114 2219 2343 2468 2602 2746 2891
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 7 | 748 759 769 780 792 803 815 827 839 851 864 877 889 902 915 928 941 954 967 980 993
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 8 | 1044 1097 1158 1229 1299 1378 1514 1598 1691 1785 1879 1983 2096 2210 2325 2450 2566 2692 2828 2964 3111
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 9 | 800 809 819 829 840 851 861 873 884 895 907 919 931 943 955 968 981 993 1006 1019
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 10 | 1202 1281 1342 1414 1483 1553 1666 1751 1836 1931 2035 2149 2263 2387 2512 2638 2773 2919 3065 3221
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 11 | 850 858 867 876 886 896 906 916 927 938 949 960 971 983 995 1006 1018 1030 1043
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 12 | 1281 1352 1483 1589 1676 1755 1862 1948 2035 2123 2219 2316 2423 2548 2683 2828 2964 3111 3267
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 13 | 901 907 914 922 930 940 950 959 969 979 989 1000 1011 1022 1033 1044 1056 1067
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 14 | 1360 1457 1536 1606 1773 1913 2027 2123 2228 2334 2441 2548 2647 2764 2882 3010 3147 3304
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 15 | 950 960 963 968 975 983 991 1001 1010 1020 1029 1039 1049 1059 1070 1081
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 16 | 1474 1571 1668 1764 1826 1887 2202 2299 2405 2521 2638 2764 2882 3010 3138 3258
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 17 | 989 1001 1010 1018 1021 1026 1030 1040 1049 1059 1068 1077 1087 1097
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 18 | 1597 1703 1799 1940 2062 2212 2361 2476 2593 2710 2837 2955 3092 3230
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 19 | 1000 1006 1018 1022 1039 1051 1064 1075 1085 1095 1105 1114 1124
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 4 | 19 | 1133
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 4 | 20 | 3442
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 5 | 17 | 1107
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 5 | 18 | 3368
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 5 | 19 | 1143
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 5 | 20 | 3590
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 6 | 17 | 1117
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 6 | 18 | 3516
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 6 | 19 | 1152
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 6 | 20 | 3748
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 7 | 15 | 1092
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 7 | 16 | 3387
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 7 | 17 | 1127
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 7 | 18 | 3655
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 7 | 19 | 1162
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 7 | 20 | 3897
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 8 | 15 | 1103
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 8 | 16 | 3525
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 8 | 17 | 1138
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 8 | 18 | 3804
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 8 | 19 | 1172
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 8 | 20 | 4055
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 9 | 13 | 1079
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 9 | 14 | 3470
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 9 | 15 | 1114
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 9 | 16 | 3674
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 9 | 17 | 1149
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 9 | 18 | 3934
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 9 | 19 | 1182
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 9 | 20 | 4223
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 10 | 11 | 1055
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 10 | 12 | 3424
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 10 | 13 | 1091
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 10 | 14 | 3637
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 10 | 15 | 1126
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 10 | 16 | 3822
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 10 | 17 | 1160
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 10 | 18 | 4083
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 10 | 19 | 1193
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 10 | 20 | 4382
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 11 | 9 | 1032
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 11 | 10 | 3388
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 11 | 11 | 1068
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 11 | 12 | 3590
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 11 | 13 | 1103
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 11 | 14 | 3804
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 11 | 15 | 1137
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 11 | 16 | 4009
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 11 | 17 | 1171
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 11 | 18 | 4242
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 11 | 19 | 1204
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 11 | 20 | 4531
28 | 1 | Performance data (cont) | 1 | 1 | 0.1
28 | 1 | Performance data (cont) | 1 | 3 | 0.2
28 | 1 | Performance data (cont) | 1 | 5 | 0.4
28 | 1 | Performance data (cont) | 1 | 7 | 0.6
28 | 1 | Performance data (cont) | 1 | 9 | 0.8
28 | 1 | Performance data (cont) | 1 | 11 | 1
28 | 1 | Performance data (cont) | 1 | 13 | 1.2
28 | 1 | Performance data (cont) | 1 | 15 | 1.4
28 | 1 | Performance data (cont) | 2 | 1 | Rpm
28 | 1 | Performance data (cont) | 2 | 2 | Watts
28 | 1 | Performance data (cont) | 2 | 3 | Rpm
28 | 1 | Performance data (cont) | 2 | 4 | Watts
28 | 1 | Performance data (cont) | 2 | 5 | Rpm
28 | 1 | Performance data (cont) | 2 | 6 | Watts
28 | 1 | Performance data (cont) | 2 | 7 | Rpm
28 | 1 | Performance data (cont) | 2 | 8 | Watts
28 | 1 | Performance data (cont) | 2 | 9 | Rpm
28 | 1 | Performance data (cont) | 2 | 10 | Watts
28 | 1 | Performance data (cont) | 2 | 11 | Rpm
28 | 1 | Performance data (cont) | 2 | 12 | Watts
28 | 1 | Performance data (cont) | 2 | 13 | Rpm
28 | 1 | Performance data (cont) | 2 | 14 | Watts
28 | 1 | Performance data (cont) | 2 | 15 | Rpm
28 | 1 | Performance data (cont) | 2 | 16 | Watts
28 | 1 | Performance data (cont) | 2 | 17 | Rpm
28 | 1 | Performance data (cont) | 3 | 1 | 656 691 727 765 802 840 878 916 954 993 1031
28 | 1 | Performance data (cont) | 3 | 2 | 258 304 350 487 539 600 669 739 827 916 1022
28 | 1 | Performance data (cont) | 3 | 3 | 722 753 785 821 854 888 923 958 993 1029 1066
28 | 1 | Performance data (cont) | 3 | 4 | 304 350 405 532 585 646 716 795 883 973 1081
28 | 1 | Performance data (cont) | 3 | 5 | 840 867 895 923 953 984 1015 1046 1079 1112 1145
28 | 1 | Performance data (cont) | 3 | 6 | 424 470 534 638 700 771 843 924 1022 1123 1241
28 | 1 | Performance data (cont) | 3 | 7 | 939 965 991 1019 1046 1073 1101 1129 1160 1190 1220
28 | 1 | Performance data (cont) | 3 | 8 | 543 608 672 843 835 907 981 1072 1173 1275 1396
28 | 1 | Performance data (cont) | 3 | 9 | 1024 1050 1076 1099 1126 1154 1182 1209 1237 1264 1292
28 | 1 | Performance data (cont) | 3 | 10 | 672 737 811 883 965 1047 1140 1241 1344 1447 1569
28 | 1 | Performance data (cont) | 3 | 11 | 1106 1127 1151 1178 1201 1226 1252 1280 1309 1336 1363
28 | 1 | Performance data (cont) | 3 | 12 | 829 884 958 1031 1106 1190 1292 1404 1517 1639 1770
28 | 1 | Performance data (cont) | 3 | 13 | 1195 1207 1222 1249 1274 1297 1320 1345 1372 1400 1428
28 | 1 | Performance data (cont) | 3 | 14 | 995 1078 1123 1182 1275 1361 1456 1569 1691 1823 1962
28 | 1 | Performance data (cont) | 3 | 15 | 1269 1285 1301 1316 1338 1363 1388 1410 1434 1459
28 | 1 | Performance data (cont) | 3 | 16 | 1179 1262 1354 1353 1439 1534 1639 1744 1866 1997
28 | 1 | Performance data (cont) | 3 | 17 | 1347 1360 1370 1382 1402 1424 1448 1473 1496
28 | 1 | Performance data (cont) | 4 | 17 | 1519
28 | 1 | Performance data (cont) | 4 | 18 | 2188
28 | 1 | Performance data (cont) | 5 | 15 | 1486
28 | 1 | Performance data (cont) | 5 | 16 | 2145
28 | 1 | Performance data (cont) | 5 | 17 | 1543
28 | 1 | Performance data (cont) | 5 | 18 | 2335
28 | 2 | Performance data (cont) | 1 | 1 | 0.2
28 | 2 | Performance data (cont) | 1 | 3 | 0.4
28 | 2 | Performance data (cont) | 1 | 5 | 0.6
28 | 2 | Performance data (cont) | 1 | 7 | 0.8
28 | 2 | Performance data (cont) | 1 | 9 | 1
28 | 2 | Performance data (cont) | 1 | 11 | 1.2
28 | 2 | Performance data (cont) | 1 | 13 | 1.4
28 | 2 | Performance data (cont) | 1 | 15 | 1.6
28 | 2 | Performance data (cont) | 1 | 17 | 1.8
28 | 2 | Performance data (cont) | 2 | 1 | Rpm
28 | 2 | Performance data (cont) | 2 | 2 | Watts
28 | 2 | Performance data (cont) | 2 | 3 | Rpm
28 | 2 | Performance data (cont) | 2 | 4 | Watts
28 | 2 | Performance data (cont) | 2 | 5 | Rpm
28 | 2 | Performance data (cont) | 2 | 6 | Watts
28 | 2 | Performance data (cont) | 2 | 7 | Rpm
28 | 2 | Performance data (cont) | 2 | 8 | Watts
28 | 2 | Performance data (cont) | 2 | 9 | Rpm
28 | 2 | Performance data (cont) | 2 | 10 | Watts
28 | 2 | Performance data (cont) | 2 | 11 | Rpm
28 | 2 | Performance data (cont) | 2 | 12 | Watts
28 | 2 | Performance data (cont) | 2 | 13 | Rpm
28 | 2 | Performance data (cont) | 2 | 14 | Watts
28 | 2 | Performance data (cont) | 2 | 15 | Rpm
28 | 2 | Performance data (cont) | 2 | 16 | Watts
28 | 2 | Performance data (cont) | 2 | 17 | Rpm
28 | 2 | Performance data (cont) | 2 | 18 | Watts
28 | 2 | Performance data (cont) | 2 | 19 | Rpm
28 | 2 | Performance data (cont) | 3 | 1 | 429 435 447 459 465 471 482 494 501 507 520 533 546 559 572 585 598 610 623
28 | 2 | Performance data (cont) | 3 | 2 | 410 421 443 465 473 487 524 554 577 592 638 684 731 779 835 883 940 998 1056
28 | 2 | Performance data (cont) | 3 | 3 | 424 429 439 549 554 559 569 581 587 592 604 615 626 637 648 660 671 682 694
28 | 2 | Performance data (cont) | 3 | 4 | 538 553 584 615 630 646 684 723 747 771 827 875 932 989 1056 1114 1182 1258 1335
28 | 2 | Performance data (cont) | 3 | 5 | 600 605 615 625 630 635 645 654 659 663 672 683 693 704 715 727 739 750 761
28 | 2 | Performance data (cont) | 3 | 6 | 659 683 731 779 803 827 875 924 956 981 1031 1081 1140 1207 1275 1353 1439 1526 1613
28 | 2 | Performance data (cont) | 3 | 7 | 671 675 683 691 695 699 708 717 722 727 737 747 756 765 775 785 795 806 817
28 | 2 | Performance data (cont) | 3 | 8 | 843 867 916 965 989 1014 1064 1123 1156 1182 1250 1327 1396 1473 1543 1321 1691 1779 1866
28 | 2 | Performance data (cont) | 3 | 9 | 736 739 746 753 757 760 768 776 780 784 793 802 813 823 832 841 851 860
28 | 2 | Performance data (cont) | 3 | 10 | 1046 1071 1122 1173 1199 1224 1284 1344 1378 1404 1473 1552 1630 1718 1814 1901 1997 2084
28 | 2 | Performance data (cont) | 3 | 11 | 778 783 794 805 810 816 824 832 836 839 846 855 863 872 882
28 | 2 | Performance data (cont) | 3 | 12 | 1252 1282 1343 1404 1439 1465 1526 1587 1621 1656 1726 1805 1884 1962 2058
28 | 2 | Performance data (cont) | 3 | 13 | 800 808 825 842 850 859 872 882 887 891 898 906
28 | 2 | Performance data (cont) | 3 | 14 | 1501 1532 1594 1656 1691 1718 1779 1849 1884 1919 1997 2076
28 | 2 | Performance data (cont) | 3 | 15 | 765 795 826 857 873 888 909 925
28 | 2 | Performance data (cont) | 3 | 16 | 1735 1770 1840 1910 1945 1980 2050 2119
28 | 2 | Performance data (cont) | 3 | 17 | 736 759 805
28 | 2 | Performance data (cont) | 3 | 18 | 1945 1988 2075
28 | 2 | Performance data (cont) | 3 | 19 | 666
28 | 2 | Performance data (cont) | 4 | 19 | 697
28 | 2 | Performance data (cont) | 4 | 20 | 2123
28 | 2 | Performance data (cont) | 5 | 19 | 760
28 | 2 | Performance data (cont) | 5 | 20 | 2250
28 | 2 | Performance data (cont) | 6 | 17 | 851
28 | 2 | Performance data (cont) | 6 | 18 | 2162
28 | 2 | Performance data (cont) | 6 | 19 | 823
28 | 2 | Performance data (cont) | 6 | 20 | 2377
28 | 2 | Performance data (cont) | 7 | 17 | 863
28 | 2 | Performance data (cont) | 7 | 18 | 2206
28 | 2 | Performance data (cont) | 7 | 19 | 855
28 | 2 | Performance data (cont) | 7 | 20 | 2445
28 | 2 | Performance data (cont) | 8 | 17 | 897
28 | 2 | Performance data (cont) | 8 | 18 | 2249
28 | 2 | Performance data (cont) | 8 | 19 | 887
28 | 2 | Performance data (cont) | 8 | 20 | 2504
28 | 2 | Performance data (cont) | 9 | 17 | 931
28 | 2 | Performance data (cont) | 9 | 18 | 2326
28 | 2 | Performance data (cont) | 9 | 19 | 935
28 | 2 | Performance data (cont) | 9 | 20 | 2595
28 | 2 | Performance data (cont) | 10 | 17 | 955
28 | 2 | Performance data (cont) | 10 | 18 | 2394
28 | 2 | Performance data (cont) | 10 | 19 | 972
28 | 2 | Performance data (cont) | 10 | 20 | 2678
28 | 2 | Performance data (cont) | 11 | 15 | 931
28 | 2 | Performance data (cont) | 11 | 16 | 2162
28 | 2 | Performance data (cont) | 11 | 17 | 964
28 | 2 | Performance data (cont) | 11 | 18 | 2436
28 | 2 | Performance data (cont) | 11 | 19 | 986
28 | 2 | Performance data (cont) | 11 | 20 | 2718
28 | 2 | Performance data (cont) | 12 | 15 | 936
28 | 2 | Performance data (cont) | 12 | 16 | 2197
28 | 2 | Performance data (cont) | 12 | 17 | 973
28 | 2 | Performance data (cont) | 12 | 18 | 2479
28 | 2 | Performance data (cont) | 12 | 19 | 999
28 | 2 | Performance data (cont) | 12 | 20 | 2759
28 | 2 | Performance data (cont) | 13 | 15 | 946
28 | 2 | Performance data (cont) | 13 | 16 | 2275
28 | 2 | Performance data (cont) | 13 | 17 | 987
28 | 2 | Performance data (cont) | 13 | 18 | 2554
28 | 2 | Performance data (cont) | 13 | 19 | 1019
28 | 2 | Performance data (cont) | 13 | 20 | 2839
28 | 2 | Performance data (cont) | 14 | 15 | 954
28 | 2 | Performance data (cont) | 14 | 16 | 2352
28 | 2 | Performance data (cont) | 14 | 17 | 997
28 | 2 | Performance data (cont) | 14 | 18 | 2637
28 | 2 | Performance data (cont) | 14 | 19 | 1034
28 | 2 | Performance data (cont) | 14 | 20 | 2917
28 | 2 | Performance data (cont) | 15 | 13 | 913
28 | 2 | Performance data (cont) | 15 | 14 | 2154
28 | 2 | Performance data (cont) | 15 | 15 | 961
28 | 2 | Performance data (cont) | 15 | 16 | 2436
28 | 2 | Performance data (cont) | 15 | 17 | 1006
28 | 2 | Performance data (cont) | 15 | 18 | 2727
28 | 2 | Performance data (cont) | 15 | 19 | — — — — — — —
28 | 2 | Performance data (cont) | 16 | 13 | 921
28 | 2 | Performance data (cont) | 16 | 14 | 2240
28 | 2 | Performance data (cont) | 16 | 15 | 969
28 | 2 | Performance data (cont) | 16 | 16 | 2529
28 | 2 | Performance data (cont) | 16 | 17 | 1014
28 | 2 | Performance data (cont) | 16 | 18 | 2807
28 | 2 | Performance data (cont) | 17 | 13 | 930
28 | 2 | Performance data (cont) | 17 | 14 | 2335
28 | 2 | Performance data (cont) | 17 | 15 | 976
28 | 2 | Performance data (cont) | 17 | 16 | 2620
28 | 2 | Performance data (cont) | 17 | 17 | 1021
28 | 2 | Performance data (cont) | 17 | 18 | 2902
28 | 2 | Performance data (cont) | 18 | 11 | 892
28 | 2 | Performance data (cont) | 18 | 12 | 2162
28 | 2 | Performance data (cont) | 18 | 13 | 939
28 | 2 | Performance data (cont) | 18 | 14 | 2428
28 | 2 | Performance data (cont) | 18 | 15 | 984
28 | 2 | Performance data (cont) | 18 | 16 | 2710
28 | 2 | Performance data (cont) | 18 | 17 | — — — —
28 | 2 | Performance data (cont) | 18 | 18 | — — — —
28 | 2 | Performance data (cont) | 19 | 11 | 902
28 | 2 | Performance data (cont) | 19 | 12 | 2266
28 | 2 | Performance data (cont) | 19 | 13 | 948
28 | 2 | Performance data (cont) | 19 | 14 | 2529
28 | 2 | Performance data (cont) | 19 | 15 | 993
28 | 2 | Performance data (cont) | 19 | 16 | 2799
28 | 2 | Performance data (cont) | 20 | 11 | 912
28 | 2 | Performance data (cont) | 20 | 12 | 2369
28 | 2 | Performance data (cont) | 20 | 13 | 958
28 | 2 | Performance data (cont) | 20 | 14 | 2637
28 | 2 | Performance data (cont) | 20 | 15 | 1002
28 | 2 | Performance data (cont) | 20 | 16 | 2902
28 | 2 | Performance data (cont) | 21 | 9 | 870
28 | 2 | Performance data (cont) | 21 | 10 | 2180
28 | 2 | Performance data (cont) | 21 | 11 | 921
28 | 2 | Performance data (cont) | 21 | 12 | 2479
28 | 2 | Performance data (cont) | 21 | 13 | 968
28 | 2 | Performance data (cont) | 21 | 14 | 2751
28 | 2 | Performance data (cont) | 21 | 15
28 | 2 | Performance data (cont) | 21 | 16
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 1 | 0.2
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 3 | 0.4
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 5 | 0.6
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 7 | 0.8
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 9 | 1
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 11 | 1.2
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 13 | 1.4
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 15 | 1.6
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 17 | 1.8
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 1 | Rpm
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 2 | Watts
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 3 | Rpm
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 4 | Watts
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 5 | Rpm
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 6 | Watts
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 7 | Rpm
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 8 | Watts
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 9 | Rpm
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 10 | Watts
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 11 | Rpm
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 12 | Watts
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 13 | Rpm
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 14 | Watts
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 15 | Rpm
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 16 | Watts
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 17 | Rpm
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 18 | Watts
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 19 | Rpm
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 1 | 437 448 460 471 483 484 495 505 516 527 537 548 560 571 582 593 605 616
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 2 | 333 369 404 449 494 562 607 646 692 739 795 851 916 981 1047 1123 1207 1292
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 3 | 517 526 534 544 553 560 570 579 589 599 609 619 629 639 649 659 670 680
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 4 | 440 476 512 557 593 677 723 763 810 859 907 956 1014 1072 1140 1207 1284 1361
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 5 | 590 597 605 613 620 631 638 646 655 664 672 680 688 698 708 717 727 737
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 6 | 566 602 638 683 728 810 851 899 956 1006 1064 1114 1173 1241 1310 1387 1465 1543
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 7 | 653 660 668 675 682 690 699 708 717 724 731 738 747 756 764 773 781 789
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 8 | 692 746 791 361 881 940 998 1047 1106 1165 1216 1275 1344 1422 1499 1578 1648 1726
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 9 | 712 717 723 730 738 747 755 761 767 775 784 794 802 810 816 823 832 841
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 10 | 755 836 908 971 1034 1081 1140 1199 1250 1318 1387 1456 1534 1604 1674 1753 1840 1927
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 11 | 770 778 779 783 789 800 805 812 819 827 833 840 847 856 865 875 883
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 12 | 827 881 944 1052 1150 1233 1284 1344 1413 1482 1552 1621 1700 1788 1875 1962 2050
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 13 | 805 815 825 830 840 850 857 862 867 873 880 888 895 901 908
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 14 | 881 926 980 1070 1159 1353 1447 1517 1578 1639 1718 1805 1884 1971 2050
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 15 | 811 822 835 843 860 879 896 908 915 920 926 931 938
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 16 | 944 989 1052 1150 1195 1233 1473 1639 1753 1831 1901 1971 2108
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 17 | 830 843 855 868 880 925 935 944 952 963
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 18 | 998 1079 1186 1303 1429 1604 1709 1836 1920 2005
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 19 | 883 898 910 924 942 964 975 984 993 1001
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 4 | 17 | 970
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 4 | 18 | 2134
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 4 | 19 | 1007
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 4 | 20 | 2221
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 5 | 17 | 976
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 5 | 18 | 2230
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 5 | 19 | 1017
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 5 | 20 | 2362
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 6 | 17 | 981
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 6 | 18 | 2309
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 6 | 19 | 1024
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 6 | 20 | 2496
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 7 | 15 | 945
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 7 | 16 | 2203
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 7 | 17 | 986
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 7 | 18 | 2389
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 7 | 19 | 1029
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 7 | 20 | 2605
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 8 | 15 | 953
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 8 | 16 | 2300
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 8 | 17 | 993
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 8 | 18 | 2478
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 8 | 19 | 1034
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 8 | 20 | 2707
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 9 | 13 | 915
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 9 | 14 | 2186
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 9 | 15 | 960
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 9 | 16 | 2389
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 9 | 17 | 1000
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 9 | 18 | 2587
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 9 | 19 | 1039
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 9 | 20 | 2800
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 10 | 13 | 924
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 10 | 14 | 2291
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 10 | 15 | 966
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 10 | 16 | 2487
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 10 | 17 | 1008
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 10 | 18 | 2698
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 10 | 19 | 1046
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 10 | 20 | 2904
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 11 | 11 | 889
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 11 | 12 | 2177
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 11 | 13 | 934
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 11 | 14 | 2389
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 11 | 15 | 972
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 11 | 16 | 2587
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 11 | 17 | 1015
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 11 | 18 | 2819
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 11 | 19 | 1053
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 11 | 20 | 3029
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 1 | 0.2
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 3 | 0.4
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 5 | 0.6
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 7 | 0.8
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 9 | 1
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 11 | 1.2
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 13 | 1.4
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 15 | 1.6
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | 17 | 1.8
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 1 | Rpm
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 2 | Watts
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 3 | Rpm
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 4 | Watts
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 5 | Rpm
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 6 | Watts
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 7 | Rpm
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 8 | Watts
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 9 | Rpm
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 10 | Watts
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 11 | Rpm
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 12 | Watts
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 13 | Rpm
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 14 | Watts
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 15 | Rpm
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 16 | Watts
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 17 | Rpm
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 18 | Watts
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | 19 | Rpm
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 1 | 529 541 553 566 579 593 607 621 636 650 665 680 696 711 727 742 758 773 789 805 821
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 2 | 535 579 632 685 737 790 947 1010 1073 1137 1210 1283 1365 1456 1540 1641 1742 1845 1958 2070 2202
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 3 | 605 615 626 636 647 659 670 681 693 705 717 728 739 750 762 774 786 799 812 826 840
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 4 | 693 746 790 843 904 957 1113 1170 1226 1291 1357 1431 1506 1582 1666 1759 1854 1948 2053 2166 2290
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 5 | 669 680 692 702 713 722 732 742 751 761 772 783 794 805 817 828 840 852 863 875 887
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 6 | 834 886 948 1018 1080 1141 1267 1332 1398 1464 1548 1632 1717 1811 1897 1992 2088 2193 2290 2405 2521
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 7 | 719 729 740 751 763 775 782 795 808 819 830 839 848 857 867 877 888 899 910 921 932
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 8 | 948 1009 1071 1141 1220 1290 1423 1506 1590 1674 1759 1836 1914 2000 2096 2193 2307 2423 2548 2665 2792
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 9 | 775 791 792 798 807 817 833 842 851 861 871 883 896 908 919 929 938 947 957 966 976
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 10 | 1158 1211 1237 1290 1352 1431 1565 1641 1725 1811 1905 2009 2123 2237 2343 2450 2557 2656 2773 2891 3019
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 11 | 815 827 832 845 856 867 879 889 898 908 917 925 935 945 955 967 980 992 1003 1014
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 12 | 1308 1369 1413 1510 1589 1624 1751 1819 1897 1974 2070 9175 2281 2387 2512 2638 2773 9910 3047 3184
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 13 | 880 889 895 903 911 920 927 934 942 950 960 969 979 988 996 1005 1015 1025 1036
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 14 | 1352 1448 1571 1668 1747 1799 1940 2018 2105 2193 2272 2370 2468 2575 2692 2819 2946 3083 3230
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 15 | 911 920 929 940 952 965 973 980 987 994 1001 1009 1018 1028 1037 1046 1056 1064
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 16 | 1606 1676 1755 1826 1887 2010 2123 2210 2307 2405 2503 2602 2701 2801 2901 3019 3147 3285
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 17 | 940 951 965 980 989 1000 1013 1022 1030 1037 1045 1051 1058 1066 1074 1084
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 18 | 1685 1747 1843 1940 2054 2150 2290 2396 2503 2602 2710 2828 2937 3047 3166 3276
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 19 | 971 985 999 1010 1021 1035 1046 1058 1068 1077 1085 1092 1100 1106
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 4 | 19 | 1113
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 4 | 20 | 3414
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 5 | 19 | 1121
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 5 | 20 | 3544
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 6 | 17 | 1093
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 6 | 18 | 3396
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 6 | 19 | 1129
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 6 | 20 | 3674
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 7 | 17 | 1103
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 7 | 18 | 3516
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 7 | 19 | 1137
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 7 | 20 | 3795
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 8 | 15 | 1073
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 8 | 16 | 3433
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 8 | 17 | 1112
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 8 | 18 | 3655
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 8 | 19 | 1147
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 8 | 20 | 3925
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 9 | 13 | 1049
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 9 | 14 | 3396
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 9 | 15 | 1083
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 9 | 16 | 3590
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 9 | 17 | 1121
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 9 | 18 | 3804
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 9 | 19 | 1157
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 9 | 20 | 4055
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 10 | 11 | 1024
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 10 | 12 | 3322
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 10 | 13 | 1061
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 10 | 14 | 3553
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 10 | 15 | 1093
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 10 | 16 | 3748
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 10 | 17 | 1129
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 10 | 18 | 3962
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 10 | 19 | 1166
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 10 | 20 | 4204

## Cooling_Capacity
source_page | table_no | page_title | table_row | col_1 | col_2 | col_3 | col_4 | col_5 | col_6 | col_7 | col_8 | col_9 | col_10 | col_11 | col_12 | col_13 | col_14 | col_15 | col_16 | col_17 | col_18 | col_19 | col_20
15 | 1 | Performance data | 1 | col_1: 700/0.05; col_2: 950/0.07
15 | 2 | Performance data | 1 |  | 13 | 16 | 19 | 22 | 13 | 16 | 19 | 22 | 13 | 16 | 19
15 | 2 | Performance data | 2 | TC SHC kW | 15.8 15.8 3.98 | 17.7 15.5 4.11 | 19.6 13.1 4.25 | 21.5 10.4 4.39 | 16.8 16.8 4.08 | 18.7 18.1 4.21 | 20.7 14.9 4.35 | 22.6 11.6 4.49 | 17.4 17.4 4.12 | 19.3 19.3 4.27 | 21.3 16.6 4.41
15 | 2 | Performance data | 3 | TC SHC kW | 15.2 15.2 4.26 | 17.1 15.3 4.41 | 19.0 12.8 4.56 | 20.6 10.2 4.71 | 16.2 16.2 4.38 | 18.1 17.9 4.51 | 20.1 14.7 4.66 | 22.0 11.4 4.82 | 17.0 17.0 4.43 | 18.8 18.8 4.58 | 20.7 16.4 4.73
15 | 2 | Performance data | 4 | TC SHC kW | 14.7 14.7 4.54 | 16.5 15.0 4.70 | 18.4 12.6 4.87 | 20.3 10.0 5.04 | 15.6 15.6 4.66 | 17.5 17.5 4.82 | 19.4 14.5 4.98 | 21.3 11.2 5.15 | 16.6 16.6 4.74 | 18.2 18.2 4.89 | 20.0 16.1 5.05
15 | 2 | Performance data | 5 | TC SHC kW | 14.1 14.1 4.81 | 15.9 14.7 4.99 | 17.8 12.3 5.17 | 19.7 9.8 5.36 | 15.0 15.0 4.92 | 16.9 16.9 5.10 | 18.8 14.3 5.29 | 20.7 11.0 5.48 | 16.2 16.2 5.05 | 17.7 17.7 5.20 | 19.4 15.8 5.37
15 | 2 | Performance data | 6 | TC SHC kW | 13.7 13.7 5.01 | 15.5 14.5 5.20 | 17.3 12.2 5.39 | 19.3 9.6 5.60 | 14.5 14.5 5.12 | 16.4 16.4 5.31 | 18.2 14.1 5.52 | 20.2 10.9 5.73 | 15.8 15.8 5.28 | 17.3 17.3 5.61 | 18.8 15.6 5.61
15 | 2 | Performance data | 7 | TC SHC kW | 12.7 12.7 5.33 | 14.6 14.1 5.54 | 16.5 11.8 5.76 | 18.3 9.3 5.99 | 14.0 14.0 5.46 | 15.6 15.6 5.68 | 17.3 13.7 5.90 | 19.2 10.6 6.13 | 15.4 15.4 5.68 | 16.6 16.6 5.83 | 17.9 15.2 5.99
15 | 2 | Performance data | 8 | TC SHC kW | 12.0 12.0 5.60 | 13.8 13.8 5.82 | 15.8 11.5 6.05 | 17.6 9.1 6.29 | 13.5 13.5 5.75 | 15.1 15.1 5.97 | 16.7 13.4 6.20 | 18.5 10.3 6.45 | 15.1 15.1 5.99 | 16.1 16.1 6.14 | 17.2 14.8 6.31
15 | 2 | Performance data | 9 | TC SHC kW | 11.2 11.2 5.85 | 13.1 13.1 6.09 | 15.1 11.2 6.34 | 16.9 8.8 6.60 | 13.0 13.0 6.04 | 14.5 14.5 6.26 | 15.9 13.1 6.50 | 17.7 10.0 6.76 | 14.8 14.8 6.31 | 15.5 15.5 6.46 | 16.5 14.4 6.61
15 | 2 | Performance data | 10 | TC SHC kW | 10.5 10.5 6.11 | 12.4 12.4 6.36 | 14.4 11.0 6.63 | 16.2 8.6 6.91 | 12.7 12.7 6.31 | 13.9 13.9 6.56 | 15.3 12.8 6.81 | 16.9 9.8 7.08 | 14.4 14.4 6.62 | 15.0 15.0 6.77 | 15.7 14.1 6.92
16 | 1 | Performance data (cont) | 1 |  | 14 | 16 | 18 | 20 | 22 | 14 | 16 | 18 | 20
16 | 1 | Performance data (cont) | 2 | TC SHC kW | 19.5 19.4 5.02 | 20.9 18.0 5.16 | 22.5 16.2 5.34 | 24.3 14.3 5.54 | 26.0 12.3 5.72 | 21.6 21.4 5.28 | 22.3 20.5 5.37 | 23.7 18.5 5.52 | 25.3 16.1 5.70
16 | 1 | Performance data (cont) | 3 | TC SHC kW | 19.1 18.9 5.25 | 20.4 17.7 5.38 | 21.9 16.0 5.56 | 23.7 14.1 5.76 | 25.4 12.1 5.96 | 21.0 21.0 5.51 | 21.7 20.2 5.58 | 23.1 18.3 5.74 | 24.7 15.9 5.92
16 | 1 | Performance data (cont) | 4 | TC SHC kW | 18.6 18.4 5.49 | 19.8 17.3 5.61 | 21.3 15.7 5.78 | 23.0 13.9 5.98 | 24.8 11.9 6.19 | 20.5 20.5 5.74 | 21.1 19.8 5.8 | 22.4 18.0 5.96 | 24.1 15.7 6.15
16 | 1 | Performance data (cont) | 5 | TC SHC kW | 18.0 17.8 5.77 | 19.1 16.9 5.88 | 20.6 15.4 6.04 | 22.2 13.6 6.25 | 23.9 11.6 6.47 | 19.9 19.8 6.03 | 20.3 19.4 6.07 | 21.5 17.7 6.22 | 23.2 15.4 6.43
16 | 1 | Performance data (cont) | 6 | TC SHC kW | 17.3 17.2 6.09 | 18.2 16.4 6.18 | 19.63 15.0 6.34 | 21.3 13.2 6.55 | 23.0 11.3 6.77 | 18.2 19.1 6.33 | 19.4 18.9 6.37 | 20.6 17.3 6.61 | 22.3 15.0 6.73
16 | 1 | Performance data (cont) | 7 | TC SHC kW | 16.6 16.6 6.40 | 18.3 15.9 6.48 | 18.7 14.6 6.63 | 20.3 12.8 6.84 | 22.0 10.9 7.07 | 18.4 18.4 6.65 | 18.6 18.3 6.67 | 19.6 16.9 6.81 | 21.3 14.7 7.02
16 | 1 | Performance data (cont) | 8 | TC SHC kW | 15.9 15.9 6.71 | 16.4 15.4 6.77 | 17.7 14.2 6.92 | 19.4 12.5 7.13 | 21.0 10.6 7.36 | 17.7 17.7 6.97 | 17.7 17.6 6.97 | 18.7 16.4 7.10 | 20.2 14.3 7.30
16 | 1 | Performance data (cont) | 9 | TC SHC kW | 15.2 15.2 7.02 | 15.5 14.9 7.05 | 16.7 13.8 7.20 | 18.3 12.1 7.41 | 19.9 10.2 7.64 | 16.9 16.9 7.27 | 16.9 16.9 7.27 | 17.7 15.8 7.39 | 19.1 13.9 7.57
16 | 1 | Performance data (cont) | 10 | TC SHC kW | 14.4 14.4 7.33 | 14.5 14.3 7.33 | 15.6 13.3 7.47 | 17.3 11.7 7.67 | 18.8 9.9 7.91 | 16.1 16.1 7.56 | 16.1 16.1 7.57 | 16.8 15.2 7.67 | 18.0 13.5 7.85
16 | 2 | Performance data (cont) | 1 |  | 14 | 16 | 18 | 20 | 22 | 14 | 16 | 18 | 20
16 | 2 | Performance data (cont) | 2 | TC SHC kW | 21.8 21.8 5.33 | 22.5 20.9 5.41 | 23.9 18.9 5.55 | 25.5 16.4 5.73 | 27.1 13.6 5.91 | 22.9 22.8 5.49 | 23.1 22.4 5.51 | 24.3 20.5 5.65 | 26.1 17.7 5.83
16 | 2 | Performance data (cont) | 3 | TC SHC kW | 21.3 21.2 5.55 | 21.9 20.6 5.62 | 23.3 18.7 5.77 | 24.9 16.2 5.96 | 26.5 13.5 6.14 | 22.4 22.3 5.72 | 22.5 22.0 5.73 | 23.7 20.2 5.86 | 25.4 17.5 6.05
16 | 2 | Performance data (cont) | 4 | TC SHC kW | 20.8 20.7 5.78 | 21.2 20.2 5.84 | 22.5 18.4 5.98 | 24.2 16.0 6.17 | 25.9 13.3 6.38 | 21.8 21.8 5.94 | 21.9 21.7 5.96 | 23.1 20.0 6.08 | 24.7 17.3 6.28
16 | 2 | Performance data (cont) | 5 | TC SHC kW | 20.2 20.2 6.07 | 20.5 19.8 6.11 | 21.7 18.1 6.25 | 23.4 15.7 6.45 | 25.2 13.0 6.66 | 21.2 21.2 6.23 | 21.2 21.0 6.23 | 22.2 19.5 6.36 | 23.8 17.0 6.54
16 | 2 | Performance data (cont) | 6 | TC SHC kW | 19.5 19.4 6.39 | 19.6 19.2 6.41 | 20.7 17.7 6.55 | 22.4 15.3 6.75 | 24.1 12.7 6.96 | 20.4 20.4 6.54 | 20.4 20.4 6.54 | 20.7 19.0 6.66 | 22.8 16.6 6.84
16 | 2 | Performance data (cont) | 7 | TC SHC kW | 18.7 18.7 6.69 | 18.7 18.6 6.70 | 19.8 17.2 6.83 | 21.3 15.0 7.04 | 23.1 12.4 7.26 | 19.6 19.6 6.86 | 19.6 19.6 6.86 | 20.4 18.4 6.95 | 21.7 16.3 7.12
16 | 2 | Performance data (cont) | 8 | TC SHC kW | 17.9 17.9 7.01 | 17.9 17.9 7.01 | 18.8 16.7 7.13 | 20.3 14.6 7.33 | 22.0 12.1 7.55 | 18.8 18.8 7.16 | 18.8 18.8 7.16 | 19.4 17.8 7.25 | 20.6 15.9 7.41
16 | 2 | Performance data (cont) | 9 | TC SHC kW | 17.1 17.1 7.31 | 17.1 17.1 7.31 | 17.9 16.1 7.42 | 19.2 14.2 7.59 | 20.8 11.7 7.83 | 17.9 17.9 7.46 | 17.9 17.9 7.47 | 18.5 17.2 7.54 | 19.5 15.5 7.69
16 | 2 | Performance data (cont) | 10 | TC SHC kW | 16.3 16.3 7.61 | 16.3 16.3 7.61 | 16.9 15.4 7.70 | 18.0 13.9 7.87 | 19.6 11.4 8.1 | 17.1 17.1 7.76 | 17.1 17.1 7.77 | 17.4 16.5 7.82 | 18.3 15.1 7.95
17 | 1 | COOLING CAPACITIES — SI (cont) | 1 | 1200/0.07 | 14: 1400/.08
17 | 2 | COOLING CAPACITIES — SI (cont) | 1 |  | 13 | 16 | 19 | 22 | 13 | 16 | 19 | 22 | 13 | 16 | 19
17 | 2 | COOLING CAPACITIES — SI (cont) | 2 | TC SHC kW | 24.7 24.1 6.25 | 25.2 23.2 6.38 | 28.4 19.3 6.60 | 30.8 15.0 6.70 | 26.0 25.2 6.60 | 26.2 24.6 6.68 | 29.1 20.5 6.97 | 31.5 15.5 7.06 | 27.9 26.5 7.25 | 27.9 26.5 7.25 | 29.9 22.0 7.66
17 | 2 | COOLING CAPACITIES — SI (cont) | 3 | TC SHC kW | 24.0 23.4 6.61 | 24.3 22.8 6.69 | 27.5 19.0 6.96 | 30.3 14.8 7.09 | 25.5 24.6 6.97 | 25.5 24.3 7.02 | 28.4 20.4 7.35 | 30.9 15.4 7.46 | 27.1 25.7 7.61 | 27.1 25.8 7.60 | 29.3 22.0 8.04
17 | 2 | COOLING CAPACITIES — SI (cont) | 4 | TC SHC kW | 23.0 22.5 7.00 | 23.2 22.0 7.06 | 26.5 18.7 7.33 | 29.6 14.6 7.48 | 24.7 23.9 7.34 | 24.7 23.9 7.34 | 27.5 20.1 7.71 | 30.3 15.2 7.86 | 26.4 25.0 7.98 | 26.4 25.0 7.97 | 28.4 21.8 8.42
17 | 2 | COOLING CAPACITIES — SI (cont) | 5 | TC SHC kW | 22.3 21.7 7.32 | 22.4 21.4 7.36 | 25.5 18.4 7.71 | 28.7 14.3 7.87 | 23.7 22.8 7.72 | 23.7 22.8 7.72 | 26.3 19.7 8.09 | 29.4 15.0 8.25 | 25.6 24.2 8.37 | 25.6 24.2 8.36 | 27.3 21.5 8.77
17 | 2 | COOLING CAPACITIES — SI (cont) | 6 | TC SHC kW | 21.7 21.1 7.56 | 21.7 20.9 7.59 | 24.6 17.9 8.01 | 28.0 14.1 8.17 | 23.1 22.2 8.00 | 23.0 22.2 7.99 | 25.6 19.5 8.37 | 28.7 14.8 8.57 | 25.0 23.6 8.66 | 25.0 23.6 8.65 | 26.4 21.2 9.03
17 | 2 | COOLING CAPACITIES — SI (cont) | 7 | TC SHC kW | 20.7 20.1 7.96 | 20.7 20.1 7.96 | 23.1 17.4 8.44 | 26.7 13.6 8.66 | 22.0 21.2 8.42 | 22.0 21.2 8.41 | 23.9 18.8 8.82 | 27.4 14.3 9.06 | 23.6 22.2 9.15 | 23.6 22.2 9.14 | 25.0 20.7 9.47
17 | 2 | COOLING CAPACITIES — SI (cont) | 8 | TC SHC kW | 19.9 19.3 8.29 | 19.9 19.3 8.29 | 22.0 16.9 8.78 | 25.5 13.2 9.04 | 21.2 20.3 8.75 | 21.2 20.3 8.75 | 22.7 18.3 9.15 | 26.3 14.0 9.44 | 22.7 21.3 9.52 | 22.7 21.3 9.51 | 23.7 20.2 9.80
17 | 2 | COOLING CAPACITIES — SI (cont) | 9 | TC SHC kW | 19.1 18.5 8.62 | 19.1 18.5 8.62 | 20.8 16.4 9.05 | 24.3 12.8 9.42 | 20.3 19.4 9.08 | 20.3 19.4 9.08 | 21.5 17.8 9.48 | 25.0 13.5 9.83 | 21.8 20.4 9.88 | 21.8 20.4 9.87 | 22.3 19.5 10.10
18 | 1 | Performance data (cont) | 1 |  | 14 | 16 | 18 | 20 | 22 | 14 | 16 | 18 | 20
18 | 1 | Performance data (cont) | 2 | TC SHC kW | 26.6 26.4 6.82 | 28.2 24.8 6.98 | 30.5 22.8 7.17 | 33.1 20.3 7.35 | 34.7 17.3 7.42 | 30.5 30.4 7.09 | 31.4 29.3 7.17 | 32.7 26.2 7.27 | 34.3 22.2 7.39
18 | 1 | Performance data (cont) | 3 | TC SHC kW | 25.8 25.6 7.20 | 27.0 24.2 7.34 | 29.4 22.3 7.54 | 32.1 19.9 7.73 | 33.8 16.8 7.82 | 29.6 29.5 7.47 | 30.4 28.7 7.53 | 31.8 25.9 7.65 | 33.5 22.2 7.80
18 | 1 | Performance data (cont) | 4 | TC SHC kW | 24.7 24.6 7.61 | 25.8 23.5 7.93 | 28.2 21.7 8.11 | 30.8 19.4 8.32 | 32.8 16.4 8.45 | 28.5 28.5 8.09 | 29.1 27.9 8.12 | 30.7 25.4 8.26 | 32.6 21.9 8.46
18 | 1 | Performance data (cont) | 5 | TC SHC kW | 23.6 23.5 8.03 | 24.5 22.7 8.13 | 26.6 21.1 8.31 | 29.4 18.8 8.53 | 31.8 16.1 8.67 | 27.3 27.3 8.30 | 27.7 27.0 8.32 | 29.4 24.8 8.47 | 31.5 21.6 8.67
18 | 1 | Performance data (cont) | 6 | TC SHC kW | 22.4 22.3 8.47 | 23.0 21.8 8.53 | 25.0 20.3 8.73 | 27.9 18.2 8.96 | 30.7 17.8 9.15 | 26.1 26.0 8.74 | 26.3 26.0 8.74 | 27.9 24.1 8.89 | 30.1 21.2 9.11
18 | 1 | Performance data (cont) | 7 | TC SHC kW | 21.1 21.1 8.95 | 21.5 20.9 8.97 | 23.4 19.6 9.15 | 26.2 17.5 9.40 | 29.5 15.3 9.64 | 24.7 24.7 9.20 | 24.7 24.7 9.20 | 26.4 23.3 9.34 | 28.7 20.7 9.56
18 | 1 | Performance data (cont) | 8 | TC SHC kW | 20.0 20.0 9.40 | 20.1 19.9 9.40 | 21.7 18.7 9.60 | 24.4 16.8 9.86 | 27.9 14.8 10.11 | 23.1 23.1 9.70 | 23.1 23.1 9.71 | 24.4 22.0 9.82 | 26.6 20.0 10.03
18 | 1 | Performance data (cont) | 9 | TC SHC kW | 19.1 10.1 9.89 | 19.1 19.1 9.89 | 20.3 17.9 10.06 | 22.6 16.2 10.32 | 26.0 14.2 10.59 | 21.5 21.5 10.22 | 21.5 21.5 10.22 | 22.4 20.7 10.31 | 24.3 19.1 10.50
18 | 1 | Performance data (cont) | 10 | TC SHC kW | 18.3 18.3 10.37 | 18.3 18.3 10.37 | 19.1 17.2 10.52 | 20.9 15.5 10.77 | 24.0 13.5 11.07 | 20.0 20.0 10.74 | 20.0 20.0 10.74 | 20.4 18.4 10.81 | 21.9 18.1 10.98
18 | 2 | Performance data (cont) | 1 |  | 14 | 16 | 18 | 20 | 22 | 14 | 16 | 18 | 20
18 | 2 | Performance data (cont) | 2 | TC SHC kW | 31.5 31.4 7.12 | 31.9 30.6 7.16 | 33.3 27.8 7.30 | 35.3 24.0 7.50 | 37.2 19.9 7.70 | 31.7 31.7 7.15 | 23.1 31.1 7.18 | 33.5 28.3 7.32 | 35.3 24.4 7.51
18 | 2 | Performance data (cont) | 3 | TC SHC kW | 30.8 30.8 7.53 | 31.0 30.1 7.54 | 32.4 27.4 7.68 | 34.2 23.6 7.88 | 36.2 19.6 8.10 | 31.0 31.0 7.54 | 31.2 30.5 7.57 | 32.5 27.9 7.71 | 34.4 24.0 7.90
18 | 2 | Performance data (cont) | 4 | TC SHC kW | 30.0 30.0 7.95 | 30.1 29.6 7.97 | 31.4 27.2 8.11 | 33.2 23.4 8.30 | 35.2 19.3 8.51 | 30.3 30.2 7.99 | 30.4 30.1 7.99 | 31.6 27.6 8.13 | 33.3 23.7 8.31
18 | 2 | Performance data (cont) | 5 | TC SHC kW | 29.1 29.1 8.40 | 29.1 29.0 8.41 | 30.3 26.7 8.54 | 32.1 23.1 8.73 | 34.0 18.9 8.95 | 29.4 29.4 8.44 | 29.4 29.4 8.44 | 30.5 27.1 8.56 | 32.2 23.5 8.75
18 | 2 | Performance data (cont) | 6 | TC SHC kW | 28.1 27.9 8.87 | 28.0 28.0 8.87 | 29.1 26.1 8.89 | 30.8 22.8 9.17 | 32.8 18.5 9.40 | 28.3 28.3 8.91 | 28.3 28.3 8.91 | 29.3 26.5 9.01 | 31.0 23.3 9.19
18 | 2 | Performance data (cont) | 7 | TC SHC kW | 26.5 14.7 9.37 | 26.5 26.5 9.36 | 27.7 25.1 9.46 | 29.5 22.5 9.64 | 31.5 18.3 9.88 | 27.0 26.9 9.41 | 27.0 27.0 9.40 | 28.0 25.6 9.50 | 29.7 23.0 9.66
18 | 2 | Performance data (cont) | 8 | TC SHC kW | 24.8 24.8 9.87 | 24.8 24.8 9.87 | 25.7 23.8 9.96 | 27.5 21.8 10.12 | 30.0 18.0 10.36 | 25.2 25.2 9.92 | 25.2 25.2 9.92 | 26.1 24.4 9.99 | 27.7 22.3 10.13
18 | 2 | Performance data (cont) | 9 | TC SHC kW | 23.0 23.0 10.39 | 23.0 23.0 10.39 | 23.7 22.4 10.45 | 25.3 20.9 10.59 | 28.3 17.5 10.86 | 23.4 23.4 10.43 | 23.4 23.4 10.43 | 24.0 23.0 10.49 | 25.5 21.4 10.61
18 | 2 | Performance data (cont) | 10 | TC SHC kW | 21.3 21.3 10.93 | 21.3 21.3 10.93 | 21.6 21.0 10.95 | 22.8 19.9 11.07 | 26.5 17.0 11.38 | 21.6 21.6 10.97 | 21.6 21.6 10.97 | 21.8 21.4 10.99 | 23.0 20.4 11.10
19 | 1 | COOLING CAPACITIES — SI (cont) | 1 | 1500/0.13 | 14: 2000/0.17
19 | 2 | COOLING CAPACITIES — SI (cont) | 1 |  | 13 | 16 | 19 | 22 | 13 | 16 | 19 | 22 | 13 | 16 | 19
19 | 2 | COOLING CAPACITIES — SI (cont) | 2 | TC SHC kW | 34.7 34.7 8.92 | 38.0 33.8 8.99 | 41.4 28.1 9.08 | 44.4 22.0 9.13 | 37.0 37.0 9.00 | 40.0 39.9 9.06 | 43.2 31.7 9.13 | 46.3 24.0 9.22 | 36.6 36.6 9.05 | 40.1 40.1 9.10 | 43.6 33.5 9.15
19 | 2 | COOLING CAPACITIES — SI (cont) | 3 | TC SHC kW | 32.1 32.1 9.34 | 35.8 32.8 9.46 | 39.6 27.4 9.60 | 43.0 21.6 9.70 | 34.8 34.8 9.47 | 38.2 38.2 9.57 | 41.6 31.1 9.68 | 44.9 23.7 9.80 | 35.5 35.5 9.60 | 38.7 38.7 9.63 | 42.1 32.4 9.74
19 | 2 | COOLING CAPACITIES — SI (cont) | 4 | TC SHC kW | 29.4 29.4 9.78 | 33.6 31.9 9.94 | 37.9 26.7 10.12 | 41.6 21.1 10.27 | 32.9 32.9 9.95 | 36.3 36.3 10.08 | 40.0 30.5 10.22 | 43.4 23.3 10.39 | 34.4 34.4 10.15 | 37.4 37.4 10.10 | 40.6 32.5 10.25
19 | 2 | COOLING CAPACITIES — SI (cont) | 5 | TC SHC kW | 26.7 26.7 10.20 | 31.5 30.9 10.42 | 36.2 26.0 10.64 | 40.2 20.7 10.85 | 30.8 30.8 10.40 | 34.5 34.5 10.59 | 38.3 29.9 10.76 | 42.0 22.9 10.96 | 33.0 33.0 10.49 | 36.0 36.0 10.65 | 39.1 31.9 10.82
19 | 2 | COOLING CAPACITIES — SI (cont) | 6 | TC SHC kW | 24.7 24.7 10.52 | 29.9 29.7 10.80 | 34.9 25.5 11.03 | 39.1 20.3 11.30 | 29.2 29.2 10.77 | 33.1 33.1 11.00 | 37.0 29.4 11.18 | 40.9 22.7 11.40 | 31.4 31.4 10.40 | 35.0 35.0 11.07 | 38.0 31.5 11.25
19 | 2 | COOLING CAPACITIES — SI (cont) | 7 | TC SHC kW | 21.1 21.1 11.10 | 26.8 26.8 11.40 | 32.3 24.4 11.71 | 37.1 19.7 12.00 | 26.9 26.9 11.42 | 30.8 30.8 11.64 | 34.7 28.3 11.88 | 38.8 22.1 12.13 | 30.5 30.5 11.64 | 53.1 33.1 11.79 | 35.8 30.6 11.96
19 | 2 | COOLING CAPACITIES — SI (cont) | 8 | TC SHC kW | 20.5 20.5 11.62 | 25.3 25.3 11.93 | 30.2 23.5 12.25 | 35.2 19.1 12.58 | 25.7 25.7 12.05 | 28.8 28.8 12.24 | 32.2 27.1 12.44 | 36.9 21.5 12.73 | 29.1 29.1 12.26 | 31.0 31.0 12.38 | 33.4 29.4 12.52
19 | 2 | COOLING CAPACITIES — SI (cont) | 9 | TC SHC kW | 20.4 20.4 12.15 | 24.1 24.1 12.45 | 27.9 27.9 12.78 | 33.2 33.2 13.17 | 24.5 24.5 12.68 | 26.9 26.9 12.84 | 29.6 25.8 13.00 | 34.9 21.0 13.33 | 27.7 27.7 12.88 | 29.0 29.0 12.97 | 30.8 28.1 13.10
19 | 2 | COOLING CAPACITIES — SI (cont) | 10 | TC SHC kW | 20.1 20.1 12.67 | 22.8 22.8 12.98 | 25.8 21.4 13.31 | 31.3 17.8 13.75 | 23.3 23.3 13.34 | 24.9 24.9 13.43 | 27.0 24.5 13.56 | 33.1 20.3 13.93 | 26.2 26.0 13.49 | 26.9 26.8 13.57 | 28.2 26.7 13.67
20 | 1 | Performance data (cont) | 1 | 1500/0.05 | 2000/0.17 13: 2000/0.07
20 | 2 | Performance data (cont) | 1 |  | 62 | 67 | 72 | 62 | 67 | 72 | 62 | 67
20 | 2 | Performance data (cont) | 2 | TC SHC kW | 60.0 50.5 4.44 | 66.0 42.6 4.57 | 72.1 34.5 4.71 | 63.0 58.2 4.52 | 69.2 48.5 4.66 | 76.1 38.3 4.84 | 65.2 64.3 4.58 | 71.5 54.0 4.74
20 | 2 | Performance data (cont) | 3 | TC SHC kW | 57.2 49.4 4.85 | 63.2 41.6 5.00 | 69.4 33.5 5.17 | 60.3 57.3 4.96 | 66.3 47.5 5.11 | 72.4 37.1 5.28 | 62.6 62.6 5.03 | 68.0 52.8 5.18
20 | 2 | Performance data (cont) | 4 | TC SHC kW | 54.4 48.1 5.25 | 60.2 40.4 5.43 | 66.3 32.4 5.62 | 57.1 55.6 5.35 | 62.9 46.4 5.54 | 69.4 36.2 5.75 | 60.0 60.0 5.47 | 64.7 52.0 5.62
20 | 2 | Performance data (cont) | 5 | TC SHC kW | 51.0 46.5 5.64 | 56.9 39.1 5.83 | 62.9 31.2 6.05 | 54.2 53.5 5.76 | 59.5 45.2 5.97 | 65.7 35.0 6.19 | 57.2 57.2 5.90 | 61.1 50.7 6.05
20 | 2 | Performance data (cont) | 6 | TC SHC kW | 47.6 45.0 6.02 | 53.7 37.8 6.24 | 59.5 30.0 6.48 | 51.4 51.3 6.17 | 56.0 44.0 6.39 | 62.0 33.8 6.63 | 54.4 54.4 6.33 | 57.4 49.4 6.48
20 | 2 | Performance data (cont) | 7 | TC SHC kW | 44.7 43.5 6.39 | 50.3 36.6 6.65 | 55.8 28.8 6.90 | 48.7 48.7 6.61 | 52.3 42.5 6.77 | 58.0 32.4 7.03 | 51.6 51.6 6.79 | 53.5 47.7 6.87
20 | 3 | Performance data (cont) | 1 | 1950/0.06 | 2000/0.07 62: 2400/0.075; 2000/0.07 67: 2500/0.075
20 | 4 | Performance data (cont) | 1 |  | 62 | 67 | 72 | 62 | 67 | 72 | 62 | 67 | 72 | 62 | 67
20 | 4 | Performance data (cont) | 2 | TC SHC kW | 71.9 56.3 5.47 | 80.1 46.6 5.73 | 88.3 55.1 6.02 | 74.9 62.3 5.60 | 83.0 50.5 5.86 | 90.9 57.0 6.14 | 75.3 63.6 5.64 | 83.6 51.2 5.90 | 91.3 60.4 6.14 | 77.4 69.1 5.74 | 85.2 55.3 6.00
20 | 4 | Performance data (cont) | 3 | TC SHC kW | 69.0 59.7 5.77 | 77.1 50.5 6.04 | 85.4 40.6 6.34 | 71.7 66.6 5.90 | 79.8 55.6 6.17 | 88.2 43.6 6.47 | 72.2 68.0 5.93 | 80.2 56.6 6.19 | 88.5 44.1 6.49 | 74.3 73.8 6.05 | 82.0 62.0 6.31
20 | 4 | Performance data (cont) | 4 | TC SHC kW | 64.9 57.9 6.32 | 72.7 48.8 6.61 | 80.8 39.1 6.54 | 67.4 64.6 6.45 | 75.2 54.0 6.75 | 83.5 42.1 6.60 | 67.8 65.8 6.48 | 75.6 55.1 6.76 | 83.8 42.7 6.69 | 70.7 70.5 6.60 | 77.1 60.2 6.86
20 | 4 | Performance data (cont) | 5 | TC SHC kW | 60.4 55.7 6.59 | 68.1 47.2 6.86 | 76.2 37.5 7.19 | 63.0 62.2 6.71 | 70.4 52.4 7.00 | 78.6 40.8 7.32 | 63.5 63.2 6.74 | 70.8 53.4 7.02 | 78.8 41.3 7.34 | 66.7 66.7 6.90 | 72.0 58.6 7.11
20 | 4 | Performance data (cont) | 6 | TC SHC kW | 55.9 53.2 6.99 | 63.4 45.4 7.26 | 71.1 35.9 7.58 | 59.0 59.0 7.13 | 65.4 50.6 7.39 | 73.2 39.0 7.71 | 59.7 59.7 7.17 | 65.6 51.6 7.41 | 73.5 39.6 7.72 | 62.5 62.7 7.34 | 66.8 56.8 7.49
20 | 4 | Performance data (cont) | 7 | TC SHC kW | 51.1 50.4 7.37 | 58.4 43.5 7.63 | 65.8 34.1 7.95 | 55.1 55.0 7.54 | 60.0 48.6 7.75 | 67.7 37.3 8.08 | 55.8 55.8 7.58 | 60.3 49.8 6.77 | 57.9 37.9 8.10 | 58.7 58.6 7.75 | 61.3 54.8 7.87
20 | 5 | Performance data (cont) | 1 | 2000/0.07 | 2400/0.075 62: 2500/.08; 2500/0.075 67: 3000/0.10
20 | 6 | Performance data (cont) | 1 |  | 62 | 67 | 72 | 62 | 67 | 72 | 62 | 67 | 72 | 62 | 67
20 | 6 | Performance data (cont) | 2 | TC SHC kW | 79.2 65.7 6.44 | 90.1 56.4 6.56 | 99.5 46.2 6.68 | 85.0 74.9 6.76 | 95.2 62.5 6.93 | 103.7 49.2 7.06 | 88.9 81.9 7.12 | 98.5 67.3 7.39 | 106.4 51.4 7.49 | 92.3 86.0 7.56 | 100.9 71.2 7.93
20 | 6 | Performance data (cont) | 3 | TC SHC kW | 74.6 63.7 6.85 | 85.8 54.8 7.06 | 96.0 44.9 7.21 | 79.4 72.2 7.25 | 90.6 60.8 7.46 | 100.2 48.1 7.59 | 84.4 78.9 7.59 | 94.3 66.0 7.90 | 103.0 50.5 8.04 | 88.3 83.9 8.01 | 96.7 70.3 8.45
20 | 6 | Performance data (cont) | 4 | TC SHC kW | 70.2 61.6 7.26 | 80.4 52.5 7.58 | 91.4 43.2 7.75 | 74.7 69.6 7.62 | 82.9 59.2 7.98 | 96.1 46.8 8.15 | 79.1 75.3 8.08 | 84.1 64.4 8.43 | 98.9 49.3 8.60 | 84.5 80.1 8.53 | 91.5 68.7 8.99
20 | 6 | Performance data (cont) | 5 | TC SHC kW | 65.5 59.3 7.64 | 75.6 50.5 8.05 | 86.8 41.6 8.28 | 70.4 55.4 8.03 | 79.9 56.7 8.50 | 91.0 45.0 8.69 | 75.1 72.2 8.50 | 83.0 61.8 8.98 | 93.9 47.7 9.16 | 79.3 75.0 9.07 | 85.9 67.0 9.48
20 | 6 | Performance data (cont) | 6 | TC SHC kW | 60.7 56.5 8.01 | 70.5 48.5 8.47 | 81.7 39.8 8.81 | 66.0 63.5 8.45 | 74.4 54.5 8.96 | 85.6 43.2 9.21 | 70.9 68.0 8.96 | 77.3 59.8 9.44 | 88.4 45.9 9.69 | 75.0 70.6 9.57 | 79.5 64.3 10.00
20 | 6 | Performance data (cont) | 7 | TC SHC kW | 45.4 53.6 8.43 | 65.1 46.3 8.90 | 75.7 37.5 9.35 | 61.8 60.0 8.88 | 68.7 52.4 9.39 | 79.9 41.3 9.77 | 66.6 63.7 9.43 | 71.3 57.6 9.88 | 82.6 44.0 10.26 | 70.6 66.2 10.06 | 73.3 61.9 10.41
21 | 1 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 2500/0.09 | 2500/.08 62: 3200/0.105; 3000/0.10 67: 3800/0.12
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 1 |  | 62 | 67 | 72 | 62 | 67 | 72 | 62 | 67 | 72 | 62 | 67
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 2 | TC SHC kW | 95.1 77.4 7.39 | 108.3 64.2 7.69 | 116.7 77.2 7.83 | 104.5 87.6 7.55 | 112.8 70.1 7.74 | 121.4 82.0 8.00 | 106.2 101.9 7.5 | 114.9 74.6 7.81 | 124.4 84.7 8.10 | 107.0 95.0 7.56 | 115.8 75.9 7.84
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 3 | TC SHC kW | 88.9 79.9 7.91 | 102.3 69.3 8.24 | 112.0 55.1 8.42 | 98.5 93.5 8.08 | 108.3 77.7 8.34 | 116.9 60.0 8.60 | 101.8 100.3 8.10 | 110.3 83.4 8.39 | 119.2 63.7 8.69 | 102.7 102.2 8.15 | 110.8 85.1 8.41
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 4 | TC SHC kW | 81.8 76.4 8.64 | 94.7 66.2 8.94 | 107.2 53.8 8.85 | 91.2 89.5 8.77 | 102.5 76.0 9.08 | 110.9 58.1 8.96 | 96.8 96.7 8.8 | 104.4 82.1 9.15 | 113.7 61.4 9.03 | 98.0 98.0 8.91 | 105.0 83.9 9.17
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 5 | TC SHC kW | 74.2 72.1 9.06 | 86.4 62.8 9.42 | 101.8 51.8 9.74 | 83.4 83.4 9.26 | 95.2 73.4 9.56 | 105.3 56.9 9.88 | 89.7 89.7 9.4 | 98.2 80.5 9.65 | 107.6 60.8 9.96 | 91.3 91.3 9.48 | 98.7 82.6 9.66
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 6 | TC SHC kW | 67.4 67.3 9.71 | 77.2 59.1 10.04 | 94.2 49.5 10.42 | 75.6 75.6 9.97 | 83.8 68.9 10.19 | 99.0 55.1 10.59 | 81.3 81.2 10.1 | 87.4 76.3 10.28 | 100.6 59.0 10.66 | 82.8 82.7 10.19 | 88.4 78.7 10.31
21 | 2 | COOLING CAPACITIES — ENGLISH (cont) | 7 | TC SHC kW | 63.2 63.2 10.37 | 69.2 56.0 10.68 | 84.4 46.0 11.09 | 68.5 68.5 10.69 | 71.8 64.3 10.85 | 88.8 51.9 11.27 | 73.1 73.0 10.9 | 75.0 70.9 10.95 | 92.3 56.9 11.37 | 74.2 74.2 10.93 | 76.0 73.0 10.97
21 | 3 | COOLING CAPACITIES — ENGLISH (cont) | 1 | 3150/0.13 | 3200/0.105 62: 4200/0.17
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 1 |  | 62 | 67 | 72 | 62 | 67 | 72 | 62 | 67
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 2 | TC SHC kW | 125.1 107.5 9.48 | 137.3 90.6 9.60 | 147.5 71.7 9.69 | 133.0 125.8 9.58 | 143.5 101.9 9.67 | 154.1 78.7 9.79 | 135.1 134.0 9.59 | 145.6 109.7 9.69
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 3 | TC SHC kW | 115.4 103.1 10.15 | 129.6 87.7 10.33 | 140.9 69.8 10.49 | 124.4 120.8 10.29 | 135.9 99.8 10.43 | 147.3 77.0 10.61 | 128.9 128.3 10.34 | 138.6 108.6 10.48
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 4 | TC SHC kW | 105.5 98.9 10.83 | 122.0 84.8 11.06 | 134.4 67.8 11.30 | 115.8 115.7 11.01 | 128.2 97.8 11.20 | 140.4 75.3 11.41 | 122.7 122.7 11.11 | 131.5 107.6 11.27
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 5 | TC SHC kW | 94.1 92.7 11.54 | 112.2 81.2 11.83 | 126.9 65.3 12.10 | 106.5 106.5 11.76 | 118.9 94.8 11.98 | 132.4 73.2 12.22 | 115.2 115.2 11.92 | 122.6 105.6 12.06
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 6 | TC SHC kW | 86.9 86.8 12.26 | 100.4 76.4 12.55 | 117.9 62.5 12.91 | 96.5 96.5 12.58 | 105.3 89.8 12.74 | 123.7 70.5 13.07 | 104.6 104.6 12.73 | 109.2 100.4 12.83
21 | 4 | COOLING CAPACITIES — ENGLISH (cont) | 7 | TC SHC kW | 79.9 79.9 13.00 | 88.5 71.7 13.29 | 108.8 59.6 13.72 | 86.4 86.3 13.40 | 91.7 84.8 13.49 | 115.0 67.8 13.91 | 94.1 99.1 13.55 | 96.0 94.6 13.62

## Fan_Performance
source_page | table_no | page_title | table_row | col_1 | col_2 | col_3 | col_4 | col_5 | col_6 | col_7 | col_8 | col_9 | col_10 | col_11 | col_12 | col_13 | col_14 | col_15 | col_16 | col_17 | col_18 | col_19 | col_20
22 | 1 | Performance data (cont) | 1 | col_1: 25; col_3: 50; col_5: 100; col_7: 150; col_9: 200; col_11: 250; col_13: 300; col_15: 350
22 | 1 | Performance data (cont) | 2 | R/s | kW | R/s | kW | R/s | kW | R/s | kW | R/s | kW | R/s | kW | R/s | kW | R/s | kW | R/s
22 | 1 | Performance data (cont) | 3 | 12.1 12.8 13.5 14.2 14.9 15.7 16.4 17.2 18.0 18.7 19.4 | 0.30 0.36 0.42 0.56 0.63 0.72 0.81 0.92 1.03 1.17 1.23 | 13.1 13.7 14.4 15.1 15.8 16.5 17.2 17.9 18.6 19.2 19.8 | 0.36 0.42 0.49 0.61 0.70 0.78 0.88 0.99 1.10 1.23 1.36 | 14.8 15.5 16.1 16.7 17.3 17.9 18.6 19.2 19.9 20.6 21.3 | 0.48 0.56 0.63 0.74 0.82 0.91 1.02 1.13 1.26 1.41 1.55 | 16.4 17.0 17.5 18.1 18.7 19.3 19.9 20.6 21.2 21.8 22.4 | 0.61 0.68 0.77 0.85 0.95 1.06 1.18 1.30 1.44 1.58 1.72 | 17.8 18.4 18.9 19.4 19.9 20.5 21.1 21.7 22.3 23.0 23.6 | 0.75 0.84 0.93 1.00 1.10 1.21 1.34 1.48 1.63 1.78 1.92 | 18.7 19.5 20.1 20.6 21.1 21.7 22.2 22.8 23.4 24.0 24.6 | 0.85 0.98 1.09 1.15 1.26 1.37 1.50 1.64 1.79 1.97 2.12 | 18.7 20.1 21.1 21.7 22.2 22.8 23.3 23.8 24.4 | 0.83 1.05 1.22 1.31 1.42 1.55 1.69 1.83 1.98 | 17.8 20.0 21.5 22.9 23.3 23.8 24.3 24.9 | 0.67 1.23 1.28 1.50 1.62 1.73 1.86 2.01 | 16.0 19.1 21.3 23.9 24.4 24.8 25.2
22 | 1 | Performance data (cont) | 4 | col_17: 25.7; col_18: 2.21
22 | 1 | Performance data (cont) | 5 | col_15: 25.4; col_16: 2.18; col_17: 26.3; col_18: 2.38
22 | 1 | Performance data (cont) | 6 | col_13: 24.9; col_14: 2.14; col_15: 25.9; col_16: 2.34; col_17: — —
22 | 1 | Performance data (cont) | 7 | col_13: 25.5; col_14: 2.29
22 | 2 | Performance data (cont) | 1 | col_1: 50; col_3: 100; col_5: 150; col_7: 200; col_9: 250; col_11: 300; col_13: 350; col_15: 400; col_17: 450
22 | 2 | Performance data (cont) | 2 | R/s | kW | R/s | kW | R/s | kW | R/s | kW | R/s | kW | R/s | kW | R/s | kW | R/s | kW | R/s | kW | R/s
22 | 2 | Performance data (cont) | 3 | 7.0 7.5 8.1 8.7 9.3 9.8 10.4 11.0 | 0.27 0.37 0.47 0.57 0.67 0.80 0.94 1.11 | 9.0 9.3 9.7 10.1 10.5 11.0 11.5 12.0 | 0.45 0.55 0.65 0.75 0.85 0.99 1.13 1.31 | 9.6 10.1 10.6 11.1 11.6 12.1 12.6 13.0 | 0.53 0.66 0.79 0.92 1.05 1.21 1.38 1.58 | 11.0 11.4 11.8 12.2 12.6 13.0 13.5 13.9 | 0.70 0.84 0.98 1.12 1.26 1.43 1.63 1.85 | 12.0 12.3 12.7 13.1 13.5 13.9 14.3 14.7 | 1.86 1.02 1.18 1.34 1.50 1.67 1.87 2.11 | 13.1 13.4 13.7 14.0 14.3 14.7 | 1.03 1.19 1.37 1.55 1.73 1.93 | 13.9 14.2 14.5 14.8 15.1 | 1.25 1.43 1.61 1.79 1.97 | 15.0 15.3 15.5 15.7 | 1.74 1.86 1.98 2.10 | 15.5 15.8 | 1.96 2.10 | 16.6 | 2.45
22 | 2 | Performance data (cont) | 4 | col_19: 16.8; col_20: 2.55
22 | 2 | Performance data (cont) | 5 | col_17: 16.1; col_18: 2.24; col_19: 17; col_20: 2.65
22 | 2 | Performance data (cont) | 6 | col_17: 16.4; col_18: 2.38; col_19: 17.2; col_20: 2.75
22 | 2 | Performance data (cont) | 7 | col_15: 15.9; col_16: 2.22; col_17: 16.7; col_18: 2.52; col_19: 17.4; col_20: 2.85
22 | 2 | Performance data (cont) | 8 | col_13: 15.5; col_14: 2.18; col_15: 16.2; col_16: 2.34; col_17: 16.9; col_18: 2.69; col_19: 17.6; col_20: 2.97
22 | 2 | Performance data (cont) | 9 | col_11: 15.1; col_12: 2.13; col_13: 15.9; col_14: 2.41; col_15: 16.6; col_16: 2.66; col_17: 17.3; col_18: 2.92; col_19: — —
22 | 2 | Performance data (cont) | 10 | col_11: 15.5; col_12: 2.36; col_13: 16.3; col_14: 2.64; col_15: 17; col_16: 2.91
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 1 | col_1: 50; col_3: 100; col_5: 150; col_7: 200; col_9: 250; col_11: 300; col_13: 350; col_15: 400; col_17: 450
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | R/s | kW | R/s | kW | R/s | kW | R/s | kW | R/s | kW | R/s | kW | R/s | kW | R/s | kW | R/s | kW | R/s
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 7.6 7.9 8.2 8.4 8.8 9.2 9.7 10.2 10.6 11.1 | 0.36 0.39 0.42 0.56 0.66 0.74 0.85 0.96 1.09 1.24 | 9.2 9.3 9.5 9.6 10.0 10.4 10.8 11.2 11.7 12.1 | 0.46 0.51 0.55 0.78 0.86 0.95 1.07 1.19 1.34 1.49 | 10.2 10.4 10.6 10.8 11.1 11.5 11.8 12.2 12.6 13.0 | 0.56 0.63 0.69 0.88 0.98 1.09 1.22 1.35 1.51 1.67 | 11.3 11.4 11.5 11.7 12.0 12.4 12.8 13.1 13.5 13.9 | 0.70 0.75 0.80 0.96 1.10 1.23 1.37 1.51 1.67 1.86 | 12.7 12.8 12.9 12.6 12.9 13.2 13.6 13.9 14.3 14.7 | 0.74 0.86 1.92 1.09 1.22 1.35 1.49 1.66 1.85 2.04 | 12.9 13.0 13.1 13.3 13.7 14.0 14.4 14.7 15.0 | 0.80 0.90 1.02 1.18 1.33 1.49 1.65 1.81 2.01 | 13.6 13.9 14.2 14.3 14.5 14.8 15.1 15.4 | 0.90 1.02 1.14 1.34 1.47 1.57 1.79 1.98 | 14.4 14.6 14.8 15.1 15.4 15.6 15.8 | 1.09 1.13 1.38 1.58 1.67 1.77 1.94 | 15.2 15.4 15.6 15.9 16.2 16.4 16.5 | 1.20 1.38 1.65 1.81 1.90 1.97 2.09 | 16.2 16.3 16.5 16.7 16.8
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 4 | col_19: 17.1; col_20: 2.21
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 5 | col_19: 17.3; col_20: 2.31
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 6 | col_15: 16.1; col_16: 2.13; col_17: 16.7; col_18: 2.29; col_19: 17.4; col_20: 2.46
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 7 | col_13: 15.7; col_14: 2.18; col_15: 16.4; col_16: 2.36; col_17: 17.1; col_18: 2.54; col_19: 17.7; col_20: 2.71
23 | 1 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 8 | col_11: 15.4; col_12: 2.23; col_13: 16.1; col_14: 2.4; col_15: 16.8; col_16: 2.59; col_17: 17.4; col_18: 2.8; col_19: 18; col_20: 2.99
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 1 | col_1: 50; col_3: 100; col_5: 150; col_7: 200; col_9: 250; col_11: 300; col_13: 350; col_15: 400; col_17: 450
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 2 | R/s | kW | R/s | kW | R/s | kW | R/s | kW | R/s | kW | R/s | kW | R/s | kW | R/s | kW | R/s | kW | R/s
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 3 | 9.7 9.9 10.2 10.4 10.7 10.9 11.1 11.4 11.6 11.9 12.1 12.4 12.6 12.8 13.1 13.3 13.6 13.8 | 0.66 0.72 0.78 0.85 0.91 1.07 1.12 1.19 1.26 1.34 1.42 1.51 1.60 1.70 1.79 1.91 2.01 2.13 | 10.8 11.0 11.2 11.5 11.7 11.9 12.1 12.4 12.6 12.8 13.0 13.2 13.5 13.7 13.9 14.2 14.4 14.6 | 0.84 0.89 0.95 1.01 1.08 1.22 1.29 1.36 1.45 1.53 1.62 1.71 1.81 1.92 2.02 2.14 2.26 2.38 | 11.7 11.9 12.1 12.4 12.6 12.8 13.0 13.2 13.4 13.7 13.9 14.1 14.3 14.5 14.7 15.0 15.2 15.4 | 0.91 1.01 1.10 1.20 1.29 1.37 1.45 1.54 1.62 1.71 1.80 1.89 2.00 2.12 2.22 2.34 2.47 2.60 | 12.6 12.8 13.0 13.2 13.4 13.6 13.8 14.0 14.2 14.4 14.6 14.8 15.0 15.3 15.5 15.7 15.9 16.1 | 1.09 1.15 1.22 1.29 1.38 1.52 1.60 1.69 1.78 1.88 1.99 2.09 2.21 2.33 2.45 2.57 2.69 2.82 | 13.5 13.7 13.8 14.0 14.2 14.4 14.6 14.7 14.9 15.1 15.3 15.5 15.7 15.9 16.1 16.4 16.6 16.8 | 1.27 1.34 1.41 1.48 1.55 1.67 1.75 1.84 1.93 2.03 2.15 2.26 2.39 2.51 2.64 2.77 2.92 3.07 | 14.3 14.5 14.6 14.8 15.0 15.1 15.3 15.5 15.6 15.8 16.0 16.2 16.4 16.6 16.8 17.0 17.2 17.4 | 1.32 1.46 1.58 1.67 1.76 1.86 1.95 2.03 2.12 2.22 2.32 2.42 2.54 2.68 2.82 2.97 3.12 3.26 | 15.1 15.2 15.4 15.5 15.7 15.8 16.0 16.2 16.3 16.5 16.7 16.9 17.0 17.2 17.4 17.6 17.8 | 1.44 1.38 1.71 1.76 1.92 2.02 2.12 2.22 2.33 2.44 2.54 2.64 2.76 2.88 3.01 3.14 3.30 | 16.0 16.1 16.2 16.3 16.4 16.5 16.7 16.8 17.0 17.2 17.3 17.5 17.7 17.8 18.0 | 1.55 1.71 1.79 1.89 2.01 2.20 2.29 2.40 2.52 2.64 2.76 2.88 3.01 3.14 3.25 | 16.9 17.0 17.0 17.1 17.1 17.2 17.3 17.5 17.7 17.8 18.0 18.1 18.3 | 1.66 1.79 1.92 2.06 2.18 2.36 2.47 2.59 2.71 2.83 2.96 3.09 3.23 | 17.5 17.5 17.6 17.6 17.7 17.7 17.9 18.1 18.3 18.4 18.6 17.7
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 4 | col_19: 18.9; col_20: 3.44
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 5 | col_17: 18.5; col_18: 3.36; col_19: 19.1; col_20: 3.59
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 6 | col_17: 18.6; col_18: 3.51; col_19: 19.2; col_20: 3.75
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 7 | col_15: 18.2; col_16: 3.39; col_17: 18.8; col_18: 3.65; col_19: 19.4; col_20: 3.9
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 8 | col_15: 18.4; col_16: 3.52; col_17: 19; col_18: 3.8; col_19: 19.5; col_20: 4.06
23 | 2 | FAN PERFORMANCE (SI) — VERTICAL DISCHARGE UNITS (cont) | 9 | col_13: 18; col_14: 3.47; col_15: 18.6; col_16: 3.67; col_17: 19.2; col_18: 3.93; col_19: 19.7; col_20: 4.22
24 | 1 | Performance data (cont) | 1 | col_1: 25; col_3: 50; col_5: 100; col_7: 150; col_9: 200; col_11: 250; col_13: 300; col_15: 350
24 | 1 | Performance data (cont) | 2 | R/s | kW | R/s | kW | R/s | kW | R/s | kW | R/s | kW | R/s | kW | R/s | kW | R/s | kW | R/s
24 | 1 | Performance data (cont) | 3 | 10.8 11.5 12.1 12.8 13.4 14.1 14.7 15.4 16.1 16.8 17.5 | 0.25 0.30 0.35 0.49 0.54 0.61 0.67 0.75 0.85 0.95 1.05 | 12.0 12.5 13.1 13.7 14.3 14.9 15.5 16.1 16.7 17.4 18.1 | 0.30 0.35 0.41 0.53 0.59 0.65 0.73 0.82 0.91 1.01 1.10 | 13.9 14.4 14.9 15.4 15.9 16.5 17.0 17.6 18.2 18.7 19.6 | 0.41 0.47 0.53 0.64 0.71 0.78 0.85 0.95 1.05 1.17 1.25 | 15.6 16.1 16.5 17.0 17.5 17.9 18.4 18.9 19.5 20.0 20.5 | 0.53 0.60 0.67 0.76 0.84 0.92 1.00 1.10 1.21 1.31 1.41 | 17.0 17.5 17.9 18.3 18.8 19.3 19.8 20.3 20.8 21.2 21.8 | 0.67 0.74 0.81 0.89 0.97 1.06 1.15 1.27 1.37 1.49 1.61 | 18.4 18.8 19.2 19.6 20.0 20.5 21.0 21.5 22.0 22.4 22.8 | 0.83 0.88 0.96 1.03 1.11 1.20 1.31 1.43 1.56 1.69 1.77 | 19.8 20.1 20.4 20.8 21.3 21.7 22.1 22.5 23.0 23.5 24.1 | 1.04 1.09 1.12 1.19 1.28 1.37 1.48 1.60 1.73 1.87 2.01 | 21.2 21.5 21.7 21.9 22.3 22.8 23.2 23.6 24.0 24.5 | 1.27 1.31 1.36 1.35 1.44 1.55 1.66 1.78 1.91 2.05 | 21.9 22.3 22.6 23.0 23.4 23.8 24.2 24.6 25.1
24 | 1 | Performance data (cont) | 4 | col_17: 25.5; col_18: 2.23
24 | 1 | Performance data (cont) | 5 | col_15: 25; col_16: 2.2; col_17: 26; col_18: 2.39
24 | 2 | Performance data (cont) | 1 | col_1: 50; col_3: 100; col_5: 150; col_7: 200; col_9: 250; col_11: 300; col_13: 350; col_15: 400; col_17: 450
24 | 2 | Performance data (cont) | 2 | R/s | kW | R/s | kW | R/s | kW | R/s | kW | R/s | kW | R/s | kW | R/s | kW | R/s | kW | R/s | kW | R/s
24 | 2 | Performance data (cont) | 3 | 6.5 7.1 7.5 7.9 8.3 8.8 9.2 9.7 | 0.29 0.36 0.43 0.50 0.57 0.66 0.76 0.88 | 8.2 8.6 9.0 9.4 9.8 10.2 10.6 11.0 | 0.35 0.45 0.55 0.65 0.75 0.85 0.97 1.10 | 9.4 9.8 10.2 10.6 11.0 11.3 11.7 12.1 | 0.53 0.62 0.73 0.84 0.95 1.06 1.19 1.34 | 10.8 11.1 11.4 11.7 12.0 12.4 12.7 13.0 | 0.71 0.81 0.92 1.03 1.14 1.29 1.45 1.60 | 11.9 12.1 12.4 12.7 13.0 13.3 13.7 14.0 | 0.86 0.95 1.09 1.23 1.37 1.52 1.69 1.88 | 12.7 13.0 13.3 13.6 13.9 14.2 14.5 | 1.10 1.23 1.36 1.49 1.62 1.77 1.93 | 13.3 13.6 13.9 14.4 14.8 15.0 | 1.31 1.45 1.59 1.73 1.87 2.04 | 13.3 13.7 14.1 14.9 | 1.55 1.70 1.85 2.00 | 13.5 13.9 14.3 | 1.80 1.95 2.11 | 13.8
24 | 2 | Performance data (cont) | 4 | col_19: 14.2; col_20: 2.19
24 | 2 | Performance data (cont) | 5 | col_19: 14.6; col_20: 2.35
24 | 2 | Performance data (cont) | 6 | col_17: 15.1; col_18: 2.27; col_19: 15; col_20: 2.53
24 | 2 | Performance data (cont) | 7 | col_15: 15.5; col_16: 2.15; col_17: 16; col_18: 2.43; col_19: 16.4; col_20: 2.71
24 | 2 | Performance data (cont) | 8 | col_15: 15.8; col_16: 2.32; col_17: 16.5; col_18: 2.6; col_19: 17.1; col_20: 2.88
24 | 2 | Performance data (cont) | 9 | col_13: 15.3; col_14: 2.21; col_15: 16.1; col_16: 2.5; col_17: 16.9; col_18: 2.78; col_19: — —
24 | 2 | Performance data (cont) | 10 | col_11: 14.8; col_12: 2.14; col_13: 15.6; col_14: 2.41; col_15: 16.4; col_16: 2.7
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | col_1: 50; col_3: 100; col_5: 150; col_7: 200; col_9: 250; col_11: 300; col_13: 350; col_15: 400; col_17: 450
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | R/s | kW | R/s | kW | R/s | kW | R/s | kW | R/s | kW | R/s | kW | R/s | kW | R/s | kW | R/s | kW | R/s
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 7.3 7.4 7.6 7.6 8.0 8.4 8.8 9.1 9.5 9.9 | 0.30 0.35 0.39 0.56 0.66 0.74 0.85 0.96 1.09 1.24 | 8.6 8.7 8.8 8.9 9.3 9.6 10.0 10.3 10.7 11.0 | 0.43 0.46 0.49 0.67 0.78 0.87 0.96 1.06 1.18 1.31 | 9.8 9.9 10.0 10.2 10.5 10.7 11.1 11.3 11.7 12.0 | 0.47 0.58 0.69 0.83 0.91 0.99 1.10 1.22 1.34 1.48 | 10.8 11.0 11.1 11.1 11.4 11.8 12.1 12.3 12.6 12.9 | 0.60 0.72 0.77 0.91 1.03 1.14 1.25 1.37 1.51 1.66 | 11.8 11.9 12.0 12.1 12.4 12.7 12.9 13.2 13.5 13.8 | 0.72 0.80 0.88 1.05 1.16 1.28 1.40 1.53 1.68 1.84 | 12.8 12.9 13.0 13.1 13.3 13.5 13.8 14.0 14.3 14.6 | 0.85 0.86 0.87 1.21 1.30 1.42 1.55 1.69 1.86 2.04 | 13.6 13.7 13.8 13.9 14.1 14.3 14.5 14.8 15.0 | 0.90 0.96 1.02 1.22 1.41 1.57 1.70 1.86 2.03 | 13.6 13.8 13.9 14.0 14.6 15.1 15.3 15.5 | 0.95 1.02 1.08 0.79 1.25 1.67 1.88 2.02 | 14.2 14.4 14.6 15.0 15.4 15.7 16.0 | 0.98 1.08 1.20 1.43 1.64 1.83 2.00 | 14.4 14.7 15.0 15.6 16.0 16.4 16.7
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 4 | col_17: 16.3; col_18: 2.23; col_19: 17; col_20: 2.36
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 5 | col_15: 15.8; col_16: 2.21; col_17: 16.4; col_18: 2.4; col_19: 17.2; col_20: 2.62
25 | 1 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 6 | col_13: 15.3; col_14: 2.21; col_15: 16; col_16: 2.42; col_17: 16.7; col_18: 2.61; col_19: 17.3; col_20: 2.82
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | col_1: 50; col_3: 100; col_5: 150; col_7: 200; col_9: 250; col_11: 300; col_13: 350; col_15: 400; col_17: 450
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | R/s | kW | R/s | kW R/s |  | kW | R/s | kW | R/s | kW | R/s | kW | R/s | kW | R/s | kW | R/s | kW | R/s
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 9.0 9.2 9.4 9.7 9.9 10.1 10.4 10.6 10.8 11.1 11.3 11.6 11.9 12.0 12.4 12.6 12.9 13.2 | 0.58 0.62 0.67 0.73 0.79 0.94 1.01 1.07 1.13 1.21 1.29 1.36 1.45 1.54 1.64 1.75 1.85 1.95 | 10.2 10.4 10.6 10.8 11.0 11.2 11.4 11.6 11.8 12.0 12.1 12.3 12.5 12.7 12.9 13.1 13.3 13.5 | 0.73 0.79 0.84 0.89 0.96 1.11 1.17 1.22 1.29 1.35 1.43 1.51 1.58 1.67 1.76 1.85 1.95 2.06 | 11.3 11.5 11.7 11.9 12.1 12.2 12.4 12.5 12.7 12.9 13.1 13.2 13.4 13.6 13.8 14.0 14.2 14.4 | 0.88 0.94 1.01 1.08 1.14 1.26 1.33 1.40 1.46 1.55 1.63 1.71 1.81 1.89 1.99 2.08 2.19 2.29 | 12.1 12.3 12.5 12.7 12.9 13.0 13.3 13.5 13.7 13.8 14.0 14.1 14.3 14.5 14.6 14.8 15.0 15.2 | 1.00 1.06 1.14 1.21 1.29 1.42 1.51 1.59 1.68 1.76 1.84 1.92 2.00 2.09 2.19 2.30 2.42 2.54 | 13.2 13.2 13.3 13.5 13.6 13.9 14.0 14.2 14.4 14.5 14.7 14.9 15.1 15.3 15.5 15.6 15.8 16.0 | 1.21 1.24 1.28 1.35 1.44 1.56 1.64 1.72 1.81 1.91 2.01 2.12 2.23 2.34 2.45 2.56 2.65 2.77 | 14.2 14.3 14.4 14.5 14.6 14.7 14.8 15.0 15.1 15.3 15.4 15.6 15.8 15.9 16.1 16.3 16.5 16.7 | 1.24 1.29 1.38 1.48 1.64 1.75 1.81 1.89 1.98 2.07 2.17 2.28 2.39 2.51 2.64 2.77 2.91 3.04 | 15.1 15.1 15.2 15.3 15.4 15.5 15.6 15.7 15.8 16.0 16.2 16.3 16.5 16.6 16.8 16.9 17.1 | 1.28 1.41 1.54 1.67 1.82 1.94 2.02 2.10 2.19 2.27 2.36 2.47 2.58 2.69 2.82 2.94 3.08 | 16.0 16.0 16.1 16.1 16.2 16.2 16.3 16.5 16.6 16.7 16.8 17.0 17.1 17.3 17.4 17.6 17.7 | 1.44 1.59 1.73 1.86 1.94 2.12 2.21 2.32 2.40 2.51 2.60 2.70 2.80 2.90 3.02 3.14 3.29 | 16.5 16.6 16.6 16.7 16.8 16.9 17.0 17.2 17.3 17.4 17.5 17.6 17.8 17.9 18.1 | 1.68 1.81 1.94 2.02 2.13 2.29 2.40 2.51 2.60 2.71 2.82 2.93 3.04 3.16 3.28 | 17.3 17.3 17.4 17.4 17.5 17.4 17.6 17.8 18.0 18.1 18.2 18.3 18.4
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 4 | col_19: 18.6; col_20: 3.41
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 5 | col_19: 18.7; col_20: 3.55
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 6 | col_17: 18.2; col_18: 3.4; col_19: 18.8; col_20: 3.67
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 7 | col_17: 18.4; col_18: 3.51; col_19: 19; col_20: 3.8
25 | 2 | FAN PERFORMANCE (SI) — HORIZONTAL DISCHARGE UNITS (cont) | 8 | col_13: 17.3; col_14: 3.23; col_15: 17.9; col_16: 3.44; col_17: 18.5; col_18: 3.65; col_19: 19.1; col_20: 3.92
26 | 1 | Performance data (cont) | 1 | col_1: 0.1; col_3: 0.2; col_5: 0.4; col_7: 0.6; col_9: 0.8; col_11: 1; col_13: 1.2; col_15: 1.4
26 | 1 | Performance data (cont) | 2 | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm | Watts
26 | 1 | Performance data (cont) | 3 | 731 772 814 852 894 936 978 1021 1064 1107 1150 | 304 359 424 562 630 708 795 891 998 1114 1241 | 789 826 865 905 945 984 1024 1064 1104 1145 1186 | 368 424 497 615 692 771 859 956 1064 1182 1318 | 895 930 964 1002 1037 1072 1108 1145 1183 1222 1262 | 488 562 636 739 818 899 998 1097 1216 1353 1491 | 990 1019 1050 1084 1119 1154 1190 1225 1260 1296 1331 | 617 691 774 859 948 1047 1156 1275 1396 1534 1674 | 1074 1105 1134 1163 1194 1226 1259 1294 1330 1365 1400 | 764 847 930 998 1089 1190 1310 1439 1578 1718 1875 | 1130 1174 1208 1235 1266 1297 1327 1359 1392 1426 1461 | 875 985 1096 1156 1250 1361 1473 1604 1744 1901 2067 | 1168 1213 1265 1303 1330 1362 1393 1423 1454 1485 | 921 1078 1234 1318 1413 1534 1656 1779 1927 2084 | 1250 1315 1348 1371 1396 1422 1452 1483 | 1059 1197 1455 1499 1604 1718 1840 1980 | 1345 1401 1421 1433 1460 1485 1510 | 1216 1335 1639 1638 1796 1910 2041
26 | 1 | Performance data (cont) | 4 | col_17: 1538; col_18: 2171
26 | 1 | Performance data (cont) | 5 | col_15: 1515; col_16: 2128; col_17: 1569; col_18: 2326
26 | 1 | Performance data (cont) | 6 | col_15: 1544; col_16: 2283; col_17: 1601; col_18: 2459
26 | 1 | Performance data (cont) | 7 | col_13: 1518; col_14: 2249; col_15: 1575; col_16: 2445
26 | 2 | Performance data (cont) | 1 | col_1: 0.2; col_3: 0.4; col_5: 0.6; col_7: 0.8; col_9: 1; col_11: 1.2; col_13: 1.4; col_15: 1.6; col_17: 1.8
26 | 2 | Performance data (cont) | 2 | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm
26 | 2 | Performance data (cont) | 3 | 466 473 488 503 511 518 534 549 557 565 581 597 613 629 646 662 679 696 712 | 429 448 486 524 539 562 607 653 684 708 763 827 891 965 1039 1123 1207 1301 1396 | 564 571 585 585 592 599 613 627 633 639 652 665 679 694 709 724 740 756 771 | 567 590 637 684 708 731 787 835 867 891 948 1014 1081 1156 1241 1335 1430 1534 1639 | 623 571 641 653 659 665 677 690 697 703 717 713 745 759 772 785 798 811 824 | 731 755 803 851 875 899 965 1031 1064 1097 1173 1250 1335 1413 1508 1595 1691 1788 1892 | 689 694 705 716 722 727 738 750 756 761 773 786 799 812 825 840 854 868 | 894 923 981 1039 1072 1097 1165 1233 1267 1301 1378 1473 1560 1665 1761 1866 1980 2093 | 745 750 761 772 778 783 794 805 811 816 827 839 850 862 875 | 1041 1079 1156 1233 1275 1310 1378 1456 1499 1543 1621 1709 1805 1901 2015 | 799 804 814 824 829 834 844 855 861 866 878 889 900 | 1250 1289 1368 1447 1491 1526 1604 1691 1735 1779 1875 1971 2067 | 861 864 871 878 884 885 892 902 908 913 | 1616 1638 1682 1727 1744 1770 1840 1927 1980 2023 | 922 924 929 934 937 939 944 | 1902 1928 1980 2032 2058 2084 2119 | 759 | 2219 | 1004 | 2640
26 | 2 | Performance data (cont) | 4 | col_17: 790; col_18: 2246; col_19: 1007; col_20: 2652
26 | 2 | Performance data (cont) | 5 | col_17: 853; col_18: 2283; col_19: 1013; col_20: 2677
26 | 2 | Performance data (cont) | 6 | col_17: 916; col_18: 2326; col_19: 1019; col_20: 2702
26 | 2 | Performance data (cont) | 7 | col_17: 947; col_18: 2343; col_19: 1022; col_20: 2710
26 | 2 | Performance data (cont) | 8 | col_17: 979; col_18: 2369; col_19: 1025; col_20: 2727
26 | 2 | Performance data (cont) | 9 | col_17: 987; col_18: 2428; col_19: 1039; col_20: 2791
26 | 2 | Performance data (cont) | 10 | col_15: 949; col_16: 2188; col_17: 1002; col_18: 2495; col_19: 1041; col_20: 2831
26 | 2 | Performance data (cont) | 11 | col_15: 953; col_16: 2232; col_17: 1003; col_18: 2521; col_19: 1045; col_20: 2854
26 | 2 | Performance data (cont) | 12 | col_15: 957; col_16: 2275; col_17: 1004; col_18: 2554; col_19: 1050; col_20: 2878
26 | 2 | Performance data (cont) | 13 | col_13: 924; col_14: 2128; col_15: 967; col_16: 2377; col_17: 1010; col_18: 2637; col_19: 1056; col_20: 2925
26 | 2 | Performance data (cont) | 14 | col_13: 935; col_14: 2223; col_15: 978; col_16: 2479; col_17: 1019; col_18: 2735; col_19: 1061; col_20: 3002
26 | 2 | Performance data (cont) | 15 | col_13: 946; col_14: 2335; col_15: 989; col_16: 2595; col_17: 1030; col_18: 2847; col_19: — — — — — — —
26 | 2 | Performance data (cont) | 16 | col_11: 911; col_12: 2171; col_13: 957; col_14: 2445; col_15: 1000; col_16: 2702; col_17: 1040; col_18: 2956
26 | 2 | Performance data (cont) | 17 | col_11: 923; col_12: 2275; col_13: 968; col_14: 2554; col_15: 1011; col_16: 2832; col_17: — — — — —; col_18: — — — — —
26 | 2 | Performance data (cont) | 18 | col_9: 887; col_10: 2128; col_11: 934; col_12: 2386; col_13: 980; col_14: 2661; col_15: 1022; col_16: 2933
26 | 2 | Performance data (cont) | 19 | col_9: 900; col_10: 2240; col_11: 946; col_12: 2504; col_13: 991; col_14: 2775; col_15: — — —; col_16: — — —
26 | 2 | Performance data (cont) | 20 | col_9: 914; col_10: 2369; col_11: 959; col_12: 2629; col_13: 1003; col_14: 2886
26 | 2 | Performance data (cont) | 21 | col_7: 881; col_8: 2206; col_9: 928; col_10: 2495; col_11: 971; col_12: 2759; col_13: 1014; col_14: 3009
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 1 | col_1: 0.2; col_3: 0.4; col_5: 0.6; col_7: 0.8; col_9: 1; col_11: 1.2; col_13: 1.4; col_15: 1.6; col_17: 1.8
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 471 483 495 508 521 532 544 557 570 583 596 609 622 635 649 662 675 689 | 369 404 449 485 530 630 677 716 763 818 867 924 989 1047 1123 1190 1267 1353 | 552 562 573 583 594 605 616 628 639 651 663 674 686 698 713 722 734 746 | 494 530 575 620 665 763 803 859 907 965 1031 1097 1165 1241 1318 1396 1482 1569 | 617 627 638 648 659 670 680 690 700 711 721 732 744 755 767 778 790 801 | 611 656 710 755 809 891 940 998 1064 1123 1190 1267 1335 1413 1491 1578 1674 1761 | 679 685 694 704 714 725 735 746 757 767 777 787 797 808 818 829 839 851 | 719 773 827 881 944 1014 1081 1148 1216 1284 1353 1430 1508 1595 1683 1779 1875 1971 | 740 754 757 759 766 778 787 796 805 815 826 836 847 857 867 878 888 | 818 881 944 1007 1070 1148 1216 1284 1353 1430 1517 1595 1691 1779 1866 1962 2058 | 757 765 775 791 807 825 835 844 854 863 871 880 890 901 912 | 881 944 1007 1070 1150 1275 1353 1430 1508 1587 1665 1753 1849 1945 2050 | 765 775 793 808 823 874 880 888 897 907 916 926 934 | 944 1025 1088 1186 1339 1422 1491 1569 1648 1744 1831 1927 2015 | 811 825 848 887 918 926 933 934 940 947 956 | 1034 1097 1240 1357 1519 1613 1656 1718 1853 1946 2039 | 889 907 929 954 963 974 983 988 989 991 | 1321 1429 1528 1690 1834 1920 1963 1980 2031 2099 | 946 959 975 987 999
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 4 | col_19: 1012; col_20: 2134
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 5 | col_19: 1017; col_20: 2177
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 6 | col_19: 1025; col_20: 2230
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 7 | col_19: 1032; col_20: 2282
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 8 | col_19: 1038; col_20: 2318
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 9 | col_17: 997; col_18: 2195; col_19: 1043; col_20: 2380
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 10 | col_15: 966; col_16: 2134; col_17: 1004; col_18: 2291; col_19: 1045; col_20: 2478
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 11 | col_15: 976; col_16: 2238; col_17: 1013; col_18: 2397; col_19: 1051; col_20: 2569
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 12 | col_13: 943; col_14: 2160; col_15: 985; col_16: 2344; col_17: 1023; col_18: 2514; col_19: 1059; col_20: 2688
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 13 | col_13: 952; col_14: 2265; col_15: 994; col_16: 2451; col_17: 1032; col_18: 2633; col_19: 1068; col_20: 2819
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 14 | col_11: 922; col_12: 2203; col_13: 962; col_14: 2371; col_15: 1003; col_16: 2560; col_17: 1042; col_18: 2763; col_19: 1078; col_20: 2952
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 15 | col_11: 933; col_12: 2309; col_13: 973; col_14: 2496; col_15: 1011; col_16: 2679; col_17: 1051; col_18: 2895; col_19: 1087; col_20: 3097
27 | 1 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 16 | [8 empty] | 898 | 2212 | 943 | 2424 | 983 | 2624 | 1021 | 2810 | 1060 | 3029 | 1090 | 3276
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 1 | col_1: 0.2; col_3: 0.4; col_5: 0.6; col_7: 0.8; col_9: 1; col_11: 1.2; col_13: 1.4; col_15: 1.6; col_17: 1.8
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 2 | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 3 | 570 584 598 612 626 640 654 668 683 697 711 726 741 755 770 784 799 814 829 843 858 | 623 676 728 781 873 913 1065 1129 1194 1267 1340 1423 1506 1598 1700 1794 1905 2009 2131 2246 2378 | 636 649 662 675 688 702 714 727 741 754 767 780 794 808 821 835 849 863 877 892 906 | 799 842 904 957 1018 1080 1218 1291 1365 1448 1531 1624 1717 1819 1923 2027 2140 2254 2378 2503 2629 | 693 705 717 729 741 754 767 780 793 806 819 832 845 858 871 884 897 910 923 937 950 | 886 948 1027 1115 1202 1290 1373 1456 1540 1624 1708 1802 1897 2000 2114 2219 2343 2468 2602 2746 2891 | 748 759 769 780 792 803 815 827 839 851 864 877 889 902 915 928 941 954 967 980 993 | 1044 1097 1158 1229 1299 1378 1514 1598 1691 1785 1879 1983 2096 2210 2325 2450 2566 2692 2828 2964 3111 | 800 809 819 829 840 851 861 873 884 895 907 919 931 943 955 968 981 993 1006 1019 | 1202 1281 1342 1414 1483 1553 1666 1751 1836 1931 2035 2149 2263 2387 2512 2638 2773 2919 3065 3221 | 850 858 867 876 886 896 906 916 927 938 949 960 971 983 995 1006 1018 1030 1043 | 1281 1352 1483 1589 1676 1755 1862 1948 2035 2123 2219 2316 2423 2548 2683 2828 2964 3111 3267 | 901 907 914 922 930 940 950 959 969 979 989 1000 1011 1022 1033 1044 1056 1067 | 1360 1457 1536 1606 1773 1913 2027 2123 2228 2334 2441 2548 2647 2764 2882 3010 3147 3304 | 950 960 963 968 975 983 991 1001 1010 1020 1029 1039 1049 1059 1070 1081 | 1474 1571 1668 1764 1826 1887 2202 2299 2405 2521 2638 2764 2882 3010 3138 3258 | 989 1001 1010 1018 1021 1026 1030 1040 1049 1059 1068 1077 1087 1097 | 1597 1703 1799 1940 2062 2212 2361 2476 2593 2710 2837 2955 3092 3230 | 1000 1006 1018 1022 1039 1051 1064 1075 1085 1095 1105 1114 1124
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 4 | col_19: 1133; col_20: 3442
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 5 | col_17: 1107; col_18: 3368; col_19: 1143; col_20: 3590
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 6 | col_17: 1117; col_18: 3516; col_19: 1152; col_20: 3748
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 7 | col_15: 1092; col_16: 3387; col_17: 1127; col_18: 3655; col_19: 1162; col_20: 3897
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 8 | col_15: 1103; col_16: 3525; col_17: 1138; col_18: 3804; col_19: 1172; col_20: 4055
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 9 | col_13: 1079; col_14: 3470; col_15: 1114; col_16: 3674; col_17: 1149; col_18: 3934; col_19: 1182; col_20: 4223
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 10 | col_11: 1055; col_12: 3424; col_13: 1091; col_14: 3637; col_15: 1126; col_16: 3822; col_17: 1160; col_18: 4083; col_19: 1193; col_20: 4382
27 | 2 | FAN PERFORMANCE (ENGLISH) — VERTICAL DISCHARGE UNITS (cont) | 11 | [8 empty] | 1032 | 3388 | 1068 | 3590 | 1103 | 3804 | 1137 | 4009 | 1171 | 4242 | 1204 | 4531
28 | 1 | Performance data (cont) | 1 | col_1: 0.1; col_3: 0.2; col_5: 0.4; col_7: 0.6; col_9: 0.8; col_11: 1; col_13: 1.2; col_15: 1.4
28 | 1 | Performance data (cont) | 2 | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm
28 | 1 | Performance data (cont) | 3 | 656 691 727 765 802 840 878 916 954 993 1031 | 258 304 350 487 539 600 669 739 827 916 1022 | 722 753 785 821 854 888 923 958 993 1029 1066 | 304 350 405 532 585 646 716 795 883 973 1081 | 840 867 895 923 953 984 1015 1046 1079 1112 1145 | 424 470 534 638 700 771 843 924 1022 1123 1241 | 939 965 991 1019 1046 1073 1101 1129 1160 1190 1220 | 543 608 672 843 835 907 981 1072 1173 1275 1396 | 1024 1050 1076 1099 1126 1154 1182 1209 1237 1264 1292 | 672 737 811 883 965 1047 1140 1241 1344 1447 1569 | 1106 1127 1151 1178 1201 1226 1252 1280 1309 1336 1363 | 829 884 958 1031 1106 1190 1292 1404 1517 1639 1770 | 1195 1207 1222 1249 1274 1297 1320 1345 1372 1400 1428 | 995 1078 1123 1182 1275 1361 1456 1569 1691 1823 1962 | 1269 1285 1301 1316 1338 1363 1388 1410 1434 1459 | 1179 1262 1354 1353 1439 1534 1639 1744 1866 1997 | 1347 1360 1370 1382 1402 1424 1448 1473 1496
28 | 1 | Performance data (cont) | 4 | col_17: 1519; col_18: 2188
28 | 1 | Performance data (cont) | 5 | col_15: 1486; col_16: 2145; col_17: 1543; col_18: 2335
28 | 2 | Performance data (cont) | 1 | col_1: 0.2; col_3: 0.4; col_5: 0.6; col_7: 0.8; col_9: 1; col_11: 1.2; col_13: 1.4; col_15: 1.6; col_17: 1.8
28 | 2 | Performance data (cont) | 2 | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm
28 | 2 | Performance data (cont) | 3 | 429 435 447 459 465 471 482 494 501 507 520 533 546 559 572 585 598 610 623 | 410 421 443 465 473 487 524 554 577 592 638 684 731 779 835 883 940 998 1056 | 424 429 439 549 554 559 569 581 587 592 604 615 626 637 648 660 671 682 694 | 538 553 584 615 630 646 684 723 747 771 827 875 932 989 1056 1114 1182 1258 1335 | 600 605 615 625 630 635 645 654 659 663 672 683 693 704 715 727 739 750 761 | 659 683 731 779 803 827 875 924 956 981 1031 1081 1140 1207 1275 1353 1439 1526 1613 | 671 675 683 691 695 699 708 717 722 727 737 747 756 765 775 785 795 806 817 | 843 867 916 965 989 1014 1064 1123 1156 1182 1250 1327 1396 1473 1543 1321 1691 1779 1866 | 736 739 746 753 757 760 768 776 780 784 793 802 813 823 832 841 851 860 | 1046 1071 1122 1173 1199 1224 1284 1344 1378 1404 1473 1552 1630 1718 1814 1901 1997 2084 | 778 783 794 805 810 816 824 832 836 839 846 855 863 872 882 | 1252 1282 1343 1404 1439 1465 1526 1587 1621 1656 1726 1805 1884 1962 2058 | 800 808 825 842 850 859 872 882 887 891 898 906 | 1501 1532 1594 1656 1691 1718 1779 1849 1884 1919 1997 2076 | 765 795 826 857 873 888 909 925 | 1735 1770 1840 1910 1945 1980 2050 2119 | 736 759 805 | 1945 1988 2075 | 666
28 | 2 | Performance data (cont) | 4 | col_19: 697; col_20: 2123
28 | 2 | Performance data (cont) | 5 | col_19: 760; col_20: 2250
28 | 2 | Performance data (cont) | 6 | col_17: 851; col_18: 2162; col_19: 823; col_20: 2377
28 | 2 | Performance data (cont) | 7 | col_17: 863; col_18: 2206; col_19: 855; col_20: 2445
28 | 2 | Performance data (cont) | 8 | col_17: 897; col_18: 2249; col_19: 887; col_20: 2504
28 | 2 | Performance data (cont) | 9 | col_17: 931; col_18: 2326; col_19: 935; col_20: 2595
28 | 2 | Performance data (cont) | 10 | col_17: 955; col_18: 2394; col_19: 972; col_20: 2678
28 | 2 | Performance data (cont) | 11 | col_15: 931; col_16: 2162; col_17: 964; col_18: 2436; col_19: 986; col_20: 2718
28 | 2 | Performance data (cont) | 12 | col_15: 936; col_16: 2197; col_17: 973; col_18: 2479; col_19: 999; col_20: 2759
28 | 2 | Performance data (cont) | 13 | col_15: 946; col_16: 2275; col_17: 987; col_18: 2554; col_19: 1019; col_20: 2839
28 | 2 | Performance data (cont) | 14 | col_15: 954; col_16: 2352; col_17: 997; col_18: 2637; col_19: 1034; col_20: 2917
28 | 2 | Performance data (cont) | 15 | col_13: 913; col_14: 2154; col_15: 961; col_16: 2436; col_17: 1006; col_18: 2727; col_19: — — — — — — —
28 | 2 | Performance data (cont) | 16 | col_13: 921; col_14: 2240; col_15: 969; col_16: 2529; col_17: 1014; col_18: 2807
28 | 2 | Performance data (cont) | 17 | col_13: 930; col_14: 2335; col_15: 976; col_16: 2620; col_17: 1021; col_18: 2902
28 | 2 | Performance data (cont) | 18 | col_11: 892; col_12: 2162; col_13: 939; col_14: 2428; col_15: 984; col_16: 2710; col_17: — — — —; col_18: — — — —
28 | 2 | Performance data (cont) | 19 | col_11: 902; col_12: 2266; col_13: 948; col_14: 2529; col_15: 993; col_16: 2799
28 | 2 | Performance data (cont) | 20 | col_11: 912; col_12: 2369; col_13: 958; col_14: 2637; col_15: 1002; col_16: 2902
28 | 2 | Performance data (cont) | 21 | col_9: 870; col_10: 2180; col_11: 921; col_12: 2479; col_13: 968; col_14: 2751
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | col_1: 0.2; col_3: 0.4; col_5: 0.6; col_7: 0.8; col_9: 1; col_11: 1.2; col_13: 1.4; col_15: 1.6; col_17: 1.8
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 437 448 460 471 483 484 495 505 516 527 537 548 560 571 582 593 605 616 | 333 369 404 449 494 562 607 646 692 739 795 851 916 981 1047 1123 1207 1292 | 517 526 534 544 553 560 570 579 589 599 609 619 629 639 649 659 670 680 | 440 476 512 557 593 677 723 763 810 859 907 956 1014 1072 1140 1207 1284 1361 | 590 597 605 613 620 631 638 646 655 664 672 680 688 698 708 717 727 737 | 566 602 638 683 728 810 851 899 956 1006 1064 1114 1173 1241 1310 1387 1465 1543 | 653 660 668 675 682 690 699 708 717 724 731 738 747 756 764 773 781 789 | 692 746 791 361 881 940 998 1047 1106 1165 1216 1275 1344 1422 1499 1578 1648 1726 | 712 717 723 730 738 747 755 761 767 775 784 794 802 810 816 823 832 841 | 755 836 908 971 1034 1081 1140 1199 1250 1318 1387 1456 1534 1604 1674 1753 1840 1927 | 770 778 779 783 789 800 805 812 819 827 833 840 847 856 865 875 883 | 827 881 944 1052 1150 1233 1284 1344 1413 1482 1552 1621 1700 1788 1875 1962 2050 | 805 815 825 830 840 850 857 862 867 873 880 888 895 901 908 | 881 926 980 1070 1159 1353 1447 1517 1578 1639 1718 1805 1884 1971 2050 | 811 822 835 843 860 879 896 908 915 920 926 931 938 | 944 989 1052 1150 1195 1233 1473 1639 1753 1831 1901 1971 2108 | 830 843 855 868 880 925 935 944 952 963 | 998 1079 1186 1303 1429 1604 1709 1836 1920 2005 | 883 898 910 924 942 964 975 984 993 1001
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 4 | col_17: 970; col_18: 2134; col_19: 1007; col_20: 2221
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 5 | col_17: 976; col_18: 2230; col_19: 1017; col_20: 2362
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 6 | col_17: 981; col_18: 2309; col_19: 1024; col_20: 2496
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 7 | col_15: 945; col_16: 2203; col_17: 986; col_18: 2389; col_19: 1029; col_20: 2605
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 8 | col_15: 953; col_16: 2300; col_17: 993; col_18: 2478; col_19: 1034; col_20: 2707
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 9 | col_13: 915; col_14: 2186; col_15: 960; col_16: 2389; col_17: 1000; col_18: 2587; col_19: 1039; col_20: 2800
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 10 | col_13: 924; col_14: 2291; col_15: 966; col_16: 2487; col_17: 1008; col_18: 2698; col_19: 1046; col_20: 2904
29 | 1 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 11 | col_11: 889; col_12: 2177; col_13: 934; col_14: 2389; col_15: 972; col_16: 2587; col_17: 1015; col_18: 2819; col_19: 1053; col_20: 3029
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 1 | col_1: 0.2; col_3: 0.4; col_5: 0.6; col_7: 0.8; col_9: 1; col_11: 1.2; col_13: 1.4; col_15: 1.6; col_17: 1.8
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 2 | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm | Watts | Rpm
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 3 | 529 541 553 566 579 593 607 621 636 650 665 680 696 711 727 742 758 773 789 805 821 | 535 579 632 685 737 790 947 1010 1073 1137 1210 1283 1365 1456 1540 1641 1742 1845 1958 2070 2202 | 605 615 626 636 647 659 670 681 693 705 717 728 739 750 762 774 786 799 812 826 840 | 693 746 790 843 904 957 1113 1170 1226 1291 1357 1431 1506 1582 1666 1759 1854 1948 2053 2166 2290 | 669 680 692 702 713 722 732 742 751 761 772 783 794 805 817 828 840 852 863 875 887 | 834 886 948 1018 1080 1141 1267 1332 1398 1464 1548 1632 1717 1811 1897 1992 2088 2193 2290 2405 2521 | 719 729 740 751 763 775 782 795 808 819 830 839 848 857 867 877 888 899 910 921 932 | 948 1009 1071 1141 1220 1290 1423 1506 1590 1674 1759 1836 1914 2000 2096 2193 2307 2423 2548 2665 2792 | 775 791 792 798 807 817 833 842 851 861 871 883 896 908 919 929 938 947 957 966 976 | 1158 1211 1237 1290 1352 1431 1565 1641 1725 1811 1905 2009 2123 2237 2343 2450 2557 2656 2773 2891 3019 | 815 827 832 845 856 867 879 889 898 908 917 925 935 945 955 967 980 992 1003 1014 | 1308 1369 1413 1510 1589 1624 1751 1819 1897 1974 2070 9175 2281 2387 2512 2638 2773 9910 3047 3184 | 880 889 895 903 911 920 927 934 942 950 960 969 979 988 996 1005 1015 1025 1036 | 1352 1448 1571 1668 1747 1799 1940 2018 2105 2193 2272 2370 2468 2575 2692 2819 2946 3083 3230 | 911 920 929 940 952 965 973 980 987 994 1001 1009 1018 1028 1037 1046 1056 1064 | 1606 1676 1755 1826 1887 2010 2123 2210 2307 2405 2503 2602 2701 2801 2901 3019 3147 3285 | 940 951 965 980 989 1000 1013 1022 1030 1037 1045 1051 1058 1066 1074 1084 | 1685 1747 1843 1940 2054 2150 2290 2396 2503 2602 2710 2828 2937 3047 3166 3276 | 971 985 999 1010 1021 1035 1046 1058 1068 1077 1085 1092 1100 1106
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 4 | col_19: 1113; col_20: 3414
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 5 | col_19: 1121; col_20: 3544
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 6 | col_17: 1093; col_18: 3396; col_19: 1129; col_20: 3674
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 7 | col_17: 1103; col_18: 3516; col_19: 1137; col_20: 3795
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 8 | col_15: 1073; col_16: 3433; col_17: 1112; col_18: 3655; col_19: 1147; col_20: 3925
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 9 | col_13: 1049; col_14: 3396; col_15: 1083; col_16: 3590; col_17: 1121; col_18: 3804; col_19: 1157; col_20: 4055
29 | 2 | FAN PERFORMANCE (ENGLISH) — HORIZONTAL DISCHARGE UNITS (cont) | 10 | col_11: 1024; col_12: 3322; col_13: 1061; col_14: 3553; col_15: 1093; col_16: 3748; col_17: 1129; col_18: 3962; col_19: 1166; col_20: 4204

## Static_Pressure_Accessories
source_page | table_no | page_title | table_row | col_1 | col_2 | col_3 | col_4 | col_5 | col_6 | col_7 | col_8 | col_9 | col_10 | col_11 | col_12 | col_13 | col_14 | col_15 | col_16 | col_17 | col_18 | col_19 | col_20
33 | 1 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 1 | col_1: 700; col_2: 800; col_3: 900; col_4: 1000; col_5: 1100
33 | 1 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 2 | col_1: 20; col_2: 22; col_3: 25; col_4: 27; col_5: 30
33 | 1 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 3 | col_1: 41; col_2: 42; col_3: 42; col_4: 43; col_5: 44
33 | 1 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4 | col_1: 12; col_2: 12; col_3: 12; col_4: 12; col_5: 12
33 | 1 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 5 | col_1: 32; col_2: 40; col_3: 50; col_4: 63; col_5: 77
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 1 | 800 | 900 | 1000 | 1100 | 1200 | 1300 | 1400 | 1500 | 1600 | 1700 | 1800 | 1900 | 2000 | 2100 | 2200 | 2300
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 2 | 1 | 2 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 19 | 21 | 23 | 25 | 27 | 29
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 3 | 5 | 7 | 9 | 10 | 12 | 15 | 17 | 20 | 22 | 25 | 27 | 29 | 32 | 34 | 37 | 39
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
33 | 2 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 5 | [6 empty] | 31 | 35 | 41 | 50 | 59 | 67 | 75 | 84 | 90 | 97
33 | 3 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4: 1; 2: 1500; 3: 1600; 4: 1800; 5: 2000; 6: 2200; 7: 2400
33 | 3 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4: 2; 2: 0.09; 3: 0.09; 4: 0.1; 5: 0.11; 6: 0.11; 7: 0.12
33 | 3 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4: 3; 2: 0.16; 3: 0.16; 4: 0.17; 5: 0.17; 6: 0.17; 7: 0.18
33 | 3 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4: 4; 2: 0.05; 3: 0.05; 4: 0.05; 5: 0.05; 6: 0.05; 7: 0.05
33 | 3 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4: 5; 2: 0.13; 3: 0.15; 4: 0.19; 5: 0.24; 6: 0.29; 7: 0.35
33 | 4 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4: 1; 2: 1900; 3: 2200; 4: 2500; 5: 3000; 6: 3500; 7: 4000; 8: 4500; 9: 5000
33 | 4 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4: 2; 2: 0.01; 3: 0.02; 4: 0.03; 5: 0.05; 6: 0.07; 7: 0.08; 8: 0.1; 9: 0.12
33 | 4 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4: 3; 2: 0.02; 3: 0.03; 4: 0.05; 5: 0.07; 6: 0.09; 7: 0.12; 8: 0.14; 9: 0.16
33 | 4 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4: 4; 2: 0.02; 3: 0.02; 4: 0.02; 5: 0.03; 6: 0.04; 7: 0.05; 8: 0.06; 9: 0.07
33 | 4 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4: 5; 5: 0.125; 6: 0.18; 7: 0.27; 8: 0.34; 9: 0.4
33 | 5 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4: 1; 2: UNIT ELECTRICAL CHARACTERISTICS; 3: ACCESSORY kW
33 | 5 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4: 2; 2: 400-3-50; 3: 4.2 8.0 9.7 16.0* 17.7*
33 | 5 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4: 3; 2: 400-3-50; 3: 9.7 11.5 19.3 22.9 29.0*
33 | 5 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4: 4; 2: 400-3-50; 3: 9.7 11.5 19.3 22.9 29.0*
33 | 5 | ACCESSORY/FIOP STATIC PRESSURE DROP (Pa) — 50TFF007 | 4: 5; 2: 400-3-50; 3: 9.7† 11.5** 19.3 22.9 29.0 34.7*

## Fan_Motor_Performance
source_page | table_no | page_title | table_row | col_1 | col_2 | col_3 | col_4 | col_5 | col_6 | col_7 | col_8 | col_9 | col_10 | col_11 | col_12 | col_13 | col_14 | col_15 | col_16 | col_17 | col_18 | col_19 | col_20
30 | 1 | Performance data (cont) | 1 | col_1: UNIT RATED VOLTAGE; col_2: MAXIMUM ACCEPTABLE CONTINUOUS BkW*; col_3: MAXIMUM ACCEPTABLE CONTINUOUS BHP*; col_4: MAXIMUM ACCEPTABLE OPERATING WATTS
30 | 1 | Performance data (cont) | 2 | col_1: 400; col_2: 1.79; col_3: 2.4; col_4: 2120
30 | 1 | Performance data (cont) | 3 | col_1: 400; col_2: 1.79; col_3: 2.4; col_4: 2120
30 | 1 | Performance data (cont) | 4 | col_1: 400; col_2: 1.79; col_3: 2.4; col_4: 2120
30 | 1 | Performance data (cont) | 5 | col_1: 400; col_2: 1.79; col_3: 2.4; col_4: 2120
30 | 1 | Performance data (cont) | 6 | col_1: 400; col_2: 2.76; col_3: 3.7; col_4: 3313
30 | 2 | Performance data (cont) | 1 | col_1: 0; col_2: 1/2; col_3: 1; col_4: 11/2; col_5: 2; col_6: 21/2; col_7: 3; col_8: 31/2; col_9: 4; col_10: 41/2
30 | 2 | Performance data (cont) | 2 | col_1: 20.08; col_2: 19.67; col_3: 19.17; col_4: 18.75; col_5: 18.25; col_6: 17.83; col_7: 17.33; col_8: 16.92; col_9: 16.42; col_10: 16
30 | 2 | Performance data (cont) | 3 | col_1: 14.67; col_2: 14.25; col_3: 13.83; col_4: 13.33; col_5: 12.92; col_6: 12.5; col_7: 12.08; col_8: 11.67; col_9: 11.25; col_10: 10.83
30 | 2 | Performance data (cont) | 4 | col_1: 15; col_2: 14.58; col_3: 14.25; col_4: 13.92; col_5: 13.58; col_6: 13.25; col_7: 12.92; col_8: 12.58; col_9: 12.25; col_10: 11.92
30 | 2 | Performance data (cont) | 5 | col_1: 14.83; col_2: 14.58; col_3: 14.25; col_4: 13.72; col_5: 13.67; col_6: 13.33; col_7: 13.08; col_8: 12.75; col_9: 12.5; col_10: 12.17
30 | 3 | Performance data (cont) | 1 | col_1: 0; col_2: 1/2; col_3: 1; col_4: 11/2; col_5: 2; col_6: 21/2; col_7: 3; col_8: 31/2; col_9: 4; col_10: 41/2
30 | 3 | Performance data (cont) | 2 | col_1: 1205; col_2: 1180; col_3: 1150; col_4: 1125; col_5: 1095; col_6: 1070; col_7: 1040; col_8: 1015; col_9: 985; col_10: 960
30 | 3 | Performance data (cont) | 3 | col_1: 880; col_2: 855; col_3: 830; col_4: 800; col_5: 775; col_6: 750; col_7: 725; col_8: 700; col_9: 675; col_10: 650
30 | 3 | Performance data (cont) | 4 | col_1: 900; col_2: 875; col_3: 855; col_4: 835; col_5: 815; col_6: 795; col_7: 775; col_8: 755; col_9: 735; col_10: 715
30 | 3 | Performance data (cont) | 5 | col_1: 890; col_2: 875; col_3: 855; col_4: 835; col_5: 820; col_6: 800; col_7: 785; col_8: 765; col_9: 750; col_10: 730

## Heater_Ratings
model | heater_option_nominal_kw | heater_fla_a | mca_a | mocp_a | nominal_voltage_v | min_voltage_v | max_voltage_v | source_page
50TFF007 |  |  | 18.4 | 25 | 400 | 360 | 440 | 34
50TFF007 | 4.2 | 7.2 | 18.4 | 25 | 400 | 360 | 440 | 34
50TFF007 | 8 | 13.8 | 18.4 | 25 | 400 | 360 | 440 | 34
50TFF007 | 9.7 | 16.8 | 20.8 | 25 | 400 | 360 | 440 | 34
50TFF007 | 16 | 27.8 | 32.1 | 35 | 400 | 360 | 440 | 34
50TFF007 | 17.7 | 30.7 | 34.6 | 35 | 400 | 360 | 440 | 34
50TFF008 |  |  | 23.8 | 30 | 400 | 360 | 440 | 34
50TFF008 | 9.7 | 13.9 | 23.8 | 30 | 400 | 360 | 440 | 34
50TFF008 | 11.5 | 16.5 | 23.9 | 25 | 400 | 360 | 440 | 34
50TFF008 | 19.3 | 27.8 | 38.1 | 40 | 400 | 360 | 440 | 34
50TFF008 | 22.9 | 33.1 | 44.6 | 45 | 400 | 360 | 440 | 34
50TFF008 | 29 | 41.8 | 55.5 | 60 | 400 | 360 | 440 | 34
50TFF009 |  |  | 22.5 | 25 | 400 | 360 | 440 | 34
50TFF009 | 9.7 | 13.9 | 22.5 | 25 | 400 | 360 | 440 | 34
50TFF009 | 11.5 | 16.5 | 23.9 | 25 | 400 | 360 | 440 | 34
50TFF009 | 19.3 | 27.8 | 38.1 | 40 | 400 | 360 | 440 | 34
50TFF009 | 22.9 | 33.1 | 44.6 | 45 | 400 | 360 | 440 | 34
50TFF009 | 29 | 41.8 | 55.5 | 60 | 400 | 360 | 440 | 34
50TFF012 |  |  | 23.8 | 30 | 400 | 360 | 440 | 34
50TFF012 | 9.7 | 16.5 | 23.9 | 30 | 400 | 360 | 440 | 34
50TFF012 | 19.3 | 27.8 | 38.1 | 40 | 400 | 360 | 440 | 34
50TFF012 | 22.9 | 33.1 | 44.6 | 45 | 400 | 360 | 440 | 34
50TFF012 | 29 | 41.8 | 55.5 | 60 | 400 | 360 | 440 | 34
50TFF012 | 34.7 | 50.1 | 65.9 | 70†† | 400 | 360 | 440 | 34
50TFF014 |  |  | 29.4 | 35 | 400 | 360 | 440 | 34
50TFF014 | 11.5 | 16.5 | 29.4 | 35 | 400 | 360 | 440 | 34
50TFF014 | 19.3 | 27.8 | 40.8 | 45 | 400 | 360 | 440 | 34
50TFF014 | 22.9 | 33.1 | 47.3 | 50 | 400 | 360 | 440 | 34
50TFF014 | 29 | 41.8 | 58.2 | 60 | 400 | 360 | 440 | 34
50TFF014 | 34.7 | 50.1 | 68.6 | 70†† | 400 | 360 | 440 | 34

## Electric_Heating_Capacities
model | electric_heat_kw | heater_fla_a | mca_a | mocp_a | nominal_voltage_v | power_supply | source_page
50TFF007 |  |  | 18.4 | 25 | 400 | 400 V / 3 phase / 50 Hz | 34
50TFF007 | 4.2 | 7.2 | 18.4 | 25 | 400 | 400 V / 3 phase / 50 Hz | 34
50TFF007 | 8 | 13.8 | 18.4 | 25 | 400 | 400 V / 3 phase / 50 Hz | 34
50TFF007 | 9.7 | 16.8 | 20.8 | 25 | 400 | 400 V / 3 phase / 50 Hz | 34
50TFF007 | 16 | 27.8 | 32.1 | 35 | 400 | 400 V / 3 phase / 50 Hz | 34
50TFF007 | 17.7 | 30.7 | 34.6 | 35 | 400 | 400 V / 3 phase / 50 Hz | 34
50TFF008 |  |  | 23.8 | 30 | 400 | 400 V / 3 phase / 50 Hz | 34
50TFF008 | 9.7 | 13.9 | 23.8 | 30 | 400 | 400 V / 3 phase / 50 Hz | 34
50TFF008 | 11.5 | 16.5 | 23.9 | 25 | 400 | 400 V / 3 phase / 50 Hz | 34
50TFF008 | 19.3 | 27.8 | 38.1 | 40 | 400 | 400 V / 3 phase / 50 Hz | 34
50TFF008 | 22.9 | 33.1 | 44.6 | 45 | 400 | 400 V / 3 phase / 50 Hz | 34
50TFF008 | 29 | 41.8 | 55.5 | 60 | 400 | 400 V / 3 phase / 50 Hz | 34
50TFF009 |  |  | 22.5 | 25 | 400 | 400 V / 3 phase / 50 Hz | 34
50TFF009 | 9.7 | 13.9 | 22.5 | 25 | 400 | 400 V / 3 phase / 50 Hz | 34
50TFF009 | 11.5 | 16.5 | 23.9 | 25 | 400 | 400 V / 3 phase / 50 Hz | 34
50TFF009 | 19.3 | 27.8 | 38.1 | 40 | 400 | 400 V / 3 phase / 50 Hz | 34
50TFF009 | 22.9 | 33.1 | 44.6 | 45 | 400 | 400 V / 3 phase / 50 Hz | 34
50TFF009 | 29 | 41.8 | 55.5 | 60 | 400 | 400 V / 3 phase / 50 Hz | 34
50TFF012 |  |  | 23.8 | 30 | 400 | 400 V / 3 phase / 50 Hz | 34
50TFF012 | 9.7 | 16.5 | 23.9 | 30 | 400 | 400 V / 3 phase / 50 Hz | 34
50TFF012 | 19.3 | 27.8 | 38.1 | 40 | 400 | 400 V / 3 phase / 50 Hz | 34
50TFF012 | 22.9 | 33.1 | 44.6 | 45 | 400 | 400 V / 3 phase / 50 Hz | 34
50TFF012 | 29 | 41.8 | 55.5 | 60 | 400 | 400 V / 3 phase / 50 Hz | 34
50TFF012 | 34.7 | 50.1 | 65.9 | 70†† | 400 | 400 V / 3 phase / 50 Hz | 34
50TFF014 |  |  | 29.4 | 35 | 400 | 400 V / 3 phase / 50 Hz | 34
50TFF014 | 11.5 | 16.5 | 29.4 | 35 | 400 | 400 V / 3 phase / 50 Hz | 34
50TFF014 | 19.3 | 27.8 | 40.8 | 45 | 400 | 400 V / 3 phase / 50 Hz | 34
50TFF014 | 22.9 | 33.1 | 47.3 | 50 | 400 | 400 V / 3 phase / 50 Hz | 34
50TFF014 | 29 | 41.8 | 58.2 | 60 | 400 | 400 V / 3 phase / 50 Hz | 34
50TFF014 | 34.7 | 50.1 | 68.6 | 70†† | 400 | 400 V / 3 phase / 50 Hz | 34

## Dimensions_Accessories
source_page | source_line | dimension_or_note
11 | 1 | Accessory dimensions
11 | 2 | A R C O C O E F S C S U O R R B Y “A” UN 5 I 0 T T S F I F ZE B C ALT DRA D IN HOLE G “E A ” S PO “ W F” ER CON “G TR ” OL C P O K N G N . E A C C T C O Y R .
11 | 3 | C C R R R R F F C C U U R R B B 0 0 0 0 1 2 A A 0 0 0 0 1 2 ¢ ¢ - - 2 0 † † [ [ 3 6 5 1 6 0 ] ] 007 [19 3 ] / 4 N † PT 3 1 /4 1 † / 4 [1 † 9 [3 ] 1 N . P 7] T [1 1 2 /2 . † 7] C C R R B B T T M M P P W W R R 0 0 0 0 2 1 A A 0 0 0 0
11 | 4 | NPT
11 | 5 | 1¢- [ 9 5 1 5 1 1 /1 ] 6 † [ 1 4 ¢ 0 -4 6 † ] [ 1 4 3 4 / . 4 5 † ]
11 | 6 | [12.
11 | 7 | 1
11 | 8 | 7
11 | 9 | /
11 | 10 | ]
11 | 11 | 2 †
11 | 12 | NPT
11 | 13 | 3/4 † [19] NPT
11 | 14 | 1/2 †
11 | 15 | CRBTMPWR003A00
11 | 16 | 3/4 † 11/4 † [31.7] [12.7]
11 | 17 | CRBTMPWR004A00
11 | 18 | [19] NPT NPT
11 | 19 | NOTES: 6. Service clearance 4 ft on each side.
11 | 20 | 1. Roof curb accessory is shipped
11 | 21 | disassembled. 7. Direction of airflow.
11 | 22 | 2. Insulated panels. 8. Connector packages CRBTMPWR001A00
11 | 23 | 3. Dimensions in [ ] are in millimeters. and 002A00 are for thru-the-curb connec-
11 | 24 | 4. Roof curb: galvanized steel. tions. Packages CRBTMP003A00 and
11 | 25 | 5. Attach ductwork to curb (flanges of duct 004A00 are for thru-the-bottom connections.
11 | 26 | rest on curb).
11 | 27 | 11
12 | 1 | Accessory dimensions (cont)
12 | 2 | A R C O C O E F S C S U O R R B Y “A” UN 5 I 0 T T S F I F ZE “B” “C” “ D D R ” A A I L N T G “E A ” S PO “ W F” ER CON “G TR ” OL CO PA N C N K E A C G TO E R
12 | 3 | CRRFCURB003A00 1¢-2† [356] HOLE ACCESSORY
12 | 4 | CRRFCURB004A00 2¢-0† [610] 008-014 3/4 † 3/4 † [19] NPT 1/2 † [12.7] CRBTMPWR001A00
12 | 5 | 2 [8 1 ¢- 2 6 8 † 7 7 ] / 1¢ [ - 5 1 1 8 6 0 † 3 1 ] 5/ [ 1 4 3 4 / . 4 5 † ] [1 [1 2 9 . 1 7 ] / ] 2 N † N P P T T 11 3 / / 4 4 † † [ [ 3 1 1 9 . ] 7 N ] N PT PT 1/2 N † [ P 1 T 2.7] C C R RB B T T M M P P W W R R 0 0 0 0 2 3 A A 0 0 0 0
12 | 6 | [19
12 | 7 | 3
12 | 8 | ]
12 | 9 | / 4
12 | 10 | N
12 | 11 | †
12 | 12 | PT
12 | 13 | 11/4 † [31.7] NPT NPT CRBTMPWR004A00
12 | 14 | NOTES: 6. Service clearance 4 ft on each side.
12 | 15 | 1. Roof curb accessory is shipped
12 | 16 | disassembled. 7. Direction of airflow.
12 | 17 | 2. Insulated panels, 1† thick polyurethane
12 | 18 | 3.
12 | 19 | f
12 | 20 | D
12 | 21 | o
12 | 22 | i
12 | 23 | a
12 | 24 | m
12 | 25 | m
12 | 26 | e
12 | 27 | ,
12 | 28 | n
12 | 29 | 1
12 | 30 | s
12 | 31 | 3
12 | 32 | io
12 | 33 | /4
12 | 34 | n s
12 | 35 | lb
12 | 36 | i n
12 | 37 | d e
12 | 38 | [
12 | 39 | n s
12 | 40 | ]
12 | 41 | it
12 | 42 | a
12 | 43 | y
12 | 44 | r
12 | 45 | .
12 | 46 | e in millimeters.
12 | 47 | 8. C
12 | 48 | 0
12 | 49 | o
12 | 50 | 2
12 | 51 | n
12 | 52 | A
12 | 53 | ne
12 | 54 | 0
12 | 55 | ct or
12 | 56 | a r
12 | 57 | p
12 | 58 | e
12 | 59 | a ck
12 | 60 | fo
12 | 61 | a
12 | 62 | r
12 | 63 | g e
12 | 64 | t
12 | 65 | s
12 | 66 | h r
12 | 67 | C
12 | 68 | u
12 | 69 | R
12 | 70 | -t
12 | 71 | B
12 | 72 | he
12 | 73 | T
12 | 74
12 | 75 | M
12 | 76 | cu
12 | 77 | P
12 | 78 | r
12 | 79 | W
12 | 80 | b
12 | 81 | R
12 | 82 | c
12 | 83 | 0
12 | 84 | o
12 | 85 | 0
12 | 86 | n
12 | 87 | 1
12 | 88 | n
12 | 89 | A
12 | 90 | e
12 | 91 | 0
12 | 92 | c
12 | 93 | 0
12 | 94 | ti o
12 | 95 | a
12 | 96 | n
12 | 97 | n
12 | 98 | s
12 | 99 | d
12 | 100 | .
12 | 101 | 4. Roof curb: 16 gage steel. Packages CRBTMP003A00 and 004A00 are
12 | 102 | 5. Attach ductwork to curb (flanges of duct for thru-the-bottom connections.
12 | 103 | rest on curb).
12 | 104 | 12

## Physical_Data_Complete
model | condenser_coil_rows | condenser_coil_fins_per_m | condenser_face_area_sqm | condenser_fan_type | condenser_fan_nominal_lps | condenser_fan_quantity | condenser_fan_diameter_mm | condenser_fan_motor_bkw | condenser_fan_speed_rps | evaporator_coil_rows | evaporator_coil_fins_per_m | evaporator_face_area_sqm | evaporator_fan_type | evaporator_fan_quantity | evaporator_fan_size_mm | evaporator_fan_nominal_lps | evaporator_motor_kw | max_continuous_bkw | motor_frame | fan_speed_range_rps | fan_bearing_type | max_allowable_rps | return_filter_quantity | return_filter_size_mm | outdoor_screen_quantity | outdoor_screen_size_mm | high_pressure_cutout_kpa | high_pressure_reset_kpa | low_pressure_cutout_kpa | low_pressure_reset_kpa | freeze_open_c | freeze_close_c | source_page
50TFF007 | 2 | 669 | 0.97 | Propeller | 1415 | 1 | 559 | 0.25 | 16 | 4 | 590 | 0.51 | Centrifugal | 1 | 254 x 254 | 1130 | 1.12 | 1.79 | 56 | 15.50-20.08 | Ball | 35 | 2 | 406 x 635 x 51 | 1 | 508 x 610 x 25 | 3448 | 2206 | 48 | 152 | -1 | 7 | 4
50TFF008 | 1 | 669 | 1.9 | Propeller | 2880 | 2 | 559 | 0.19 | 15.5 | 3 | 590 | 0.74 | Centrifugal | 1 | 381 x 381 | 1230 | 1.12 | 1.79 | 56 | 10.33-14.67 | Ball | 26.7 | 4 | 406 x 508 x 51 | 1 | 508 x 635 x 25 | 3103 | 2206 | 48 | 152 | -1 | 7 | 4
50TFF009 | 2 | 669 | 1.67 | Propeller | 2880 | 2 | 559 | 0.19 | 15.5 | 3 | 590 | 0.74 | Centrifugal | 1 | 381 x 381 | 1420 | 1.12 | 1.79 | 56 | 10.33-14.67 | Ball | 26.7 | 4 | 406 x 508 x 51 | 1 | 508 x 635 x 25 | 3103 | 2206 | 48 | 152 | -1 | 7 | 4
50TFF012 | 2 | 669 | 1.9 | Propeller | 3050 | 2 | 559 | 0.19 | 15.5 | 3 | 590 | 0.93 | Centrifugal | 1 | 381 x 381 | 1700 | 1.5 | 1.79 | 56 | 11.50-15.00 | Ball | 26.7 | 4 | 508 x 508 x 51 | 1 | 406 x 635 x 25 | 3103 | 2206 | 48 | 152 | -1 | 7 | 4
50TFF014 | 2 | 669 | 2.3 | Propeller | 3050 | 2 | 559 | 0.19 | 15.5 | 4 | 590 | 1.03 | Centrifugal | 1 | 381 x 381 | 1980 | 2.24 | 2.76 | 56 | 11.83-14.83 | Ball | 26.7 | 4 | 508 x 508 x 51 | 1 | 406 x 635 x 25 | 3448 | 2206 | 48 | 152 | -1 | 7 | 4

## Electric_Heat_Part_Numbers
unit_model | electrical_characteristics | heater_kw | part_number | notes | source_page
50TFF007 | 400-3-50 | 4.2 | 50DJ90-0921 |  | 33
50TFF007 | 400-3-50 | 8 | 50DJ90-0941 |  | 33
50TFF007 | 400-3-50 | 9.7 | 50DJ90-0951 |  | 33
50TFF007 | 400-3-50 | 16 | 50DJ90-0941 | Two heater packages required | 33
50TFF007 | 400-3-50 | 17.7 | 50DJ90-0941, 0951 | Two heater packages required | 33
50TFF008 | 400-3-50 | 9.7 | 50DJ90-1681 |  | 33
50TFF008 | 400-3-50 | 11.5 | 50DJ90-1631 |  | 33
50TFF008 | 400-3-50 | 19.3 | 50DJ90-1641 |  | 33
50TFF008 | 400-3-50 | 22.9 | 50DJ90-1651 |  | 33
50TFF008 | 400-3-50 | 29 | 50DJ90-1681, 1641 | Two heater packages required | 33
50TFF009 | 400-3-50 | 9.7 | 50DJ90-1681 |  | 33
50TFF009 | 400-3-50 | 11.5 | 50DJ90-1631 |  | 33
50TFF009 | 400-3-50 | 19.3 | 50DJ90-1641 |  | 33
50TFF009 | 400-3-50 | 22.9 | 50DJ90-1651 |  | 33
50TFF009 | 400-3-50 | 29 | 50DJ90-1681, 1641 | Two heater packages required | 33
50TFF012 | 400-3-50 | 9.7 | 50DJ90-1681 | Available on 012 only | 33
50TFF012 | 400-3-50 | 11.5 | 50DJ90-1631 | Available on 012 only | 33
50TFF012 | 400-3-50 | 19.3 | 50DJ90-1641 |  | 33
50TFF012 | 400-3-50 | 22.9 | 50DJ90-1651 |  | 33
50TFF012 | 400-3-50 | 29 | 50DJ90-1681, 1641 |  | 33
50TFF012 | 400-3-50 | 34.7 | 50DJ90-1631, 1651 | Two heater packages required | 33
50TFF014 | 400-3-50 | 11.5 | 50DJ90-1631 | Available on 014 only | 33
50TFF014 | 400-3-50 | 19.3 | 50DJ90-1641 |  | 33
50TFF014 | 400-3-50 | 22.9 | 50DJ90-1651 |  | 33
50TFF014 | 400-3-50 | 29 | 50DJ90-1681, 1641 |  | 33
50TFF014 | 400-3-50 | 34.7 | 50DJ90-1631, 1651 | Two heater packages required | 33
NOTE |  |  |  | kW ratings are at 400 V; heaters are field installed only. | 33

## Additional_Data_Index
data_group | new_or_updated_sheet | what_it_contains | source_pages
Corrected airflow | Unit_Specs | Separated evaporator nominal airflow from condenser nominal airflow and added condenser fan quantity/diameter/motor/speed. | 4-5
Complete physical data | Physical_Data_Complete | Coils, fans, filters, outdoor screens, pulley/speed-related summary, and safety thermostat/switch settings by model. | 4-5
Base dimensions | Base_Dimensions | Added J/K dimensions, connection sizes and key installation clearances. | 9-10
Electric heat ordering | Electric_Heat_Part_Numbers | Accessory part numbers, 400-3-50 electrical characteristic, and heater package footnotes. | 33
Validation | Validation_Report | Checks performed, status, corrections and additions. | 4-5, 9-10, 33-34

## Model_Nomenclature
position_or_code | meaning | available_values_or_definition | example_50TFF007Z--903AA | source_page
50 | Product family / function | Cooling only with optional electric heat | 50 | 3
TFF | Unit type | Constant volume | TFF | 3
007 / 008 / 009 / 012 / 014 | Nominal capacity | 007=17.6 kW (5 tons); 008=21.5 kW (6.1 tons); 009=24.3 kW (6.9 tons); 012=29.2 kW (8.3 tons); 014=35.9 kW (10.2 tons) | 007 | 3
- / Z | Factory-installed communicating control | - = no control; Z = Apollo communicating control | Z | 3
Coil fin option | Evaporator/condenser coil materials | - = Al evaporator, Al condenser; B = Cu evaporator, Cu condenser; C = Al evaporator, Cu condenser; D = Technicoat-coated condenser coil with aluminum fins; V = precoated aluminum condenser coil fins | - | 3
9 | Voltage-Phase-Frequency | 9 = 400-3-50 | 9 | 3
0 | Design series | 0 = Original | 0 | 3
3 | Packaging | 3 = Export | 3 | 3
AA | Factory-installed option code | Refer to 50TFF ordering data / FIOP code table | AA | 3
Legend | Material abbreviations | Al = Aluminum; Cu = Copper; FIOP = Factory-Installed Option; all coils have copper tubes |  | 3
Quality assurance | Certifications shown in PDF | ISO 9002; EN 29002; BS5750 Part 2; ANSI/ASQC Q92; UL mark shown |  | 3

## Selection_Procedure
step | SI_example | English_example | source_page
I. Design requirements | Cooling 28 kW; SHC 19 kW; heating 18 kW; condenser entering air 36 C; evaporator entering air 26.7 C edb/20 C ewb; airflow 1520 L/s; ESP 300 Pa; 400-3-50; Durablade economizer. | Cooling 96,000 Btuh; SHC 70,000 Btuh; heating 62,000 Btuh; condenser entering air 95 F; evaporator entering air 80 F edb/67 F ewb; airflow 3200 cfm; ESP 1.10 in. wg; 400-3-50; Durablade economizer. | 13
II. Select cooling unit | For 50TFF012 at stated conditions: gross TC 30.1 kW and SHC 21.2 kW. | For 50TFF012 at stated conditions: gross TC 102,500 Btuh and SHC 76,000 Btuh. | 13
III. Select electric heat | Required 18 kW; select 19.3 kW heater at 400 V. | 62,000 Btuh / 3413 = 18.2 kW; select 19.3 kW heater at 400 V; gross 65,871 Btuh. | 13
IV. Fan selection | Static pressure total = 300 + 9 economizer + 14 electric heat = 323 Pa. At 1520 L/s: 14.5 r/s and 1.56 kW. | Static pressure total = 1.10 + 0.04 + 0.06 = 1.20 in. wg. At 3200 cfm: 844 rpm and 1430 W. | 13
V. Net capacities | Net cooling = 30.1 - 1.56 = 28.5 kW; net sensible = 21.2 - 1.56 = 19.6 kW; net heating = 19.3 + 1.56 = 24.9 kW. | Net cooling = 102,500 - 1430 x 3.413 = 97,619 Btuh; net sensible = 71,119 Btuh; net heating = 65,871 + 4,881 = 70,752 Btuh. | 14
Rating notes | Ratings are gross and exclude evaporator-fan motor power/heat. Direct interpolation permitted; do not extrapolate. | Same rule applies in English tables. | 15,21

## Application_Controls_Notes
topic | normalized_value_or_note | source_page
Standard low ambient cooling | Standard operation down to -3.8 C (25 F); with Motormaster I or II down to -17.8 C (0 F). | 6
Maximum operating ambient | Capable of starting/running at 46.1 C (115 F) ambient at ±10% voltage per guide specifications. | 43
Condensate drain | Sloped pan supports external side or internal bottom drain; field-supplied P-trap required. | 2
Economizer outdoor air | Durablade adjustable from 100% outdoor air to 100% return air; manual outdoor-air damper up to 50%; 25% and 100% two-position accessories available. | 2
Economizer relief | EconoMi$er: up to 100% barometric relief for 007 and 90% return-air relief for 008-014; Durablade: 30% return-air relief. | 31
Compressor timing | Apollo/programmable thermostat recycle delay 5 minutes; EconoMi$er control note states compressor minimum on/off/interstage delay 2 minutes. | 3
Cooling control setpoints | EconoMi$er stage 1 supply-air set point 12.8 C (55 F); modulation thresholds documented on pages 38-39. | 38
Heating control | With heater, W1 energizes IFM and HC1; W2 energizes HC2 for second-stage heat; economizer at minimum during heating. | -1
Clearance | Condenser coil: 36 in one side and 12 in other; overhead 60 in; horizontal supply/return end 0 in; control-box side clearances per NEC. | 9
Filters | Standard throwaway 51 mm (2 in.) filters; model-specific quantities/sizes in Physical_Data_Complete. | 1
Indoor air quality | Meets ASHRAE 62; optional dirty-filter switch and CO2/enthalpy sensors available. | -2
Motors | Commercial-duty motors with permanently lubricated bearings; condenser motors totally enclosed. | -1

## Completeness_Audit
pdf_pages | section | status | Excel_location | audit_note
1-3 | Features, benefits, nomenclature and QA | COMPLETE | PDF_Text; Model_Nomenclature; Options_Accessories; Application_Controls_Notes | Text retained; nomenclature and key codes normalized.
4-5 | Physical data SI and English | COMPLETE | Unit_Specs; Physical_Data_Complete; Extracted_Tables | Cross-checked model-by-model; pressure relief corrected by compressor type.
6-8 | Options/accessories and controls descriptions | COMPLETE | Options_Accessories; PDF_Text; Application_Controls_Notes | Options table normalized; descriptive text retained.
9-10 | Base unit dimensions | COMPLETE | Base_Dimensions; Extracted_Tables | H/J/K, weights, connections and clearances included.
11-12 | Accessory dimensions | RAW + KEY VALUES | Dimensions_Accessories; Base_Dimensions | Original OCR-like raw extraction retained; key roof-curb connection data normalized in Base_Dimensions.
13-14 | Selection procedure | COMPLETE | Selection_Procedure; PDF_Text | SI and English worked examples normalized.
15-29 | Cooling and fan performance tables | COMPLETE | Cooling_Capacity; Fan_Performance; Performance_Tables; Extracted_Tables | Raw and structured tables retained; no charts interpreted.
30-33 | Fan motor, economizer, exhaust, pressure-drop, heater tables | COMPLETE | Fan_Motor_Performance; Static_Pressure_Accessories; Electric_Heat_Part_Numbers; Extracted_Tables | All table cells retained; heater part numbers normalized.
34 | Electrical data | COMPLETE | Electrical_Data; Electric_Heating_Capacities; Heater_Ratings | Cross-checked against page 34.
35-37 | Piping/wiring schematics and legends | RAW | PDF_Text; Extracted_Tables | Diagrams intentionally not interpreted per user instruction; legends/text retained.
38-40 | Controls and operating sequence | COMPLETE | PDF_Text; Application_Controls_Notes | Full prose retained; key setpoints and sequences normalized.
41 | Application data | RAW + KEY VALUES | PDF_Text; Application_Controls_Notes | Full application text retained; key limits/clearances summarized.
42-44 | Guide specifications | RAW | PDF_Text | Full guide-specification text retained; not duplicated into a second normalized sheet because it is prose.