## README
field | value
Source file | 50TJProductData.pdf
Product | Carrier 50TJ016-028 Single-Package Rooftop Units
Purpose | Structured extraction for product-selection software, using the supplied hvac_catalog.xlsx style as a reference.
Units | SI/English values are retained where present.
Performance data | Performance_Tables contains extracted table cells from pages 19-32, indexed by source page/table/row/column.
Audit | PDF_Text preserves text from all 56 pages; source_page is retained on extracted tables.
Added/verified sheets | Electrical_Data (PDF p.33); Accessory_Dimensions (pp.14-16); Cooling_Capacity (pp.19-22); Fan_Performance (pp.24-30); Static_Pressure_Accessories (p.31); Fan_Motor_Performance (p.32)
Structured format | Each row represents one source-table row and includes source_page, table_no, table_row, and col_1..col_23.

## Unit_Specs
model | nominal_capacity_kw | nominal_capacity_tons | cooling_min_lps | cooling_min_cfm | cooling_max_lps | cooling_max_cfm | base_weight_kg | base_weight_lb | compressor_models | capacity_stages_pct | refrigerant_circuits | charge_circuit1_kg | charge_circuit2_kg | condenser_rows_fins_m | condenser_face_area_sqm | evaporator_rows_fins_m | evaporator_face_area_sqm | evaporator_airflow_lps | evaporator_motor_kw | max_continuous_bkw | motor_frame | fan_speed_range_rps | refrigerant | expansion_device | rated_power
50TJ016 | 52.8 | 15 | 2125 | 4500 | 3525 | 7500 | 708 | 1560 | 2...ZR108KC | 50/50 | 2 | 4.81 | 4.81 | 2...669 | 2.02 | 2...669 | 1.63 | 2832 | 2.76 | 3.17 | 56H | 12.38-16.38 / 17.05-21.67 | R-22 | TXV | 400-3-50
50TJ024 | 70.3 | 20 | 2800 | 6000 | 4800 | 10000 | 816 | 1800 | 1...ZR16M3, 1...ZR125KC | 55/45 | 2 | 6.76 | 5.72 | 3...590 | 2.02 | 3...590 | 1.63 | 3776 | 5.59 | 7.68 | 213T | 12.8-15.2 / 16.6-20.3 | R-22 | TXV | 400-3-50
50TJ028 Standard | 87.9 | 25 | 3300 | 7000 | 5300 | 11250 | 885 | 1950 | 1...ZR19M3, 1...ZR16M3 | 55/45 | 2 | 9.07 | 6.03 | 4...590 | 2.02 | 4...590 | 1.63 | 4720 | 7.46 | 9.92 (400V) / 8.60 (220V) | 215T | 14.8-17.8 / 18.6-22.4 | R-22 | TXV | 400-3-50
50TJ028 High Static DEC | 87.9 | 25 | 3300 | 7000 | 5300 | 11250 | 885 | 1950 | 1...ZR19M3, 1...ZR16M3 | 55/45 | 2 | 9.07 | 6.03 | 4...590 | 2.02 | 4...590 | 1.63 | 4720 | 7.46 | 9.92 (400V) / 8.60 (220V) | 215T | 14.8-17.8 / 18.6-22.4 | R-22 | TXV | 400-3-50

## Heater_Ratings
model | unit_voltage_v | heater_kw | heater_stages | percent_heat_per_stage | minimum_airflow_lps | minimum_airflow_cfm
50TJ016 | 380 | 20.3 | 2 | 50/50 | 2124 | 4509
50TJ016 | 380 | 34.5 | 3 | 67/33 | 2124 | 4509
50TJ016 | 380 | 50 | 4 | 50/50 | 2124 | 4509
50TJ016 | 400 | 22.5 | 2 | 50/50 | 2124 | 4509
50TJ016 | 400 | 38.2 | 3 | 67/33 | 2124 | 4509
50TJ016 | 400 | 55.4 | 4 | 50/50 | 2124 | 4509
50TJ016 | 416 | 24.3 | 2 | 50/50 | 2124 | 4509
50TJ016 | 416 | 41.1 | 3 | 67/33 | 2124 | 4509
50TJ016 | 416 | 59.7 | 4 | 50/50 | 2124 | 4509
50TJ024 | 380 | 20.3 | 2 | 50/50 | 2832 | 6012
50TJ024 | 380 | 34.5 | 3 | 67/33 | 2832 | 6012
50TJ024 | 380 | 50 | 4 | 50/50 | 2832 | 6012
50TJ024 | 400 | 22.5 | 2 | 50/50 | 2832 | 6012
50TJ024 | 400 | 38.2 | 3 | 67/33 | 2832 | 6012
50TJ024 | 400 | 55.4 | 4 | 50/50 | 2832 | 6012
50TJ024 | 416 | 24.3 | 2 | 50/50 | 2832 | 6012
50TJ024 | 416 | 41.1 | 3 | 67/33 | 2832 | 6012
50TJ024 | 416 | 59.7 | 4 | 50/50 | 2832 | 6012
50TJ028 | 380 | 20.3 | 2 | 50/50 | 3303 | 7012
50TJ028 | 380 | 34.5 | 3 | 67/33 | 3303 | 7012
50TJ028 | 380 | 50 | 4 | 50/50 | 3303 | 7012
50TJ028 | 400 | 22.5 | 2 | 50/50 | 3303 | 7012
50TJ028 | 400 | 38.2 | 3 | 67/33 | 3303 | 7012
50TJ028 | 400 | 55.4 | 4 | 50/50 | 3303 | 7012
50TJ028 | 416 | 24.3 | 2 | 50/50 | 3303 | 7012
50TJ028 | 416 | 41.1 | 3 | 67/33 | 3303 | 7012
50TJ028 | 416 | 59.7 | 4 | 50/50 | 3303 | 7012

## Options_Accessories
item | option_factory_installed | accessory_field_installed | installation_note
Apollo Direct Digital Communicating Controls | X |  | Factory installed
Service Option Package | X |  | Factory installed
Integrated Economizer | X | X | Factory installed
Electric Heat (400-3-50 Units Only) | X | X | Factory installed
Enviro-Shield Condenser Coil Options | X |  | Factory installed
Hail Guard Condenser Coil Grille |  | X | Field installed
Alternate Drive | X |  | Factory installed
Electronic Programmable Thermostat |  | X | Field installed
25% Open Two-Position Damper |  | X | Field installed
Barometric Relief Damper |  | X | Field installed
Roof Curbs |  | X | Field installed
Horizontal Adapter Curb |  | X | Field installed
Thermostats and Subbases |  | X | Field installed
Power Exhaust |  | X | Field installed
Low-Ambient Kit |  | X | Field installed
Winter Start Time-Delay Relay |  | X | Field installed
Motormaster III Head Pressure Control (Speed Control) |  | X | Field installed
Time Guard II Control Circuit |  | X | Field installed
Accusensor III Enthalpy Sensor |  | X | Field installed
Hydronic Glycol Coil |  | X | Field installed

## Base_Dimensions
model | base_weight_lb | base_weight_kg | corner_a_lb | corner_a_kg | corner_b_lb | corner_b_kg | corner_c_lb | corner_c_kg | corner_d_lb | corner_d_kg | dim_x_ft_in | dim_x_mm | dim_y_ft_in | dim_y_mm
50TJ016 | 1560 | 708 | 392 | 178 | 366 | 166 | 387 | 176 | 416 | 188 | 3-5 | 1041 | 3-6 | 1067
50TJ024 | 1800 | 816 | 423 | 192 | 412 | 185 | 490 | 220 | 475 | 213 | 3-3 | 991 | 3-7 | 1092
50TJ028 Standard | 1950 | 885 | 441 | 200 | 416 | 189 | 533 | 242 | 560 | 254 | 3-1 | 940 | 3-6 | 1067
50TJ028 High Static DEC | 1950 | 885 | 441 | 200 | 416 | 189 | 553 | 251 | 580 | 263 | 3-1 | 940 | 3-6 | 1067

## PDF_Text
source_page | page_text
1 | Product 50TJ016-028 Single-Package Rooftop Units Data Electric Cooling with Electric Heat Option 50 Hz Nominal Capacity: 52.8 to 87.9 kW (15 to 25 Tons) Standard Efficiency Rooftop Units with: • Dual, electrically and mechanically independent refrigerant circuits (cid:127) Scroll compressors on each circuit (cid:127) TXV refrigerant metering devices (cid:127) Pre-painted galvanized steel cabinet for long life and quality appearance (cid:127) Non-corrosive, sloped condensate drain pans meet ASHRAE 62-99 (IAQ) (cid:127) Fifty-one mm (2-in.) air filters (cid:127) Heating options: — Electric heat — Hydronic glycol heating coil Features/Benefits Every compact one-piece unit arrives fully assembled, charged, tested, and ready to run. Durable, dependable construction Designed for durability in any climate, the weather-resistant cabinets are con- structed of galvanized steel, bonder- ized, and all exterior panels are coated with a prepainted baked enamel finish. The paint finish is non-chalking, and is capable of withstanding ASTM B117 (U.S.A.) 500-hour Salt Spray Test. All internal cabinet panels are primed, permitting longer life and a more attractive appearance for the entire unit. Totally enclosed condenser-fan motors and permanently lubricated bearings provide additional unit dependability. Copyright 2000 Carrier Corporation Form 50TJ-C11PD
2 | Easy installation Thru-the-curb service connections Quiet, efficient operation and allow power and control wiring to be dependable performance All units fit one size roof curb. The routed through the curb, minimizing contractor can order and install the Scroll compressors have vibration iso- roof penetrations. Both power and roof curb early in the construction lators for extremely quiet operation. control connections are made on the stage, before decisions on size require- Efficient fan and motor design permits same side of the unit to simplify instal- ments are made. operation at very low sound levels. lation. In addition, color-coded wires All units feature base rail design with These units offer high energy effi- permit easy tracing and diagnostics. forklift slots and rigging holes for easier ciency and lower utility costs through maneuvering. Durable packaging pro- Integrated economizers and part load operation using 2 stages of tects all units during shipment and outdoor air cooling. Each stage of cooling has its storage. own scroll compressor and indepen- During a first stage call for cooling, if The units can be easily converted the outdoor-air temperature is below dent refrigerant circuit. Each circuit from a vertical to a horizontal dis- the control changeover set point, the features a thermostatic expansion charge configuration by using the hori- discharge-air sensor modulates the valve (TXV) for refrigerant metering. zontal supply/return adapter roof economizer outdoor-air damper open Quiet and efficient operation is pro- curbs. to achieve the set point. When second- vided by belt-driven evaporator fans. NOTE: On units using horizontal sup- stage cooling is called for, the no. 1 The belt-driven evaporator-fan with ply and return, the accessory baromet- compressor is energized in addition to variable-pitch pulleys allows adjustment ric relief or power exhaust MUST be the economizer. If the outdoor-air tem- to available static pressure to meet the installed on the return ductwork. perature is above the changeover set job requirements of even the most de- point, the first stage of compression is manding applications. A standard (low- Convenient duct openings in the activated and the economizer stays at medium static) and alternate (high stat- unit basepans permit side-by-side or vent position. Economizer operation is ic) drive is available for these units. concentric duct connections (see Appli- controlled by Accusensor™ dry-bulb cation data section on page 48) with- Carrier Apollo controls add thermostat that senses outdoor-air out requiring internal unit modification. reliability, efficiency, and temperature. Accessory upgrade kits simplification The non-corrosive sloped conden- include solid-state enthalpy sensor con- sate pan permits either an external, trol and differential enthalpy sensor. The Apollo direct digital controls are horizontal, side condensate drain (out- ordered as a factory-installed option. For units without economizer, year- side the roof curb) or an internal, verti- Designed and manufactured exclusively round ventilation is enhanced by a cal, bottom drain (inside the roof curb). by Carrier, the controls can be used to manual outdoor-air damper. The Both options require an external, field- actively monitor and control all modes damper can be preset to admit up to supplied P-trap. of operation, as well as to monitor 25% outdoor air. Factory- and field-installed electric evaporator-fan status, filter status, In addition, the barometric relief heaters are available in a wide range of indoor-air quality (humidity and carbon damper or power exhaust accessory capacities. dioxide), supply-air temperature, and can be utilized to help maintain proper outdoor-air temperature. Indoor-air quality begins with building pressure. Carrier rooftops Sloped condensate pans minimize bio- logical growth in rooftop units in ac- cordance with ASHRAE (American Table of contents Society of Heating, Refrigeration, and Air Conditioning Engineers) Standard Page 62. Fifty-one mm (2-in.) filters with op- tional dirty filter indicator switch pro- Features/Benefits . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 1-3 vide for greater particle reduction in Model Number Nomenclature . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 3 the return air. The face-split evapora- Capacity Ratings . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 4 tor coils improve the dehumidification Physical Data . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 5-7 capability of the standard units, and Options and Accessories . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 8-11 accessory enthalpy controls available Base Unit Dimensions. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 12,13 with the optional economizers maxi- Accessory Dimensions . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 14-16 mize building humidity control. Selection Procedure . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 17,18 Performance Data . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 19-32 Simple electrical connections Electrical Data . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 33 Terminal boards, located in the base Typical Piping and Wiring . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 34 unit control box, facilitate connections Typical Wiring Schematic . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 35-38 to room thermostat, outdoor thermo- Controls . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 39-47 stat(s), economizer, and electric heat. Application Data . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 48-50 Service panels are quickly removed, Guide Specifications . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 51-54 permitting easy servicing. 2
3 | Features/Benefits (cont) The Apollo communicating controls Additional data points may be ac- wind-blown panel puncturing deli- are factory-installed into the unit con- cessed when a third party EMS system cate roof materials. The 4 extended trol box, and come equipped with built- utilizing a DataPORT™ or DataLINK™ access panels are also equipped in diagnostic capabilities. Light- device is connected to the CCN port of with “tie back” retaining devices to emitting diodes (LEDs) simplify trouble- a master thermostat. The data points hold the door in the open position shooting by indicating thermostat com- that are Read/Write may be forced by while servicing the unit. mands for both stages of heating and the user to change operating parme- (cid:127) An external, covered, 115-v cooling, evaporator fan operation, and ters. Refer to the Points Display table Ground Fault Interrupt (GFI) recep- economizer operation. The Apollo in the Application Data section on tacle is provided as a convenient communicating controls are designed page 49 for additional information and power source for drills, lights, refrig- to work specifically with the Carrier a list of accessible data points. erant recovery units, or other elec- TEMP and VVT® (variable volume and Service option package trical service tools. Simply connect temperature) thermostats. The Apollo the outlet to a field-supplied and controls, combined with Carrier ther- Servicing a rooftop unit has never properly fused branch circuit power mostats, incorporate a 5-minute recy- been easier with the new factory- supply. cle delay timer between modes of op- installed service option package for (cid:127) An integral non-fused disconnect eration to prevent short cycling. these rooftop units. This package in- switch within the rooftop unit cludes the following features: The standard rooftop control system reduces installation time, labor and is readily adaptable to all conventional (cid:127) Hinged access panels are provided material costs. Safety is assured by and programmable thermostats. In ad- for the filter/indoor-fan motor, com- an interlock which prevents access dition, units with the Apollo controls pressors, evaporator fan, and con- to the control box unless the switch are suitable for integration into the trol box areas. Quick access to is in the OFF position. In addition, Carrier Comfort Network (CCN) build- major components is accomplished the externally mounted handle ing control systems if required. This by simply unlatching and swinging incorporates power lockout capabil- system gives the unit thermostats the open the various panels. Each ity to further protect service flexibility to communicate with almost hinged panel is permanently personnel. any thermostat or Carrier Control Net- mounted to the unit, thereby elimi- work (CCN) system. nating the concern of a dropped or Model number nomenclature 50 TJ – 024 Z – – 9 7 3 YA 50 – Cooling Only/Cooling with Factory-Installed Options* Optional Electric Heat Packaging 3 – Export TJ – Constant Volume Design Series 0 – Original 7 – Copeland scroll 8 – Two Outdoor Fans (50TJ016 Only) Nominal Tons 016 – 52.8 kW (15 Tons) Voltage 024 – 70.3 kW (20 Tons) 8 – 220-3-50 028 – 87.9 kW (25 Tons) 9 – 400-3-50 Coil Protection Options - – Al/Cu Condenser & Evaporator B – Cu/Cu Condenser & Evaporator C – Cu/Cu Condenser & Al/Cu Evaporator Service/Control Options E – E-Coated Al/Cu Condenser Coil - – Standard Controls F – E-Coated Cu/Cu Condenser Coil Z – Apollo Controls V – Black Pre-Coated Condenser Fins LEGEND Al — Aluminum Cu — Copper FIOP — Factory-Installed Option *Refer to 50TJ Price Pages for 50TJ FIOP code table or contact your local Carrier representative for more details. 3
4 | Capacity ratings COOLING OPERATING RANGE UNIT MINIMUM MAXIMUM* 50TJ L/s cfm L/s cfm 016 2125 4500 3525 7,500 024 2800 6000 4800 10,000 028 3300 7000 5300 11,250 *Operation at these levels may be limited by entering evaporator air wet bulb temperatures. See Cooling Capacities tables on pages 19-22 for further details. ELECTRIC RESISTANCE HEATER DATA (400-3-50 Units Only) HEATER kW MINIMUM UNIT Unit Voltage HEATER % HEAT MAXIMUM HEATING AIRFLOW 50TJ STAGES PER STAGE STAGES* 380 400 416 L/s cfm 20.3 22.5 24.3 2 50/50 2 016 34.5 38.2 41.1 2 67/33 3 2124 4500 50.0 55.4 59.7 2 50/50 4 20.3 22.5 24.3 2 50/50 2 024 34.5 38.2 41.1 2 67/33 3 2832 6000 50.0 55.4 59.7 2 50/50 4 20.3 22.5 24.3 2 50/50 2 028 34.5 38.2 41.1 2 67/33 3 3303 7000 50.0 55.4 59.7 2 50/50 4 *Maximum number of stages using accessory low-ambient kit or head pressure control device and low-ambient kit. NOTE: Heaters are rated at nominal voltage of 400-3-50 and are available on 400-3-50 units only. For rating of heater at unit nameplate voltage refer to correct column of table. 4
5 | Physical data — SI 028 028 UNIT 50TJ 016 024 (Standard) (High-Static DEC Option) NOMINAL CAPACITY (kW) 52.8 70.3 87.9 87.9 OPERATING WEIGHT (kg) For Operating Weights, see page 7 COMPRESSOR Scroll Quantity...Model (Ckt 1, Ckt 2) 2...ZR108KC 1...ZR16M3, 1...ZR125KC 1...ZR19M3, 1...ZR16M3 1...ZR19M3, 1...ZR16M3 Capacity Stages (%) 50/50 55/45 55/45 55/45 Number of Refrigerant Circuits 2 2 2 2 Oil (ml) (Ckt 1, Ckt 2) 3135 4022, 3135 4022, 4022 4022, 4022 REFRIGERANT TYPE R-22 Expansion Device TXV Operating Charge (kg) Circuit 1* 4.81 6.76 9.07 9.07 Circuit 2 4.81 5.72 6.03 6.03 CONDENSER COIL Cross-Hatched 3/8-in. Copper Tubes, Aluminum Lanced, Aluminum Pre-Coated, or Copper Plate Fins Rows...Fins/m 2...669 3...590 4...590 4...590 Total Face Area (sq m) 2.02 2.02 2.02 2.02 CONDENSER FAN Propeller Type Propeller Type Nominal L/s 6700 8600 Quantity...Diameter (mm) 2...762 2...762 Motor BkW...r/s 0.75...17.9 3.73...17.9 Watts Input (Total) 3400 7800 EVAPORATOR COIL Cross-Hatched 3/8-in. Copper Tubes, Aluminum Lanced or Copper Plate Fins, Face Split Rows...Fins/m 2...669 3...590 4...590 4...590 Total Face Area (sq m) 1.63 1.63 1.63 1.63 EVAPORATOR FAN Centrifugal Type Quantity...Size (mm) 2...254 x 254 2...305 x 305 2...305 x 305 2...305 x 305 Type Drive Belt Belt Belt Belt Nominal L/s 2832 3776 4720 4720 Motor kW 2.76 5.59 7.46 7.46 Motor Nominal r/s 28.8 29.1 29.0 29.0 9.92 (400 v), 9.92 (400 v), Maximum Continuous BkW 3.17 7.68 8.60 (220 v) 8.60 (220 v) Motor Frame Size 56H 213T 215T 215T Fan r/s Range Low-Medium Static 12.38-16.38 12.8-15.2 14.8-17.8 14.8-17.8 High Static 17.05-21.67 16.6-20.3 18.6-22.4 18.6-22.4 Motor Bearing Type Ball Ball Ball Ball Maximum Allowable r/s 25.8 25.8 25.8 25.8 Motor Pulley Pitch Diameter (mm) Low-Medium Static 79/104 140/165 125/150 125/150 High Static 94/119 137/168 125/150 125/150 Nominal Motor Shaft Diameter (mm) 22 35 35 35 Fan Pulley Pitch Diameter (mm) Low-Medium Static 152 239 203 203 High Static 132 201 163.0 163.0 Nominal Fan Shaft Diameter (mm) 30 36.5 36.5 36.5 Belt, Quantity...Type...Length (mm) Low-Medium Static 1...BX...1067 1...BX...1372 2...BX...1270 2...BX...1270 High Static 1...BX...1067 1...BX...1270 2...BX...1194 2...BX...1194 Pulley Center Line Distance (mm) 343-394 371-391 371-391 371-391 Speed Change per Full Turn of Low-Medium Static .80 .47 .60 .60 Movable Pulley Flange (r/s) High Static .92 .62 .75 .75 Movable Pulley Maximum Full Turns Low-Medium Static 5 5 5 5 From Closed Position High Static 5 6 5 5 Factory Setting 3.5 3 3 3 Factory Speed Setting (r/s) Low-Medium Static 13.58 13.75 16.01 16.01 High Static 18.43 18.42 20.08 20.08 HIGH-PRESSURE SWITCH (kPa) Cutout 2951 Reset (Auto.) 2206 LOW-PRESSURE SWITCH (kPa) Cutout 186 Reset (Auto.) 303 FREEZE PROTECTION THERMOSTAT (C) Opens –1 ± 2 Closes 7 ± 2 OUTDOOR-AIR INLET SCREENS Cleanable Quantity...Size (mm) 2...508 x 635 x 25 1...508 x 508 x 25 RETURN-AIR FILTERS Throwaway† Quantity...Size (mm) 4...508 x 508 x 50 4...406 x 508 x 50 LEGEND *Circuit 1 uses the lower portion of condenser coil and lower portion of evaporator coils, and Circuit 2 uses the upper portion of both coils. Al — Aluminum †The 50TJ028 units requires 50-mm industrial-grade filters capable of handling BkW — Brake Kilowatts face velocities of up to 3.2 m/s (such as American Air Filter no. 5700 or Cu — Copper equivalent). DEC — Design Enhancement Center TXV — Thermostatic Expansion Valve 5
6 | Physical data — English 028 028 UNIT 50TJ 016 024 (Standard) (High-Static DEC Option) NOMINAL CAPACITY (tons) 15 20 25 25 OPERATING WEIGHT (lbs) For Operating Weights, see page 7 COMPRESSOR Scroll Quantity...Model (Ckt 1, Ckt 2) 2...ZR108KC 1...ZR16M3, 1...ZR125KC 1...ZR19M3, 1...ZR16M3 1...ZR19M3, 1...ZR16M3 Capacity Stages (%) 50/50 55/45 55/45 55/45 Number of Refrigerant Circuits 2 2 2 2 Oil (oz) (Ckt 1, Ckt 2) 106 136, 106 136, 136 136, 136 REFRIGERANT TYPE R-22 Expansion Device TXV Operating Charge (lb-oz) Circuit 1* 10-10 14-14 20-0 20-0 Circuit 2 10-10 12-10 13-5 13-5 CONDENSER COIL Cross-Hatched 3/8-in. Copper Tubes, Aluminum Lanced, Aluminum Pre-Coated, or Copper Plate Fins Rows...Fins/in. 2...17 3...15 4...15 4...15 Total Face Area (sq ft) 21.7 21.7 21.7 21.7 CONDENSER FAN Propeller Type Propeller Type Nominal Cfm 14,200 8600 Quantity...Diameter (in.) 2...30 2...762 Motor Hp...Rpm 1...1075 3.73...17.9 Watts Input (Total) 3400 7800 EVAPORATOR COIL Cross-Hatched 3/8-in. Copper Tubes, Aluminum Lanced or Copper Plate Fins, Face Split Rows...Fins/in. 2...17 3...15 4...15 4...15 Total Face Area (sq ft) 17.5 17.5 17.5 17.5 EVAPORATOR FAN Centrifugal Type Quantity...Size (in.) 2...10 x 10 2...12 x 12 2...12 x 12 2...12 x 12 Type Drive Belt Belt Belt Belt Nominal Cfm 6000 8000 10,000 10,000 Motor Hp 3.7 7.5 10 10 Motor Nominal Rpm 1438 1455 1450 1450 13.3 (400 v), 13.3 (400 v), Maximum Continuous Bhp 4.25 10.3 11.5 (220 v) 11.5 (220 v) Motor Frame Size 56H 213T 215T 215T Fan Rpm Range Low-Medium Static 743-983 769- 909 888-1069 888-1069 High Static 1023-1300 994-1216 1114-1341 1114-1341 Motor Bearing Type Ball Ball Ball Ball Maximum Allowable Rpm 1550 1550 1550 1550 Motor Pulley Pitch Diameter (in.) Low-Medium Static 3.1/4.1 5.5/6.5 4.9/5.9 4.9/5.9 High Static 3.7/4.7 5.4/6.6 4.9/5.9 4.9/5.9 Nominal Motor Shaft Diameter (in.) 7/8 13/8 13/8 13/8 Fan Pulley Pitch Diameter (in.) Low-Medium Static 6.0 10.4 8.0 8.0 High Static 5.2 7.9 6.4 6.4 Nominal Fan Shaft Diameter (in.) 13/16 17/16 17/16 17/16 Belt, Quantity...Type...Length (in.) Low-Medium Static 1...BX...42 1...BX...54 2...BX...50 2...BX...50 High Static 1...BX...42 1...BX...50 2...BX...47 2...BX...47 Pulley Center Line Distance (in.) 13.5-15.5 14.6-15.4 14.6-15.4 14.6-15.4 Speed Change per Full Turn of Low-Medium Static 48 28 36 36 Movable Pulley Flange (Rpm) High Static 55 37 45 45 Movable Pulley Maximum Full Turns Low-Medium Static 5 5 5 5 From Closed Position High Static 5 6 5 5 Factory Setting 3.5 3 3 3 Factory Speed Setting (Rpm) Low-Medium Static 815 825 960 960 High Static 1106 1105 1205 1205 HIGH-PRESSURE SWITCH (psig) Cutout 426 Reset (Auto.) 320 LOW-PRESSURE SWITCH (psig) Cutout 27 Reset (Auto.) 44 FREEZE PROTECTION THERMOSTAT (F) Opens 30 ± 5 Closes 45 ± 5 OUTDOOR-AIR INLET SCREENS Cleanable Quantity...Size (in.) 2...20 x 25 x 1 1...20 x 20 x 1 RETURN-AIR FILTERS Throwaway† Quantity...Size (in.) 4...20 x 20 x 2 4...16 x 20 x 2 LEGEND *Circuit 1 uses the lower portion of condenser coil and lower portion of evaporator coils, and Circuit 2 uses the upper portion of both coils. Al — Aluminum †The 50TJ028 units requires 2-in. industrial-grade filters capable of handling face Bhp — Brake Horsepower velocities of up to 625 ft/min (such as American Air Filter no. 5700 or equivalent). Cu — Copper DEC — Design Enhancement Center TXV — Thermostatic Expansion Valve 6
7 | Physical data (cont) OPERATING AND RIGGING WEIGHTS BASE UNIT OPERATING WEIGHTS* UNIT 016 024 028 lb kg lb kg lb kg 50TJ 1560 708 1800 816 1950 885 *Base unit weight does not include electric heaters, copper coils, economizer, power exhaust, barometric relief or crating. See Options and Accessory Weights table below for more information. NOTE: For export crating add 500 lb (227 kg). OPTION AND ACCESSORY WEIGHTS OPTION/ACCESSORY WEIGHTS OPTION/ACCESSORY 016 024 028 lb kg lb kg lb kg Electric Heater 50 23 50 23 50 23 Cu Condenser Coil 150 68 150 68 150 68 Cu Condenser and Evaporator Coils 280 127 280 127 280 127 Economizer 110 50 110 50 110 50 Barometric Relief Damper 50 23 50 23 50 23 Power Exhaust 85 39 85 39 85 39 Roof Curb (14-in. curb) 200 91 200 91 200 91 Horizontal Adapter Curb (pre-assembled) 250 113 250 113 250 113 Horizontal Adapter Cube (field-assembled) 343 156 343 156 343 156 Hail Guard 60 27 60 27 60 27 Glycol Coil 144 65 144 65 144 65 LEGEND Cu — Copper 7
8 | Options and accessories ITEM OPTION* ACCESSORY† Apollo Direct Digital Communicating Controls X Service Option Package X Integrated Economizer X X Electric Heat** (400-3-50 Units Only) X X Enviro-Shield™ Condenser Coil Options X Hail Guard Condenser Coil Grille X Alternate Drive X Electronic Programmable Thermostat X 25% Open Two-Position Damper X Barometric Relief Damper** X Roof Curbs X Horizontal Adapter Curb X Thermostats and Subbases X Power Exhaust** X Low-Ambient Kit X Winter Start Time-Delay Relay X Motormaster® III Head Pressure Control (Speed Control) X Time Guard® II Control Circuit X Accusensor™ III Enthalpy Sensor X Hydronic Glycol Coil X *Factory-installed. †Field-installed. **Not available with horizontal adapter curb. NOTE: Refer to 50TJ product ordering data or contact your local representative for accessory and option package information. HEAD PRESSURE CONTROL The 50TJ016-028 standard units are designed to operate in cooling at out- door temperatures down to 40 F (4.4 C). With accessory Motormaster III con- trol (condenser fan speed modulation) units can operate at outdoor temperatures down to –20 F (–28.9 C). The head pressure controls, which mount in the condenser section, control the condenser-fan motor to maintain correct condensing temperature. Refer to product ordering data or contact your local Carrier representative for appropriate accessory combinations for desired outdoor ambient temperature operation. MOTORMASTER III CONTROL 8
9 | FACTORY-INSTALLED APOLLO ACCUSENSOR™ III COMMUNICATING CONTROLS (Enthalpy and Differential Enthalpy Control) + Accusensor economizer controls help provide efficient, economical economizer operation. The unit economizer provides the decision- making function internally, and requires one Accusensor III sensor for solid-state enthalpy sensing. A second Accusensor III sensor The Apollo direct digital controls are designed exclusively by provides information for comparison of outdoor temperature and Carrier, and are used to actively monitor and control all modes of humidity to return-air temperature and humidity and determines the operation as well as to monitor evaporator-fan status, filter status, most economical mixture of air (purchased in addition to first solid- supply-air temperature, outdoor-air temperature, and indoor-air state enthalpy sensor for differential enthalpy sensing for all units). quality. They are designed to work in conjunction with Carrier TEMP and VVT® (Variable Volume/Variable Temperature) system thermostats. CARRIER COMMERCIAL THERMOSTAT ELECTRONIC PROGRAMMABLE THERMOSTAT Carrier’s electronic programmable thermostat provides efficient temperature control by allowing you to program heating and cooling setbacks and set ups with provi- Designed specifically for use with Carrier commercial systems, this sions for weekends and holidays. Accessory remote Carrier programmable thermostat features LED occupied/unoccupied sensing package is also available to provide tamper- displays and setback mode which can override continuous fan operation. proof control in high traffic spaces. Used in conjunction with factory-installed Apollo control, this thermostat provides a 5-minute recycle timer between modes of operation for short-cycle protection. TIME GUARD® II CONTROL Time Guard II Control automatically prevents compressor from restarting for at least 5 minutes after a shutdown. Accessory pre- vents short cycling of compressor if thermostat is changed rapidly. Time Guard II control mounts in the control compartment of unit. 9
10 | Options and accessories (cont) ELECTRIC HEATERS BAROMETRIC RELIEF/POWER EXHAUST When used with accessory/optional economizer, the barometric relief or power exhaust accessory helps to relieve building overpressurization. Electric heaters (and single point kits) are available in a wide NOTE: This is not available with horizontal supply adapter curb. range of capacities for factory or field installation. Electric heat- ers are available on 400-3-50 units only. GLYCOL COIL CARRIER DEBONAIR® THERMOSTAT Carrier ® Pm COOL AUTO HEAT Glycol coil is intended for add-on type applications or new work where a boiler system is available. Glycol coil and electric heat can- not be installed together. Carrier’s Debonair line of commercial programmable thermostats are wall-mounted, low-voltage thermostats which maintain room temperature by controlling operation of an HVAC (Heating, Ventila- tion, and Air-Conditioning) system. Separate heating and cooling set points and autochangeover capability allow occupied and unoc- cupied programming for energy savings. ENVIRO-SHIELD™ CONDENSER COIL OPTIONS Condenser coil options are available to match coil construction to site conditions for the best corrosion durability. Pre-coated coils pro- vide protection in mild coastal environments. All copper coils are best suited for moderate coastal applications, while post-coated coils provide superior protection in severe coastal and industrial applications. CONDENSER COIL PROTECTION APPLICATIONS ENVIRONMENT* DESCRIPTION Combined (Enviro-Shield Option) Standard, Mild Moderate Severe Industrial Coastal and Non-Corrosive Coastal Coastal Coastal Industrial Standard, Al/Cu X Pre-Coated Al/Cu X Cu/Cu X E-Coated Al/Cu X E-Coated Cu/Cu X X LEGEND Al/Cu — Aluminum Fin with Copper Tube Coil Cu/Cu — Copper Fin with Copper Tube Coil Enviro-Shield — Family of Coil Protection Options Pre-Coated — Epoxy Coating Applied to Fin Stock Material *See “Selection Guide: Environmental Corrosion Protection” Catalog No. 811-217 for more information. 10
11 | SERVICE OPTION PACKAGE* UNIT-MOUNTED DISCONNECT HINGED ACCESS PANEL (CONTROL BOX SHOWN) Factory-installed, internally-mounted, NEC (National Electrical Code, U.S.A.) and UL (Underwriters’ Laboratories, U.S.A.) approved non-fused switch provides unit power shutoff with disconnect lockout protection capability. The control box access door is interlocked with the non-fused disconnect. The non-fused disconnect must be in the OFF position to open this door. The switch is accessible from out- side the unit. *These options are also available individually through the DEC. 11
12 | Base unit dimensions — 50TJ016 NOTES: 1. Refer to print for roof curb accessory dimensions. 2. Dimensions in ( ) are in millimeters. 3. Center of Gravity. 4. Direction of airflow. 5. Ductwork to be attached to accessory roof curb only. 6. Minimum clearance: (cid:127) Rear, 7′-0″ (2134) for coil removal. This dimension can be reduced to 4′-0″ (1219) if conditions permit coil removal from the top. (cid:127) Left side: 4′-0″ (1219) for proper condenser coil airflow. (cid:127) Front, 4′-0″ (1219) for control box access. (cid:127) Right side: 4′-0″ (1219) for proper operation of damper and power exhaust if so equipped. (cid:127) Top, 6′-0″ (1829) to assure proper condenser fan operation. (cid:127) Local codes or jurisdiction may prevail. 7. With the exception of clearance for the condenser coil and the damper/power exhaust as stated in Note 6, a removable fence or barricade requires no clearance. 8. Dimensions are from outside of corner post. Allow 0′-5/16 ″ (8) on each side for top cover drip edge. 9. A 90 degree elbow must be installed on the supply ductwork below the unit discharge for units equipped with electric heaters. STD. UNIT ECONOMIZER CORNER CORNER CORNER CORNER DIM A DIM B DIM C UNIT WEIGHT WEIGHT A B C D ft-in. (mm) 1560 lbs 110 lbs 392 lbs 366 lbs 387 lbs 416 lbs 3-5 3-6 1-8 50TJ016 708 kg 50 kg 178 kg 166 kg 176 kg 188 kg (1041) (1067) (508) 12
13 | Base unit dimensions — 50TJ024,028 LEGEND KO — Knockout NOTES: 1. Dimensions in ( ) are in millimeters. 2. Center of gravity. 3. Direction of airflow. 4. Ductwork to be attached to accessory roof curb only. 5. Minimum clearance: a. Rear: 7′-0″ (2134) for coil removal. This dimension can be reduced to 4′-0″ (1219) if conditions permit coil removal from the top. b. Left side: 4′-0″ (1219) for proper condenser coil airflow. c. Front: 4′-0″ (1219) for control box access. d. Right side: 4′-0″ (1219) for proper operation of damper and power exhaust (if so equipped). e. Top: 6′-0″ (1829) to assure proper condenser fan operation. f. Local codes or jurisdiction may prevail. 6. With the exception of clearance for the condenser coil and the damper/power exhaust as stated in Note 5, a removable fence or barricade requires no clearance. 7. Dimensions are from outside of corner post. Allow 0′-5/16 ″ (8) on each side for top cover drip edge. 8. A 90 degree elbow must be installed on the supply ductwork below the unit discharge for units equipped with electric heaters. CORNER WEIGHT* DIMENSIONS UNIT A B C D X Y 50TJ Lb Kg Lb Kg Lb Kg Lb Kg Ft-in. mm Ft-in. mm 024 423 192 412 185 490 220 475 213 3-3 991 3-7 1092 028 441 200 416 189 533 242 560 254 3-1 940 3-6 1067 (Standard) 028 441 200 416 189 553 251 580 263 3-1 940 3-6 1067 (High Static Option) *Weights are for unit only (aluminum plate fins) and do not include options or crating. 13
14 | Accessory dimensions HORIZONTAL AND VERTICAL ROOF CURBS AND HORIZONTAL ADAPTER CURB NOTES: 1. Roof curb accessory is shipped unassembled. 2. Insulated panels, 1″ thick neoprene coated, 11/2 lb density. 3. Dimensions in ( ) are in millimeters. 4. Direction of airflow. NOTE: To prevent the hazard of stagnant water build-up in the drain pan of the indoor section, unit can only be pitched as 5. Roof curb: 16 ga. (VA03-56) steel. shown. LEGEND COMPR SECT. — Compressor Section CURB PKG. NO. REF. DESCRIPTION HEIGHT 1′-2″ Standard curb DIMENSIONS (degrees and inches) CRRFCURB010A00 (305) 14” high CRRFCURB011A00 2′-0″ St u a n n it d s a r r e d q c u u ir r i b n g for UNIT DEG. A IN. DEG. B IN. (610) high installation 50TJ .28 .45 .28 .43 CRRBCURB012A00 2′-0″ S r i e d t e u r s n u c p u p r ly b a fo n r d UNIT LEVELING TOLERANCES* (610) high installation *From edge of unit to horizontal. 14
15 | HORIZONTAL SUPPLY/RETURN ADAPTER INSTALLATION NOTE: CRRFCURB013A00 is a fully factory preassembled horizontal adapter and includes an insulated high static regain transition duct which substantially improves fan static performance. The Barometric Relief Damper and Power Exhaust accessories are not available with the horizontal adapter. ACCESSORY CURB DESCRIPTION PACKAGE NO. HEIGHT 1′-11″ Pre-Assembled, High Static, CRRFCURB013A00 (584) Horizontal Adapter BAROMETRIC RELIEF/POWER EXHAUST 2'-1 5/8" (650.9) 2'-2 1/16" (662) 1'-6 5/16" (465.1) 15
16 | Accessory dimensions (cont) FACTORY-INSTALLED NON-FUSED DISCONNECT COMPRESSOR TOP CONTROL BOX DISCONNECT SECTION DOOR SECTION DOOR HANDLE 2'-5 1/4" (743) FRONT VIEW 1'-1 11/16" (347) 16
17 | Selection procedure (with 50TJ016 example) — SI I Determine cooling and heating requirements at Before entering the Fan Performance tables, calculate design conditions: the total static pressure required based on unit compo- nents. From the given find: Given: External static pressure . . . . . . . . . . . . . . . 164 Pa Cooling Capacity Required. . . . . . . . . . . . . . . 48 kW 22.5 kW Heater static pressure. . . . . . . . . 22 Pa Sensible Heating Capacity . . . . . . . . . . . . . . . 34 kW Condenser Entering-Air Temperature . . . . . 35 C Edb Total static pressure . . . . . . . . . . . . . . . . . . 186 Pa Evaporator Entering-Air Enter Fan Performance table for unit 50TJ016 on Temperature . . . . . . . . . . . 26.7 C Edb/19 C Ewb page 24, at 2833 L/s and 186 Pa external static pres- Evaporator Air Quantity. . . . . . . . . . . . . . . 2833 L/s sure. By interpolation, find that the fan speed is External Static Pressure . . . . . . . . . . . . . . . . .164 Pa 17.8 r/s and the watts are 2640. Heating Capacity . . . . . . . . . . . . . . . . . . . . . 22 kW V Determine net cooling capacity. Power Supply (V-Ph-Hz) . . . . . . . . . . . . . . 400-3-50 Cooling capacities are gross capacities and do not in- II Select unit based on required cooling clude indoor (evaporator) fan motor (IFM) heat. Use capacity. the watts input power to the motor calculated in Sec- Entering cooling capacity table for 50TJ016 on tion IV above. page 19 at condenser entering dry bulb temperature IFM watts = 2640 35 C, air entering evaporator at 2833 L/s, 26.7 C Determine net cooling capacity using the following edb and 19 C ewb. The 50TJ016 unit will provide a formula: total cooling capacity of 52.6 kW, and a sensible heat- ing capacity of 38.5 kW. For evaporator-air tempera- Net capacity = Gross capacity – IFM heat ture other than 26.7 C edb, calculate sensible heat ca- = 52.6 kW – 2.64 kW pacity correction as required using the formula in the = 50.0 kW notes following the Cooling Capacities tables. Net sensible capacity = 38.5 kW – 2.64 kW NOTE: Unit ratings are gross capacities and do not in- clude the effect of evaporator-fan motor heat. To cal- = 35.9 kW culate net capacities, see Step V. As demonstrated above, the 50TJ016 with a standard motor and standard low-medium static drive, and a III Select electric heat. 22.5 kW electric heater meets the cooling capacity, Heating load required is 22 kW. Enter the Electric Re- sensible heating capacity, and heating capacity require- sistance Heater Data table on page 4 for the 50TJ016 ments, and is the correct choice for the given at 400-3-50. The 22.5 kW electric heater most closely conditions. satisfies the heat required. NOTE: To obtain more sensible cooling, increase IV Determine fan speed and motor horsepower quantity of air entering evaporator. requirements at design conditions. Enter Accessory/FIOP Static Pressure table on page 31 at selected unit size and heater kW. Find that at given air quantity (2833 L/s), pressure loss is 22 Pa. 17
18 | Selection procedure (with 50TJ016 example) — English I Determine cooling and heating requirements at Before entering the Fan Performance tables, calculate design conditions: the total static pressure required based on unit compo- nents. From the given find: Given: External static pressure . . . . . . . . . . . . . .0.66 in. wg Cooling Capacity Required. . . . . . . . . .168,000 Btuh 22.5 kW Heater static pressure . . . . . . . 0.09 in. wg Sensible Heating Capacity . . . . . . . . . .118,000 Btuh Condenser Entering-Air Temperature . . . . . 95 F Edb Total static pressure. . . . . . . . . . . . . . . . .0.75 in. wg Evaporator Entering-Air Enter Fan Performance table for unit 50TJ016 on Temperature . . . . . . . . . . . . . 80 F Edb/67 F Ewb page 27, at 6000 cfm and 0.75 in. wg external static Evaporator Air Quantity. . . . . . . . . . . . . . . 6000 cfm pressure. By interpolation, find that the fan speed is External Static Pressure . . . . . . . . . . . . . .0.66 in. wg 1011 rpm and the watts are 2633. Heating Capacity . . . . . . . . . . . . . . . . .76,000 Btuh V Determine net cooling capacity. Power Supply (V-Ph-Hz) . . . . . . . . . . . . . . 400-3-50 Cooling capacities are gross capacities and do not in- II Select unit based on required cooling clude indoor (evaporator) fan motor (IFM) heat. Use capacity. the watts input power to the motor calculated in Sec- Entering cooling capacity table for 50TJ016 on tion IV above. page 21 at condenser entering dry bulb temperature IFM watts = 2633 95 F, air entering evaporator at 6000 cfm, 80 F edb Determine net cooling capacity using the following and 67 F ewb. The 50TJ016 unit will provide a total formula: cooling capacity of 180,000 Btuh, and a sensible heat- ing capacity of 131,000 Btuh. For evaporator-air tem- Net capacity = Gross capacity – IFM heat perature other than 80 F edb, calculate sensible heat = 180,000 – 2633 Watts capacity correction as required using the formula in the (3.413 Btuh/Watt) notes following the Cooling Capacities tables. = 180,000 Btuh – 8986 Btuh NOTE: Unit ratings are gross capacities and do not in- = 171,014 Btuh clude the effect of evaporator-fan motor heat. To cal- culate net capacities, see Step V. Net sensible capacity = 131,000 Btuh – 8986 Btuh = 122,014 Btuh III Select electric heat. As demonstrated above, the 50TJ016 with a standard Heating load required is 76,000 Btuh. motor and standard low-medium static drive, and a 76,000 Btuh 22.5 kW electric heater, satisfies the cooling capacity, = 22,274 Watts of heat required. 3.413 Btu/W sensible heating capacity, and heating capacity require- ments, and is the correct choice for the given = 22.3 kW conditions. Enter the Electric Resistance Heater Data table on NOTE: To obtain more sensible cooling, increase page 4 for the 50TJ016 at 400-3-50. The 22.5 kW quantity of air entering evaporator. electric heater most closely satisfies the heat required. IV Determine fan speed and motor horsepower requirements a design conditions. Enter Accessory/FIOP Static Pressure table on page 31 at selected unit size and heater kW. Find that at given air quantity (6000 cfm), pressure loss is 0.09 in. wg. 18
19 | Performance data COOLING CAPACITIES — SI 50TJ016 (52.8 kW) Evaporator Air Quantity — L/s / BF Temp (C) Air Entering 2124/0.12 2478/0.14 2832/0.15 3186/0.17 3540/0.18 Condenser Evaporator Air — Ewb (C) (Edb) 17 19 22 17 19 22 17 19 22 17 19 22 17 19 22 TC 49.0 53.3 58.7 50.3 54.9 60.3 51.8 56.5 61.3 52.8 57.1 61.9 53.9 57.6 62.4 24 SHC 41.6 35.5 28.8 45.1 37.8 30.6 47.5 40.1 32.0 50.2 43.1 34.7 52.7 45.2 36.6 kW 11.3 11.7 13.3 11.5 11.9 13.4 11.6 12.0 13.5 11.7 12.0 13.6 11.7 12.1 13.6 TC 47.6 51.7 56.5 49.0 53.3 58.1 50.2 54.4 59.7 51.2 55.5 60.3 52.1 56.0 61.3 29 SHC 40.8 34.7 28.2 44.0 37.1 29.7 46.7 39.3 31.2 49.4 41.4 33.1 51.7 44.2 33.8 kW 12.7 13.0 14.7 12.8 13.2 14.9 12.9 13.3 15.0 13.0 13.4 15.1 13.1 13.5 15.2 TC 46.0 50.1 54.9 47.4 51.5 56.5 48.5 52.6 57.6 49.4 53.3 58.7 50.4 54.4 59.2 35 SHC 40.0 33.8 27.4 43.1 36.2 28.9 45.9 38.5 30.3 48.5 40.6 31.5 50.4 42.8 33.0 kW 14.1 14.5 16.3 14.3 14.6 16.5 14.4 14.7 16.6 14.5 14.9 16.7 14.6 15.0 16.8 TC 43.5 47.3 51.8 44.7 48.5 52.9 45.7 49.5 53.9 46.6 50.3 55.0 47.7 51.0 55.5 40.5 SHC 38.2 32.4 26.2 41.2 34.7 27.6 44.0 36.8 28.9 46.4 38.9 30.0 47.9 41.0 31.4 kW 15.7 16.2 18.1 15.9 16.3 18.3 16.0 16.4 18.4 16.1 16.5 18.5 16.2 16.6 18.6 TC 40.8 44.4 48.7 41.9 45.5 49.9 42.7 46.4 50.5 43.9 47.1 51.0 44.9 47.6 51.9 46 SHC 36.5 31.0 24.9 39.5 33.2 26.3 42.2 35.3 27.6 44.1 37.2 28.7 45.2 39.2 30.5 kW 17.4 17.9 18.4 17.6 18.0 18.6 17.7 18.1 18.7 17.9 18.3 18.7 18.0 18.3 18.8 TC 39.0 42.4 46.6 40.0 43.5 47.7 40.9 44.3 48.4 42.0 45.0 48.8 43.0 45.5 49.6 49 SHC 35.4 30.0 24.0 38.3 32.1 25.3 40.7 34.3 26.7 42.3 36.3 27.8 43.4 37.9 29.5 kW 18.4 18.9 19.4 18.5 19.0 19.6 18.7 19.1 19.8 18.8 19.2 19.8 18.9 19.3 19.8 TC 37.2 40.5 44.2 38.1 41.4 — 39.1 42.2 — 40.2 42.9 — 41.2 43.3 — 52 SHC 34.2 29.0 23.8 36.9 31.1 — 39.2 33.1 — 40.5 35.0 — 41.5 36.6 — kW 19.3 19.7 20.3 19.4 19.9 — 19.6 20.1 — 19.7 20.1 — 19.9 20.1 — 50TJ024 (70.3 kW) Evaporator Air Quantity — L/s / BF Temp (C) Air Entering 2832/0.075 3304/0.085 3776/0.100 4248/0.110 4720/0.120 Condenser Evaporator Air — Ewb (C) (Edb) 17 19 22 17 19 22 17 19 22 17 19 22 17 19 22 TC 64.3 70.9 76.9 65.9 72.7 78.8 67.2 74.1 80.3 68.4 75.0 81.3 69.7 75.8 82.2 24 SHC 55.1 46.5 36.9 59.5 49.7 38.9 63.6 53.0 40.8 67.2 56.0 42.8 69.6 59.1 44.5 kW 15.1 15.6 16.5 15.2 15.8 16.7 15.4 15.9 16.9 15.5 16.0 17.0 15.7 16.1 17.1 TC 62.1 68.5 74.3 63.6 70.2 76.1 64.9 71.4 77.5 66.0 72.3 78.5 67.8 73.1 79.3 29 SHC 54.0 45.4 36.0 58.4 48.8 38.0 62.4 51.9 39.9 65.6 54.8 41.7 67.6 57.9 43.5 kW 16.7 17.2 18.2 16.9 17.4 18.5 17.0 17.6 18.6 17.2 17.7 18.7 17.4 17.8 18.8 TC 59.8 65.9 71.6 61.2 67.4 73.2 62.4 68.6 74.4 63.8 69.4 75.3 65.3 70.0 76.1 35 SHC 53.0 44.4 35.0 57.1 47.7 37.0 61.0 50.7 38.9 63.7 53.6 40.6 65.1 56.7 42.4 kW 18.5 19.0 20.1 18.7 19.2 20.3 18.8 19.3 20.4 19.0 19.4 20.5 19.1 19.5 20.6 TC 57.0 63.0 68.5 58.4 64.4 70.0 59.7 65.3 71.1 61.4 66.1 71.9 62.8 66.7 72.7 40.5 SHC 51.6 43.3 33.9 55.8 46.5 35.9 59.3 49.4 37.7 61.3 52.6 39.5 62.6 55.4 41.3 kW 20.3 20.8 22.0 20.5 21.0 22.2 20.6 21.1 22.3 20.8 21.2 22.4 21.0 21.3 22.6 TC 54.2 59.9 65.2 55.6 61.2 66.6 57.1 62.1 67.6 58.7 62.7 68.3 60.0 63.2 68.9 46 SHC 50.2 42.0 32.8 54.3 45.3 34.7 56.9 48.3 36.5 58.6 51.1 38.3 59.8 53.7 40.0 kW 22.1 22.7 23.9 22.3 22.8 24.1 22.5 23.0 24.2 22.7 23.1 24.3 22.9 23.2 24.4 TC 51.2 56.6 — 52.7 57.6 — 54.3 58.4 — 55.9 59.0 — 57.0 59.4 — 52 SHC 48.7 40.7 — 52.3 43.8 — 54.2 47.0 — 55.7 49.6 — 56.9 52.1 — kW 24.0 24.6 — 24.2 24.7 — 24.4 24.9 — 24.6 25.0 — 24.8 25.0 — LEGEND 4. Formulas: BF — Bypass Factor SHCkW x 1000 Edb — Entering Dry Bulb Temperature (C) Cldb = Cedb – 1.23 x L/s Ewb — Entering Wet Bulb Temperature (C) kW — Compressor Input (kW) Leaving wet bulb = wet bulb temperature corresponding to SHC — Sensible Heat Capacity (kW) enthalpy of air leaving coil (hlwb). TC — Total Capacity (kW) TCkW x 1000 hlwb = hewb – NOTES: 1.20 x L/s 1. Ratings are gross, and do not account for the effects of the evaporator-fan motor power and heat. Where hewb is enthalpy of air entering evaporator coil (kJ/kg). 2. Direct interpolation is permissible. Do not extrapolate. 3. SHC is based on 26.7 C db temperature of air entering the unit. At any other temperature, correct the SHC read from the table of cooling capacities as follows: Corrected SHCkW = SHC + [1.23 x 10–3 x (1 – BF) x (Cdb – 26.7) x L/s] Observe the rule of sign. Above 26.7 C, SHC correction will be positive; add it to SHC. Below 26.7 C, SHC correction will be nega- tive; subtract it from SHC. 19
20 | Performance data (cont) COOLING CAPACITIES — SI (cont) 50TJ028 (87.9 kW) (Standard Fan) Evaporator Air Quantity — L/s / BF Temp (C) Air Entering 3304/0.05 3776/0.06 4248/0.07 4720/0.08 5310/0.09 Condenser Evaporator Air — Ewb (C) (Edb) 17 19 22 17 19 22 17 19 22 17 19 22 17 19 22 TC 79.4 87.6 96.5 81.2 89.6 98.6 82.7 91.0 100.3 83.9 91.9 101.6 85.7 93.4 102.6 24 SHC 67.7 57.2 46.5 72.6 60.7 48.4 77.5 64.4 51.2 81.7 68.7 53.3 85.6 72.6 56.9 kW 20.1 20.8 21.6 20.3 21.0 21.8 20.4 21.2 22.0 20.6 21.3 22.2 20.8 21.5 22.3 TC 76.6 84.5 93.1 78.3 86.4 95.0 79.8 88.0 96.6 81.0 89.1 98.1 83.1 90.4 99.1 29 SHC 66.5 55.9 45.0 71.2 59.4 47.4 75.6 62.9 49.4 79.7 66.4 51.6 83.0 70.5 54.5 kW 22.2 23.0 23.8 22.4 23.2 24.0 22.6 23.4 24.2 22.8 23.5 24.4 23.0 23.7 24.5 TC 73.7 81.2 89.4 75.2 83.0 91.1 76.7 84.2 92.7 78.1 85.5 94.0 80.3 86.6 95.2 35 SHC 65.0 54.6 44.0 69.7 58.1 46.0 74.1 61.8 48.1 77.7 64.8 50.1 80.2 68.9 53.0 kW 24.6 25.3 26.1 24.7 25.5 26.3 24.9 25.7 26.5 25.1 25.8 26.7 25.4 26.0 26.9 TC 70.5 77.8 85.4 71.9 79.2 87.2 73.5 80.4 88.6 75.0 81.4 89.6 77.2 82.5 90.4 40.5 SHC 63.3 53.3 42.6 68.0 56.5 44.7 72.0 60.1 46.6 75.0 63.3 48.8 77.1 67.2 51.6 kW 27.0 27.8 28.6 27.2 28.0 28.8 27.4 28.1 29.0 27.6 28.3 29.2 27.9 28.4 29.3 TC 67.1 74.0 81.2 68.4 75.3 82.5 70.0 76.4 83.6 71.9 77.3 — 73.8 78.2 — 46 SHC 61.9 51.8 41.0 66.2 55.0 43.1 69.8 58.4 44.9 71.8 61.7 — 73.8 65.4 — kW 29.5 30.3 31.1 29.7 30.5 31.3 30.0 30.7 31.5 30.2 30.8 — 30.5 31.0 — TC 66.1 72.7 — 67.4 73.9 — 68.9 74.8 — 70.6 75.5 — 72.4 — — 48 SHC 61.4 51.3 — 65.6 54.5 — 68.8 57.8 — 70.5 61.1 — 72.4 — — kW 30.3 31.1 — 30.5 31.2 — 30.7 31.4 — 31.0 31.5 — 31.2 — — TC 65.2 — — 66.6 — — 68.4 — — 70.0 — — — — — 49 SHC 60.9 — — 65.2 — — 68.4 — — 70.0 — — — — — kW 30.8 — — 31.0 — — 31.3 — — 31.5 — — — — — 50TJ028 (87.9 kW) (Optional High-Static Fan) Evaporator Air Quantity — L/s / BF Temp (C) Air Entering 3304/0.05 3776/0.06 4248/0.07 4720/0.08 5310/0.09 Condenser Evaporator Air — Ewb (C) (Edb) 17 19 22 17 19 22 17 19 22 17 19 22 17 19 22 TC 82.3 90.8 100.5 84.4 93.2 102.8 85.6 94.6 104.0 87.3 95.8 105.8 89.1 97.3 107.2 24 SHC 69.1 58.8 47.8 74.1 62.6 50.3 79.7 66.9 54.3 83.2 70.2 56.6 87.9 75.3 59.9 kW 18.2 18.8 19.4 18.4 19.0 19.6 18.5 19.1 19.7 18.6 19.2 19.9 18.8 19.4 20.0 TC 79.7 87.9 97.3 81.7 90.5 99.6 83.2 92.0 101.7 84.7 93.2 102.8 86.7 94.3 104.0 29 SHC 68.0 57.4 46.6 73.0 61.1 49.1 77.6 65.0 51.4 81.7 68.0 53.7 85.8 73.2 57.3 kW 20.3 20.8 21.5 20.4 21.0 21.7 20.6 21.2 21.8 20.8 21.4 22.0 20.9 21.4 22.1 TC 76.8 85.3 93.8 78.5 87.0 95.8 80.3 88.5 97.6 81.7 90.0 99.0 83.5 91.1 100.5 35 SHC 66.5 56.2 45.6 71.5 59.7 47.8 75.6 63.1 49.9 79.4 66.6 52.0 82.9 70.6 54.8 kW 22.6 23.1 23.7 22.6 23.3 23.9 22.8 23.4 24.1 23.0 23.6 24.2 23.1 23.6 24.4 TC 73.8 81.7 90.0 75.6 83.5 91.7 77.1 85.0 93.5 78.5 86.1 94.6 80.9 87.0 95.8 41 SHC 65.1 54.7 44.2 69.6 58.5 46.4 74.1 61.6 48.4 77.4 65.0 50.5 80.6 69.4 53.2 kW 24.9 25.5 26.1 25.0 25.7 26.3 25.2 25.8 26.5 25.3 25.9 26.5 25.5 26.0 26.7 TC 70.3 77.9 85.6 72.1 79.7 87.6 73.8 80.9 88.8 75.6 81.7 90.2 77.6 82.9 91.1 46 SHC 63.5 53.3 42.7 68.0 57.0 44.8 71.8 60.4 47.0 75.0 63.5 49.5 77.4 67.8 51.5 kW 27.3 27.9 28.5 27.5 28.1 28.7 27.7 28.3 28.9 27.8 28.3 28.9 28.0 28.5 29.1 TC 67.0 73.8 81.5 68.6 75.6 82.9 70.3 76.5 84.1 71.8 77.4 85.3 73.8 77.9 86.4 52 SHC 61.8 51.9 41.2 66.1 55.4 43.2 69.1 58.5 45.3 71.8 61.6 47.1 73.8 65.6 49.7 kW 29.9 30.4 31.1 30.0 30.6 31.2 30.2 30.7 31.3 30.4 30.7 31.5 30.6 30.9 31.6 LEGEND 4. Formulas: BF — Bypass Factor SHCkW x 1000 Edb — Entering Dry Bulb Temperature (C) Cldb = Cedb – 1.23 x L/s Ewb — Entering Wet Bulb Temperature (C) kW — Compressor Input (kW) Leaving wet bulb = wet bulb temperature corresponding to SHC — Sensible Heat Capacity (kW) enthalpy of air leaving coil (hlwb). TC — Total Capacity (kW) TCkW x 1000 hlwb = hewb – NOTES: 1.20 x L/s 1. Ratings are gross, and do not account for the effects of the evaporator-fan motor power and heat. Where hewb is enthalpy of air entering evaporator coil (kJ/kg). 2. Direct interpolation is permissible. Do not extrapolate. 3. SHC is based on 26.7 C db temperature of air entering the unit. At any other temperature, correct the SHC read from the table of cooling capacities as follows: Corrected SHCkW = SHC + [1.23 x 10–3 x (1 – BF) x (Cdb – 26.7) x L/s] Observe the rule of sign. Above 26.7 C, SHC correction will be positive; add it to SHC. Below 26.7 C, SHC correction will be nega- tive; subtract it from SHC. 20
21 | COOLING CAPACITIES — ENGLISH 50TJ016 (15 TONS) Evaporator Air Quantity — Cfm / BF Temp (F) Air Entering 4500/0.12 5250/0.14 6000/0.15 6750/0.17 7500/0.18 Condenser Evaporator Air — Ewb (F) (Edb) 62 67 72 62 67 72 62 67 72 62 67 72 62 67 72 TC 167 182 200 172 188 206 177 193 209 180 195 211 184 197 213 75 SHC 142 121 98 154 129 104 162 137 109 171 147 118 180 154 125 kW 11.3 11.7 13.3 11.5 11.9 13.4 11.6 12.0 13.5 11.7 12.0 13.6 11.7 12.1 13.6 TC 162 177 193 167 182 198 171 186 204 175 189 206 178 191 209 85 SHC 139 118 96 150 126 101 159 134 107 168 141 113 176 151 116 kW 12.7 13.0 14.7 12.8 13.2 14.9 12.9 13.3 15.0 13.0 13.4 15.1 13.1 13.5 15.2 TC 157 171 188 162 176 193 165 180 197 169 182 200 172 186 202 95 SHC 137 115 94 147 124 99 157 131 103 166 139 108 172 146 113 kW 14.1 14.5 16.3 14.3 14.6 16.5 14.4 14.7 16.6 14.5 14.9 16.7 14.6 15.0 16.8 TC 148 162 177 153 166 180 156 169 184 159 172 188 163 174 189 105 SHC 130 111 89 140 119 94 150 126 99 158 133 103 163 140 107 kW 15.7 16.2 18.1 15.9 16.3 18.3 16.0 16.4 18.4 16.1 16.5 18.5 16.2 16.6 18.6 TC 139 152 166 143 155 170 146 158 173 150 161 174 153 163 177 115 SHC 125 106 85 135 113 90 144 121 94 150 127 98 154 134 104 kW 17.4 17.9 18.4 17.6 18.0 18.6 17.7 18.1 18.7 17.9 18.3 18.7 18.0 18.3 18.8 TC 133 145 159 136 148 163 140 151 165 143 154 166 147 155 169 120 SHC 121 102 82 131 110 86 139 117 91 144 124 95 148 129 101 kW 18.4 18.9 19.4 18.5 19.0 19.6 18.7 19.1 19.8 18.8 19.2 19.8 18.9 19.3 19.8 TC 127 138 151 130 141 — 134 144 — 137 146 — 140 148 — 125 SHC 117 99 81 126 106 — 134 113 — 138 119 — 142 125 — kW 19.3 19.7 20.3 19.4 19.9 — 19.6 20.1 — 19.7 20.1 — 19.9 20.1 — 50TJ024 (20 TONS) Evaporator Air Quantity — Cfm / BF Temp (F) Air Entering 6000/0.075 7000/0.085 8000/0.10 9000/0.11 10,000/0.12 Condenser Evaporator Air — Ewb (F) (Edb) 62 67 72 62 67 72 62 67 72 62 67 72 62 67 72 TC 219.5 242.0 262.6 224.9 248.0 268.8 229.2 252.8 274.0 233.3 256.1 277.5 238.0 258.8 280.5 75 SHC 188.0 158.6 125.9 203.2 169.6 132.7 217.0 180.7 139.3 229.5 191.1 146.1 237.6 201.7 152.0 kW 15.1 15.6 16.5 15.2 15.8 16.7 15.4 15.9 16.9 15.5 16.0 17.0 15.7 16.1 17.1 TC 211.9 233.6 253.5 217.1 239.6 259.8 221.4 243.8 264.6 225.2 246.8 267.9 231.3 249.5 270.6 85 SHC 184.5 154.9 122.7 199.3 166.7 129.6 212.9 177.0 136.1 224.0 187.2 142.3 230.7 197.6 148.5 kW 16.7 17.2 18.2 16.9 17.4 18.5 17.0 17.6 18.6 17.2 17.7 18.7 17.4 17.8 18.8 TC 204.1 224.9 244.2 208.8 229.9 249.8 213.0 234.0 253.9 217.6 236.8 256.9 222.9 239.1 259.7 95 SHC 180.8 151.7 119.4 194.9 162.7 126.3 208.3 173.2 132.7 217.2 183.0 138.7 222.4 193.4 144.8 kW 18.5 19.0 20.1 18.7 19.2 20.3 18.8 19.3 20.4 19.0 19.4 20.5 19.1 19.5 20.6 TC 194.5 215.0 233.7 199.5 219.8 238.9 203.8 223.0 242.7 209.6 225.6 245.5 214.3 227.6 248.0 105 SHC 176.2 147.8 115.7 190.4 158.7 122.5 202.5 168.7 128.8 209.3 179.6 134.9 213.8 189.0 141.0 kW 20.3 20.8 22.0 20.5 21.0 22.2 20.6 21.1 22.3 20.8 21.2 22.4 21.0 21.3 22.6 TC 185.1 204.6 222.6 189.8 208.9 227.3 194.8 211.8 230.6 200.4 214.0 233.2 204.6 215.8 235.2 115 SHC 171.5 143.3 111.9 185.2 154.7 118.5 194.3 164.9 124.5 199.9 174.3 130.7 204.2 183.3 136.6 kW 22.1 22.7 23.9 22.3 22.8 24.1 22.5 23.0 24.2 22.7 23.1 24.3 22.9 23.2 24.4 TC 174.9 193.1 — 179.9 196.7 — 185.3 199.5 — 190.6 201.4 — 194.7 202.8 — 125 SHC 166.2 138.7 — 178.5 149.5 — 184.9 160.3 — 190.2 169.4 — 194.0 177.7 — kW 24.0 24.6 — 24.2 24.7 — 24.4 24.9 — 24.6 25.0 — 24.8 25.0 — LEGEND 4. Formulas: BF — Bypass Factor SHCBtuh Edb — Entering Dry Bulb Temperature (F) Fldb = Fedb – 1.09 x cfm Ewb — Entering Wet Bulb Temperature (F) kW — Compressor Motor Power Input Leaving wet bulb = wet bulb temperature corresponding to SHC — Sensible Heat Capacity (1000 Btuh) enthalpy of air leaving coil (hlwb). TC — Total Capacity (1000 Btuh) TCBtuh hlwb = hewb – NOTES: 4.50 x cfm 1. Ratings are gross, and do not account for the effects of the evaporator-fan motor power and heat. Where hewb is enthalpy of air entering evaporator coil (Btu/lb). 2. Direct interpolation is permissible. Do not extrapolate. 3. SHC is based on 80 F db temperature of air entering the unit. At any other temperature, correct the SHC read from the table of cooling capacities as follows: Corrected SHCBtuh = SHC + [1.10 x (1 – BF) x (Fdb – 80) x cfm] Observe the rule of sign. Above 80 F, SHC correction will be posi- tive; add it to SHC. Below 80 F, SHC correction will be negative; subtract it from SHC. 21
22 | Performance data (cont) COOLING CAPACITIES — ENGLISH (cont) 50TJ028 (25 TONS) (Standard Fan) Evaporator Air Quantity — Cfm/BF Temp (F) Air Entering 7000/0.05 8000/0.06 9000/0.07 10,000/0.08 11,250/0.09 Condenser Evaporator Air — Ewb (F) (Edb) 62 67 72 62 67 72 62 67 72 62 67 72 62 67 72 TC 270.9 298.9 329.5 277.1 305.7 336.5 282.2 310.5 342.2 286.2 313.6 346.8 292.5 318.6 350.0 75 SHC 231.2 195.1 158.8 247.7 207.1 165.1 264.4 219.8 174.6 278.8 234.5 181.9 292.1 247.9 194.1 kW 20.1 20.8 21.6 20.3 21.0 21.8 20.4 21.2 22.0 20.6 21.3 22.2 20.8 21.5 22.3 TC 261.5 288.5 317.7 267.1 295.0 324.2 272.5 300.2 329.8 276.5 304.2 334.8 283.5 308.4 338.2 85 SHC 226.8 190.8 153.6 243.1 202.9 161.9 257.9 214.6 168.8 272.2 226.7 176.0 283.3 240.5 185.9 kW 22.2 23.0 23.8 22.4 23.2 24.0 22.6 23.4 24.2 22.8 23.5 24.4 23.0 23.7 24.5 TC 251.5 277.2 305.1 256.6 283.3 311.0 261.9 287.3 316.5 266.4 291.9 320.8 274.0 295.4 325.0 95 SHC 221.8 186.4 150.1 237.9 198.3 157.1 252.7 211.0 164.2 265.2 221.3 171.0 273.7 235.0 181.0 kW 24.6 25.3 26.1 24.7 25.5 26.3 24.9 25.7 26.5 25.1 25.8 26.7 25.4 26.0 26.9 TC 240.6 265.7 291.4 245.5 270.5 297.8 250.7 274.6 302.2 256.0 277.9 305.7 263.4 281.4 308.6 105 SHC 215.9 181.8 145.2 231.9 192.9 152.5 245.8 205.0 159.2 255.9 216.1 166.5 263.2 229.5 176.0 kW 27.0 27.8 28.6 27.2 28.0 28.8 27.4 28.1 29.0 27.6 28.3 29.2 27.9 28.4 29.3 TC 229.0 252.4 277.3 233.5 256.9 281.5 239.0 260.6 285.4 245.2 263.7 — 252.0 267.0 — 115 SHC 211.2 176.8 140.0 225.9 187.6 147.1 238.3 199.4 153.4 245.0 210.6 — 251.9 223.2 — kW 29.5 30.3 31.1 29.7 30.5 31.3 30.0 30.7 31.5 30.2 30.8 — 30.5 31.0 — TC 225.6 248.0 — 230.0 252.3 — 235.1 255.3 — 240.9 257.5 — 247.2 — — 118 SHC 209.6 175.1 — 223.9 186.0 — 234.7 197.4 — 240.5 208.6 — 247.1 — — kW 30.3 31.1 — 30.5 31.2 — 30.7 31.4 — 31.0 31.5 — 31.2 — — TC 222.6 — — 227.4 — — 233.6 — — 239.0 — — — — — 120 SHC 208.0 — — 222.5 — — 233.3 — — 239.0 — — — — — kW 30.8 — — 31.0 — — 31.3 — — 31.5 — — — — — 50TJ028 (25 TONS) (Optional High-Static Fan) Evaporator Air Quantity — Cfm/BF Temp (F) Air Entering 7000/0.05 8000/0.06 9000/0.07 10,000/0.08 11,250/0.09 Condenser Evaporator Air — Ewb (F) (Edb) 62 67 72 62 67 72 62 67 72 62 67 72 62 67 72 TC 281 310 343 288 318 351 292 323 355 298 327 361 304 332 366 75 SHC 236 201 163 253 214 172 272 228 185 284 240 193 300 257 204 kW 18.2 18.8 19.4 18.4 19.0 19.6 18.5 19.1 19.7 18.6 19.2 19.9 18.8 19.4 20.0 TC 272 300 332 279 309 340 284 314 347 289 318 351 296 322 355 85 SHC 232 196 159 249 209 168 265 222 176 279 232 183 293 250 196 kW 20.3 20.8 21.5 20.4 21.0 21.7 20.6 21.2 21.8 20.8 21.4 22.0 20.9 21.4 22.1 TC 262 291 320 268 297 327 274 302 333 279 307 338 285 311 343 95 SHC 227 192 156 244 204 163 258 216 170 271 227 178 283 241 187 kW 22.6 23.1 23.7 22.6 23.3 23.9 22.8 23.4 24.1 23.0 23.6 24.2 23.1 23.6 24.4 TC 252 279 307 258 285 313 263 290 319 268 294 323 276 297 327 105 SHC 222 187 151 238 200 158 253 210 165 264 222 172 275 237 182 kW 24.9 25.5 26.1 25.0 25.7 26.3 25.2 25.8 26.5 25.3 25.9 26.5 25.5 26.0 26.7 TC 240 266 292 246 272 299 252 276 303 258 279 308 265 283 311 115 SHC 217 182 146 232 194 153 245 206 160 256 217 169 264 231 176 kW 27.3 27.9 28.5 27.5 28.1 28.7 27.7 28.3 28.9 27.8 28.3 28.9 28.0 28.5 29.1 TC 229 252 278 234 258 283 240 261 287 245 264 291 252 266 295 125 SHC 211 177 141 226 189 148 236 200 155 245 210 161 252 224 170 kW 29.9 30.4 31.1 30.0 30.6 31.2 30.2 30.7 31.3 30.4 30.7 31.5 30.6 30.9 31.6 LEGEND 4. Formulas: BF — Bypass Factor SHCBtuh Edb — Entering Dry Bulb Temperature (F) Fldb = Fedb – 1.09 x cfm Ewb — Entering Wet Bulb Temperature (F) kW — Compressor Motor Power Input Leaving wet bulb = wet bulb temperature corresponding to SHC — Sensible Heat Capacity (1000 Btuh) enthalpy of air leaving coil (hlwb). TC — Total Capacity (1000 Btuh) TCBtuh hlwb = hewb – NOTES: 4.50 x cfm 1. Ratings are gross, and do not account for the effects of the evaporator-fan motor power and heat. Where hewb is enthalpy of air entering evaporator coil (Btu/lb). 2. Direct interpolation is permissible. Do not extrapolate. 3. SHC is based on 80 F db temperature of air entering the unit. At any other temperature, correct the SHC read from the table of cooling capacities as follows: Corrected SHCBtuh = SHC + [1.10 x (1 – BF) x (Fdb – 80) x cfm] Observe the rule of sign. Above 80 F, SHC correction will be posi- tive; add it to SHC. Below 80 F, SHC correction will be negative; subtract it from SHC. 22
23 | GLYCOL HEATING PERFORMANCE GLYCOL COIL (50TJ016-028) Air Entering Evaporator — Cfm Temperature 4400 5400 7200 Entering Condenser Percent Glycol 25 50 25 50 25 50 Edb Ewt Cap Gpm Ldb Cap Gpm Ldb Cap Gpm Ldb Cap Gpm Ldb Cap Gpm Ldb Cap Gpm Ldb 200 310 33 120 293 33 116 347 37 115 327 37 111 405 43 107 381 43 104 55 180 255 27 108 237 27 105 285 30 104 264 30 101 332 35 98 306 35 95 160 200 21 97 181 21 93 223 24 94 202 23 90 259 27 89 233 27 85 200 274 29 127 257 29 124 306 32 123 287 33 119 357 38 116 333 38 113 70 180 218 23 116 201 23 112 244 26 112 224 26 109 284 30 107 259 30 104 160 164 17 104 146 17 100 183 19 101 162 19 98 212 22 97 187 22 94 200 249 26 132 233 27 129 279 30 128 260 30 125 325 34 122 302 34 119 80 180 194 21 121 177 20 117 217 23 117 197 23 114 252 26 113 228 27 109 160 140 15 109 123 14 106 156 16 107 136 16 103 180 18 103 156 19 100 GLYCOL COIL (50TJ016-028) (cont) Air Entering Evaporator — Cfm Temperature 9000 Entering Condenser Percent Glycol 25 50 Edb Ewt Cap Gpm Ldb Cap Gpm Ldb 200 453 48 102 425 48 99 55 180 371 39 93 342 39 90 160 290 31 85 260 30 82 200 400 42 111 372 42 108 70 180 317 34 103 287 33 100 160 237 25 94 208 24 91 200 364 39 118 337 38 115 80 180 281 30 109 254 29 106 160 201 21 101 173 20 78 GLYCOL COIL RATINGS (50TJ016-028) Entering Cfm Fluid 4,000 5,000 6,000 8,000 10,000 Temp (F) Gpm ∆∆∆∆ P* Gpm ∆∆∆∆ P* Gpm ∆∆∆∆ P* Gpm ∆∆∆∆ P* Gpm ∆∆∆∆ P* 200 27 1.2 31 1.5 35 1.8 41 2.4 47 2.9 180 22 0.9 25 1.1 27 1.3 32 1.6 36 2.0 160 16 0.6 19 0.7 20 0.8 24 1.0 27 1.2 LEGEND NOTES: Cap — Btuh x 1000 1. This accessory glycol coil is intended for use with a MINIMUM of Edb — Entering Dry Bulb Temperature (F) 25% glycol solution. It IS NOT intended for use solely with water Ewt — Entering Water Temperature (F) due to freeze-up conditions and the resulting water damage to the Gpm — Gallons Per Minute conditioned space. Ldb — Leaving Dry-Bulb Temperature (F) 2. Water ∆ = 20 F. *∆ P is the fluid pressure in ft of head. 23
24 | Performance data (cont) FAN PERFORMANCE — 50TJ016-028 — SI 50TJ016 (52.8 kW)* Available External Static Pressure (Pa) Airlfow 50 100 149 199 249 299 (L/s) r/s BkW kW r/s BkW kW r/s BkW kW r/s BkW kW r/s BkW kW r/s BkW kW 2124 11.4 0.95 1.10 13.2 1.10 1.28 14.8 1.26 1.47 16.3 1.42 1.65 17.7 1.58 1.84 19.0 1.75 2.03 2266 11.9 1.09 1.26 13.6 1.24 1.45 15.2 1.41 1.64 16.6 1.57 1.83 18.0 1.73 2.02 19.2 1.90 2.22 2408 12.4 1.24 1.44 14.1 1.40 1.63 15.6 1.57 1.83 17.0 1.73 2.02 18.3 1.90 2.22 19.5 2.07 2.42 2549 13.0 1.40 1.64 14.5 1.57 1.83 16.0 1.74 2.03 17.3 1.91 2.23 18.6 2.08 2.43 19.8 2.26 2.63 2691 13.5 1.58 1.84 15.0 1.75 2.04 16.4 1.93 2.25 17.7 2.10 2.45 19.0 2.28 2.65 20.1 2.45 2.86 2833 14.1 1.77 2.07 15.5 1.95 2.27 16.9 2.13 2.48 18.1 2.30 2.69 19.3 2.48 2.89 20.5 2.66 3.10 2974 14.6 1.98 2.31 16.0 2.16 2.52 17.3 2.34 2.73 18.5 2.52 2.94 19.7 2.70 3.15 20.8 2.89 3.36 3116 15.2 2.20 2.57 16.5 2.39 2.78 17.8 2.57 2.99 19.0 2.75 3.21 20.1 2.94 3.43 21.2 3.13 3.64 3257 15.8 2.44 2.84 17.0 2.62 3.06 18.3 2.81 3.28 19.4 3.00 3.50 20.5 3.19 3.72 — — — 3399 16.3 2.69 3.13 17.6 2.88 3.36 18.8 3.07 3.58 — — — — — — — — — 3541 16.9 2.95 3.44 18.1 3.15 3.67 — — — — — — — — — — — — 50TJ016 (52.8 kW)* (cont) Available External Static Pressure (Pa) Airflow 349 399 448 473 498 (L/s) r/s BkW kW r/s BkW kW r/s BkW kW r/s BkW kW r/s BkW kW 2124 20.2 1.91 2.23 21.4 2.08 2.43 22.6 2.26 2.63 23.1 2.35 2.74 23.6 2.44 2.84 2266 20.5 2.07 2.42 21.6 2.25 2.62 22.7 2.42 2.82 23.3 2.51 2.93 23.8 2.60 3.03 2408 20.7 2.25 2.62 21.8 2.42 2.82 22.9 2.60 3.03 23.5 2.69 3.14 24.0 2.78 3.24 2549 21.0 2.43 2.83 22.1 2.61 3.04 23.2 2.79 3.25 23.7 2.88 3.36 24.2 2.97 3.47 2691 21.3 2.63 3.07 22.4 2.81 3.28 23.4 3.00 3.49 23.9 3.09 3.60 24.4 3.18 3.71 2833 21.6 2.84 3.32 22.7 3.03 3.53 23.7 3.21 3.75 — — — — — — 2974 21.9 3.07 3.58 — — — — — — — — — — — — 3116 — — — — — — — — — — — — — — — 3257 — — — — — — — — — — — — — — — 3399 — — — — — — — — — — — — — — — 3541 — — — — — — — — — — — — — — — LEGEND 2. Static pressure losses (i.e., economizer) must be added to external static pressure before entering fan performance table. BkW — Brake Kilowatts 3. Interpolation is permissible. Do not extrapolate. FIOP — Factory-Installed Option 4. Fan performance is based on wet coils, clean filters, and casing loses. See kW — Input Kilowatts to Motor page 31 for accessory/FIOP static pressure information. *Standard drive range for the standard Low-Medium static drive on 50TJ016 is 5. Extensive motor and drive testing on these units ensures that the full brake 12.38 to 16.38 r/s and 17.05 to 21.67 r/s for the optional High static drive. Other kilowatt and watts range of the motor can be utilized with confidence. Using r/s require a field-supplied drive. your fan motors up to the watts or bkW rating shown will not result in nuisance tripping or premature motor failure. Unit warranty will not be affected. NOTES: 6. Use of a field-supplied motor may affect wiring size. Contact your Carrier rep- 1. Maximum continuous bkW is 3.17. Do not adjust motor rpm such that motor resentative for details. For additional information on motor performance, refer maximum bkW and/or watts is exceeded at the maximum operating L/s. to Evaporator-Fan Motor Performance table on page 32. 24
25 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) 50TJ024 (70.3 kW)* Available External Static Pressure (Pa) Airflow 50 100 149 199 249 299 349 399 (L/s) r/s BkW kW r/s BkW kW r/s BkW kW r/s BkW kW r/s BkW kW r/s BkW kW r/s BkW kW r/s BkW kW 2595 11.4 1.49 1.68 12.7 1.71 1.92 13.9 1.94 2.18 15.0 2.17 2.44 16.1 2.41 2.71 17.1 2.66 2.99 18.1 2.91 3.28 19.0 3.17 3.57 2833 12.2 1.76 2.01 13.4 1.99 2.26 14.5 2.21 2.52 15.6 2.45 2.78 16.6 2.69 3.06 17.6 2.94 3.34 18.5 3.19 3.62 19.4 3.45 3.92 3069 13.0 2.09 2.37 14.1 2.31 2.63 15.2 2.55 2.89 16.2 2.78 3.16 17.2 3.03 3.44 18.1 3.28 3.72 19.0 3.53 4.01 19.9 3.79 4.30 3305 13.8 2.45 2.78 14.9 2.68 3.04 15.9 2.91 3.31 16.8 3.15 3.58 17.8 3.40 3.86 18.7 3.65 4.15 19.6 3.91 4.44 20.4 4.16 4.73 3541 14.6 2.84 3.23 15.6 3.07 3.49 16.6 3.31 3.77 17.5 3.56 4.04 18.4 3.81 4.33 19.3 4.06 4.61 20.1 4.32 4.91 20.9 4.58 5.20 3777 15.5 3.27 3.72 16.4 3.51 3.99 17.3 3.75 4.26 18.2 4.00 4.54 19.1 4.25 4.83 19.9 4.51 5.12 20.7 4.77 5.41 21.5 5.03 5.71 4013 16.3 3.74 4.24 17.2 3.98 4.52 18.1 4.22 4.80 18.9 4.48 5.09 19.7 4.73 5.38 20.5 4.99 5.67 21.3 5.25 5.97 22.1 5.52 6.27 4249 17.2 4.24 4.82 18.0 4.49 5.10 18.9 4.74 5.38 19.7 4.99 5.67 20.4 5.25 5.96 21.2 5.51 6.26 21.9 5.77 6.56 22.7 6.04 6.86 4485 18.0 4.78 5.43 18.8 5.03 5.72 19.6 5.29 6.01 20.4 5.54 6.30 21.2 5.80 6.60 21.9 6.07 6.90 22.6 6.33 7.20 23.3 6.60 7.51 4721 18.9 5.36 6.09 19.7 5.62 6.38 20.4 5.87 6.68 21.2 6.13 6.97 21.9 6.40 7.27 22.6 6.67 7.57 23.3 6.93 7.88 24.0 7.21 8.19 50TJ024 (70.3 kW)* (cont) Available External Static Pressure (Pa) Airflow 448 473 498 (L/s) r/s BkW kW r/s BkW kW r/s BkW kW 2595 20.0 3.43 3.86 20.4 3.57 4.02 20.8 3.71 4.17 2833 20.3 3.71 4.21 20.8 3.84 4.36 21.2 3.97 4.52 3069 20.7 4.05 4.60 21.2 4.18 4.75 21.6 4.32 4.91 3305 21.2 4.43 5.03 21.6 4.56 5.18 22.0 4.70 5.34 3541 21.7 4.84 5.50 22.1 4.98 5.66 22.5 5.11 5.81 3777 22.2 5.30 6.02 22.6 5.43 6.17 23.0 5.57 6.32 4013 22.8 5.78 6.57 23.2 5.92 6.73 23.5 6.06 6.88 4249 23.4 6.31 7.17 23.7 6.45 7.33 24.1 6.59 7.48 4485 24.0 6.88 7.82 24.3 7.02 7.97 24.7 7.15 8.13 4721 24.6 7.48 8.50 — — — — — — LEGEND 3. Interpolation is permissible. Do not extrapolate. 4. Fan performance is based on wet coils, clean filters, and casing loses. See BkW — Brake Kilowatts page 31 for accessory/FIOP static pressure information. FIOP — Factory-Installed Option 5. Extensive motor and drive testing on these units ensures that the full brake kW — Input Kilowatts to Motor kilowatt and watts range of the motor can be utilized with confidence. Using *Standard drive range for Low-Medium static drive on 50TJ024 is 12.8 to 15.2 r/s. your fan motors up to the watts or bkW rating shown will not result in nuisance Standard drive range for High static drive on 50TJ024 is 16.6 to 20.3 r/s. Other tripping or premature motor failure. Unit warranty will not be affected. r/s require a field-supplied drive. 6. Use of a field-supplied motor may affect wiring size. Contact your Carrier rep- resentative for details. For additional information on motor performance, refer NOTES: to Evaporator-Fan Motor Performance table on page 32. 1. Maximum continuous bkW is 7.68. Do not adjust motor rpm such that motor maximum bkW and/or watts is exceeded at the maximum operating L/s. 2. Static pressure losses (i.e., economizer) must be added to external static pressure before entering fan performance table. 25
26 | Performance data (cont) FAN PERFORMANCE — 50TJ016-028 — SI (cont) 50TJ028 (87.9 kW)* Available External Static Pressure (Pa) Airflow 50 100 149 199 249 299 349 (L/s) r/s BkW kW r/s BkW kW r/s BkW kW r/s BkW kW r/s BkW kW r/s BkW kW r/s BkW kW 3305 14.1 2.41 2009 15.1 2.67 2222 16.2 2.93 2441 17.1 3.20 2666 18.1 3.48 2897 19.0 3.76 3133 19.8 4.05 3375 3541 14.9 2.82 2355 15.9 3.09 2574 16.9 3.36 2799 17.8 3.63 3029 18.7 3.92 3264 19.6 4.20 3504 20.4 4.50 3750 3777 15.8 3.28 2735 16.7 3.55 2961 17.7 3.83 3191 18.5 4.11 3427 19.4 4.40 3667 20.2 4.69 3911 21.0 4.99 4161 4013 16.7 3.78 3153 17.6 4.06 3384 18.4 4.34 3620 19.3 4.63 3861 20.1 4.93 4106 20.9 5.22 4355 21.6 5.53 4608 4249 17.6 4.33 3608 18.4 4.61 3845 19.2 4.90 4087 20.0 5.20 4332 20.8 5.50 4582 21.6 5.80 4836 22.3 6.11 5094 4485 18.4 4.92 4102 19.2 5.21 4345 20.0 5.51 4592 20.8 5.81 4843 21.5 6.12 5097 22.3 6.43 5356 23.0 6.74 5618 4721 19.3 5.56 4635 20.1 5.86 4884 20.8 6.16 5137 21.6 6.47 5393 22.3 6.78 5652 23.0 7.10 5915 23.7 7.42 6182 4957 20.2 6.25 5210 20.9 6.56 5464 21.7 6.87 5722 22.4 7.18 5983 23.1 7.50 6248 23.7 7.82 6515 24.4 8.14 6786 5193 21.1 6.99 5826 21.8 7.30 6086 22.5 7.62 6349 23.2 7.94 6616 23.8 8.26 6885 24.5 8.59 7157 25.1 8.92 7432 5311 21.5 7.38 6151 22.2 7.69 6413 22.9 8.01 6679 23.6 8.34 6948 24.2 8.66 7219 24.9 8.99 7494 25.5 9.32 7771 50TJ028 (87.9 kW)* (cont) Available External Airflow Static Pressure (Pa) (L/s) 399 448 r/s BkW kW r/s BkW kW 3305 20.7 4.34 3621 21.5 3.63 3873 3541 21.2 4.80 4000 22.0 4.11 4255 3777 21.8 5.30 4414 22.5 4.63 4673 4013 22.4 5.84 4866 23.1 5.20 5128 4249 23.0 6.42 5355 23.7 5.81 5621 4485 23.7 7.06 5883 24.4 6.47 6153 4721 24.4 7.74 6451 25.0 7.18 6724 4957 25.1 8.47 7060 25.7 7.94 7337 5193 25.8 9.25 7710 — — — 5311 — — — — — — LEGEND 2. Static pressure losses (i.e., economizer) must be added to external static pres- sure before entering fan performance table. BkW — Brake Kilowatts 3. Interpolation is permissible. Do not extrapolate. FIOP — Factory-Installed Option 4. Fan performance is based on wet coils, clean filters, and casing loses. See kW — Input Kilowatts to Motor page 31 for accessory/FIOP static pressure information. *Standard drive range for Low-Medium static drive on 50TJ028 is 14.8 to 17.8 r/s. 5. Extensive motor and drive testing on these units ensures that the full brake Standard drive range for High static drive on 50TJ028 is 18.6 to 22.4 r/s. Other kilowatt and watts range of the motor can be utilized with confidence. Using r/s require a field-supplied drive. your fan motors up to the watts or bkW rating shown will not result in nuisance tripping or premature motor failure. Unit warranty will not be affected. NOTES: 6. Use of a field-supplied motor may affect wiring size. Contact your Carrier repre- 1. Maximum continuous bkW is 9.92 on 400 v units and 8.60 on 220 v units. Do sentative for details. For additional information on motor performance, refer to not adjust motor rpm such that motor maximum bkW and/or watts is exceeded Evaporator-Fan Motor Performance table on page 32. at the maximum operating L/s. 26
27 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH 50TJ016 (15 TONS)* Available External Static Pressure (in. wg) Airflow 0.2 0.4 0.6 0.8 1.0 1.2 (Cfm) Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts 4500 684 1.28 1102 791 1.49 1283 887 1.70 1466 977 1.92 1652 1061 2.13 1841 1139 2.36 2034 4800 715 1.47 1265 817 1.68 1451 910 1.90 1638 997 2.12 1828 1078 2.34 2021 1155 2.57 2217 5100 747 1.67 1442 844 1.89 1633 934 2.12 1825 1018 2.34 2019 1097 2.57 2216 1171 2.80 2416 5400 779 1.90 1635 872 2.12 1831 959 2.35 2027 1040 2.58 2226 1117 2.81 2426 1189 3.05 2629 5700 812 2.14 1844 901 2.37 2044 985 2.60 2245 1063 2.84 2448 1138 3.07 2652 1209 3.31 2858 6000 845 2.40 2068 931 2.64 2273 1011 2.87 2478 1087 3.11 2685 1160 3.35 2893 1229 3.60 3103 6300 878 2.68 2309 961 2.92 2518 1039 3.16 2728 1112 3.41 2939 1183 3.65 3151 1250 3.90 3365 6600 912 2.98 2566 992 3.22 2780 1067 3.47 2994 1138 3.72 3209 1207 3.97 3425 1273 4.22 3642 6900 946 3.29 2841 1023 3.55 3059 1096 3.80 3277 1165 4.05 3496 1232 4.31 3716 — — — 7200 981 3.63 3133 1055 3.89 3355 1125 4.15 3578 — — — — — — — — — 7500 1016 3.99 3443 1087 4.25 3669 — — — — — — — — — — — — 50TJ016 (15 TONS)* (cont) Available External Static Pressure (in. wg) Airflow 1.4 1.6 1.8 1.9 2.0 (Cfm) Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts 4500 1214 2.59 2230 1285 2.82 2430 1353 3.05 2633 1386 3.17 2736 1418 3.29 2839 4800 1228 2.80 2417 1297 3.04 2619 1364 3.27 2825 1396 3.40 2928 1428 3.52 3033 5100 1243 3.04 2618 1311 3.27 2823 1376 3.51 3031 1408 3.64 3136 1439 3.76 3242 5400 1259 3.29 2835 1326 3.53 3043 1390 3.77 3254 1421 3.90 3360 1452 4.02 3467 5700 1277 3.56 3067 1342 3.80 3278 1405 4.05 3492 1435 4.17 3600 1466 4.30 3708 6000 1295 3.84 3316 1359 4.09 3530 1421 4.34 3746 — — — — — — 6300 1315 4.15 3580 — — — — — — — — — — — — 6600 — — — — — — — — — — — — — — — 6900 — — — — — — — — — — — — — — — 7200 — — — — — — — — — — — — — — — 7500 — — — — — — — — — — — — — — — LEGEND 2. Static pressure losses (i.e., economizer) must be added to external static pres- sure before entering fan performance table. Bhp — Brake Horsepower 3. Interpolation is permissible. Do not extrapolate. FIOP — Factory-Installed Option 4. Fan performance is based on wet coils, clean filters, and casing loses. See Watts — Input Watts to Motor page 31 for accessory/FIOP static pressure information. *Standard drive range for the standard Low-Medium static drive on 50TJ016 is 5. Extensive motor and drive testing on these units ensures that the full brake 743 to 983 rpm and 1023 to 1300 r/s for the optional High static drive. Other horsepower and watts range of the motor can be utilized with confidence. rpms require a field-supplied drive. Using your fan motors up to the watts or bhp rating shown will not result in nui- sance tripping or premature motor failure. Unit warranty will not be affected. NOTES: 6. Use of a field-supplied motor may affect wiring size. Contact your Carrier repre- 1. Maximum continuous bhp is 4.25. Do not adjust motor rpm such that motor sentative for details. For additional information on motor performance, refer to maximum bhp and/or watts is exceeded at the maximum operating cfm. Evaporator-Fan Motor Performance table on page 32. 27
28 | Performance data (cont) FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) 50TJ024 (20 Tons)* Available External Static Pressure (in. wg) Airflow 0.2 0.4 0.6 0.8 1.0 1.2 1.4 (cfm) Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts 5,500 682 1.99 1675 760 2.29 1922 832 2.59 2177 901 2.90 2441 965 3.22 2712 1027 3.56 2990 1086 3.89 3275 6,000 730 2.38 2005 802 2.68 2257 871 2.99 2516 935 3.31 2783 997 3.63 3057 1056 3.97 3337 1112 4.31 3623 6,500 778 2.82 2373 846 3.13 2630 911 3.44 2893 972 3.76 3164 1031 4.09 3440 1087 4.43 3722 1142 4.77 4010 7,000 828 3.31 2780 892 3.62 3042 953 3.94 3310 1011 4.26 3583 1067 4.59 3863 1121 4.93 4148 1173 5.28 4438 7,500 878 3.84 3227 938 4.15 3494 996 4.48 3766 1051 4.81 4043 1105 5.14 4326 1156 5.49 4613 1207 5.83 4906 8,000 928 4.42 3715 985 4.74 3986 1040 5.07 4263 1093 5.40 4544 1144 5.74 4830 1194 6.09 5120 1242 6.44 5415 8,500 979 5.05 4245 1033 5.38 4521 1085 5.71 4801 1136 6.05 5086 1185 6.39 5375 1232 6.74 5669 1279 7.10 5966 9,000 1030 5.73 4817 1082 6.06 5098 1131 6.40 5382 1180 6.74 5671 1227 7.09 5964 1272 7.44 6260 1317 7.80 6561 9,500 1082 6.46 5433 1131 6.80 5718 1178 7.14 6007 1225 7.49 6299 1270 7.84 6595 1313 8.20 6895 1356 8.56 7198 10,000 1134 7.25 6093 1180 7.59 6382 1226 7.94 6675 1270 8.29 6971 1313 8.65 7271 1356 9.01 7574 1397 9.37 7881 50TJ024 (20 Tons)* (cont) Available External Static Pressure (in. wg) Airflow 1.6 1.8 1.9 2.0 (cfm) Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts 5,500 1142 4.24 3567 1197 4.59 3864 1223 4.77 4015 1249 4.96 4167 6,000 1167 4.66 3915 1219 5.01 4213 1245 5.19 4364 1270 5.37 4516 6,500 1194 5.12 4304 1245 5.47 4602 1270 5.65 4754 1294 5.83 4906 7,000 1224 5.63 4733 1273 5.98 5033 1296 6.17 5184 1320 6.35 5337 7,500 1255 6.19 5203 1302 6.55 5504 1326 6.73 5657 1348 6.91 5810 8,000 1289 6.80 5714 1334 7.16 6018 1357 7.34 6171 1379 7.52 6325 8,500 1324 7.45 6268 1368 7.82 6573 1389 8.00 6728 1411 8.18 6883 9,000 1360 8.16 6865 1403 8.53 7173 1424 8.71 7328 1445 8.90 7484 9,500 1398 8.93 7505 1440 9.29 7815 1460 9.48 7972 1480 9.67 8129 10,000 1438 9.74 8190 1477 10.11 8503 — — — — — — LEGEND 2. Static pressure losses (i.e., economizer) must be added to external static pres- sure before entering fan performance table. Bhp — Brake Horsepower 3. Interpolation is permissible. Do not extrapolate. FIOP — Factory-Installed Option 4. Fan performance is based on wet coils, clean filters, and casing loses. See Watts — Input Watts to Motor page 31 for accessory/FIOP static pressure information. *Standard drive range for Low-Medium static drive on 50TJ024 is 769 to 909 rpm. 5. Extensive motor and drive testing on these units ensures that the full brake Standard drive range for High static drive on 50TJ024 is 994 to 1216 rpm. Other horsepower and watts range of the motor can be utilized with confidence. rpms require a field-supplied drive. Using your fan motors up to the watts or bhp rating shown will not result in nui- sance tripping or premature motor failure. Unit warranty will not be affected. NOTES: 6. Use of a field-supplied motor may affect wiring size. Contact your Carrier repre- 1. Maximum continuous bhp is 10.30. Do not adjust motor rpm such that motor sentative for details. For additional information on motor performance, refer to maximum bhp and/or watts is exceeded at the maximum operating cfm. Evaporator-Fan Motor Performance table on page 32. 28
29 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) 50TJ028 (25 Tons)* Available External Static Pressure (in. wg) Airflow 0.2 0.4 0.6 0.8 1.0 1.2 1.4 (cfm) Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts 7,000 845 3.26 2693 909 3.60 2979 969 3.96 3272 1028 4.32 3574 1083 4.70 3883 1137 5.08 4,200 1189 5.47 4,524 7,500 896 3.82 3156 956 4.17 3450 1014 4.54 3752 1069 4.91 4060 1123 5.29 4375 1174 5.68 4,698 1224 6.08 5,026 8,000 948 4.43 3667 1005 4.80 3969 1060 5.17 4278 1112 5.56 4593 1163 5.94 4915 1213 6.34 5,243 1261 6.75 5,577 8,500 1001 5.11 4226 1054 5.49 4537 1106 5.87 4853 1156 6.26 5175 1205 6.66 5504 1253 7.06 5,838 1299 7.47 6,177 9,000 1053 5.85 4836 1104 6.23 5155 1154 6.63 5478 1202 7.02 5808 1248 7.43 6142 1294 7.84 6,483 1338 8.26 6,828 9,500 1106 6.65 5498 1155 7.04 5824 1202 7.44 6155 1248 7.85 6492 1293 8.26 6833 1336 8.68 7,179 1379 9.11 7,530 10,000 1159 7.52 6214 1206 7.92 6547 1251 8.33 6886 1295 8.74 7229 1338 9.16 7577 1380 9.59 7,929 1421 10.02 8,286 10,500 1213 8.45 6984 1257 8.86 7325 1300 9.28 7671 1342 9.70 8020 1384 10.13 8375 1424 10.56 8,733 1464 11.00 9,096 11,000 1266 9.45 7810 1309 9.87 8159 1350 10.29 8511 1391 10.73 8868 1431 11.16 9229 1470 11.60 9,594 1508 12.05 9,963 11,250 1293 9.97 8245 1334 10.40 8597 1375 10.83 8953 1415 11.26 9313 1454 11.70 9677 1493 12.15 10,045 1530 12.60 10,417 50TJ028 (25 Tons)* (cont) Available External Airflow Static Pressure (in. wg) (cfm) 1.6 1.8 Rpm Bhp Watts Rpm Bhp Watts 7,000 1239 5.87 4,854 1288 4.91 5191 7,500 1272 6.48 5,362 1320 5.56 5703 8,000 1307 7.16 5,917 1353 6.26 6263 8,500 1344 7.89 6,523 1388 7.02 6873 9,000 1382 8.68 7,179 1424 7.85 7534 9,500 1421 9.54 7,887 1462 8.74 8247 10,000 1461 10.46 8,648 1501 9.70 9014 10,500 1503 11.45 9,464 1541 10.73 9835 11,000 1546 12.50 10,336 — — — 11,250 — — — — — — LEGEND 2. Static pressure losses (i.e., economizer) must be added to external static pres- sure before entering fan performance table. Bhp — Brake Horsepower 3. Interpolation is permissible. Do not extrapolate. FIOP — Factory-Installed Option 4. Fan performance is based on wet coils, clean filters, and casing loses. See Watts — Input Watts to Motor page 31 for accessory/FIOP static pressure information. *Standard drive range for Low-Medium static drive on 50TJ028 is 888 to 5. Extensive motor and drive testing on these units ensures that the full brake 1069 rpm. Standard drive range for High static drive on 50TJ028 is 1114 to horsepower and watts range of the motor can be utilized with confidence. 1341 rpm. Other rpms require a field-supplied drive. Using your fan motors up to the watts or bhp rating shown will not result in nui- sance tripping or premature motor failure. Unit warranty will not be affected. NOTES: 6. Use of a field-supplied motor may affect wiring size. Contact your Carrier repre- 1. Maximum continuous bhp is 13.30 on 400 v units and 11.5 on 220 v units. Do sentative for details. For additional information on motor performance, refer to not adjust motor rpm such that motor maximum bhp and/or watts is exceeded Evaporator-Fan Motor Performance table on page 32. at the maximum operating cfm. 29
30 | Performance data (cont) FAN PERFORMANCE USING ACCESSORY POWER EXHAUST HORIZONTAL SUPPLY/RETURN FAN PERFORMANCE WITH CRRFCURB013A00 HIGH-STATIC REGAIN ADAPTER NOTE: The CRRFCURB013A00 high-static regain adapter accessory may be used to provide horizontal supply/return. NOTE: The CRRFCURB013A00 horizontal supply and return adapter accessory improves 50TJ fan performance by increasing external static pressure by amount shown above. 30
31 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 L/s COMPONENT 2125 2360 2831 3400 3525 Economizer 10 12 17 22 25 Glycol Coil 55 65 87 109 114 Electric Heat (kW) 22.5 15 17 22 27 30 38.2 19 22 27 35 37 55.4 25 27 35 46 48 LEGEND NOTES: 1. The static pressure must be added to external static pressure. The FIOP — Factory-Installed Option sum and the evaporator entering-air L/s should then be used in con- junction with the Fan Performance tables to determine blower r/s and kW. 2. Heaters are rated at 400 v. ACCESSORY/FIOP STATIC PRESSURE (in. wg) — 50TJ016 CFM COMPONENT 4500 5000 6000 7200 7500 Economizer 0.04 0.05 0.07 0.09 0.10 Glycol Coil 0.22 0.26 0.35 0.44 0.46 Electric Heat (kW) 22.5 0.06 0.07 0.09 0.11 0.12 38.2 0.08 0.09 0.11 0.14 0.15 55.4 0.10 0.11 0.14 0.18 0.19 LEGEND NOTES: FIOP — Factory-Installed Option 1. The static pressure must be added to external static pressure. The sum and the evaporator entering-air cfm should then be used in con- junction with the Fan Performance tables to determine blower rpm and watts. 2. Heaters are rated at 400 v. ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ024,028 L/s COMPONENT 2800 3400 4247 4719 5300 Economizer 17 22 27 30 35 Glycol Coil 86 109 144 164 191 Electric Heat (kW) 22.5 22 27 37 43 50 38.2 28 35 45 53 61 55.4 36 46 57 65 75 LEGEND NOTES: 1. The static pressure must be added to external static pressure. The FIOP — Factory-Installed Option sum and the evaporator entering-air L/s should then be used in con- junction with the Fan Performance tables to determine blower r/s and kW. 2. Heaters are rated at 400 v. ACCESSORY/FIOP STATIC PRESSURE (in. wg) — 50TJ024,028 CFM COMPONENT 6000 7200 9000 10,000 11,250 Economizer 0.07 0.09 0.11 0.12 0.14 Glycol Coil 0.35 0.44 0.58 0.66 0.77 Electric Heat (kW) 22.5 0.09 0.11 0.15 0.17 0.20 38.2 0.11 0.14 0.18 0.21 0.25 55.4 0.14 0.18 0.23 0.26 0.30 LEGEND NOTES: FIOP — Factory-Installed Option 1. The static pressure must be added to external static pressure. The sum and the evaporator entering-air cfm should then be used in con- junction with the Fan Performance tables to determine blower rpm and watts. 2. Heaters are rated at 400 v. 31
32 | Performance data (cont) FAN R/s AT MOTOR PULLEY SETTINGS* (FACTORY-SUPPLIED DRIVES) — SI UNIT MOTOR PULLEY TURNS OPEN 50TJ 0 1/2 1 11/2 2 21/2 3 31/2 4 41/2 5 51/2 6 016** 16.38 15.99 15.58 15.19 14.78 14.38 13.98 13.58 13.18 12.78 12.38 † † 016†† 21.67 21.20 20.75 20.28 19.82 19.37 18.90 18.43 17.97 17.52 17.05 † † 024** 15.15 14.92 14.68 14.45 14.22 13.98 13.75 13.52 13.28 13.05 12.82 † † 024†† 20.27 19.97 19.66 19.35 19.03 18.73 18.42 18.12 17.80 17.50 17.19 16.88 16.57 028** 17.82 17.52 17.21 16.91 16.61 16.31 16.01 15.71 15.40 15.10 14.80 † † 028†† 22.35 21.97 21.59 21.22 20.84 20.46 20.08 19.70 19.32 18.95 18.57 † † *Approximate fan r/s shown. †Due to belt and pulley size, pulley cannot be set to this many turns open. **Low-medium static drive. ††High static drive. FAN RPM AT MOTOR PULLEY SETTINGS* (FACTORY-SUPPLIED DRIVES) — ENGLISH UNIT MOTOR PULLEY TURNS OPEN 50TJ 0 1/2 1 11/2 2 21/2 3 31/2 4 41/2 5 51/2 6 016** 983 959 935 911 887 863 839 815 791 767 743 † † 016†† 1300 1272 1245 1217 1189 1162 1134 1106 1078 1051 1023 † † 024** 909 895 881 867 853 839 825 811 797 783 769 † † 024†† 1216 1198 1179 1161 1142 1124 1105 1087 1068 1050 1031 1013 994 028** 1069 1051 1033 1015 997 979 960 942 924 906 888 † † 028†† 1341 1318 1296 1273 1250 1228 1205 1182 1159 1137 1114 † † *Approximate fan rpm shown. †Due to belt and pulley size, pulley cannot be set to this many turns open. **Low-medium static drive. ††High static drive. EVAPORATOR-FAN MOTOR PERFORMANCE MAXIMUM MAXIMUM MAXIMUM UNIT UNIT RATED ACCEPTABLE ACCEPTABLE ACCEPTABLE MAXIMUM 50TJ VOLTAGE CONTINUOUS CONTINUOUS OPERATING AMP DRAW BHP* BkW* WATTS 220 3.45 3.17 3,065 9.4 016 400 4.25 3.17 3,775 4.8 220 10.30 7.68 8,640 26.0 024 400 10.30 7.68 8,640 13.0 220 11.50 8.60 9,600 36.0 028 400 13.30 9.92 11,000 14.6 LEGEND Bhp — Brake Horsepower BkW — Fan Input Watts x Motor Efficiency *Extensive motor and electrical testing on these units ensures that the full horsepower and kilowatt ranges of the motors can be utilized with confidence. Using your fan motors up to the horsepower or kilowatt rat- ings shown in this table will not result in nuisance tripping or premature motor failure. Unit warranty will not be affected. 32
33 | Electrical data 50TJ016-028 VOLTAGE COMPRESSOR POWER ELECTRIC POWER UNIT NOMINAL RANGE No. 1 No. 2 OFM IFM EXHAUST HEAT* SUPPLY 50TJ VOLTAGE Min Max RLA LRA RLA LRA Qty Hp FLA (ea) Hp FLA FLA LRA kW FLA MCA MOCP† — — — — 90 110 220 198 242 30.1 196 30.1 196 2 1.0 6.3 3.0 9.8 4.7 10.5 — — 95 110 — — — — 47 60 4.7 10.5 — — 51 60 016 22.5 32.5 47 60 4.7 10.5 22.5 32.5 53 60 400 360 440 15.5 111 15.5 111 2 1.0 3.4 3.0 4.8 — — 38.2 55.1 75 80 4.7 10.5 38.2 55.1 81 90 — — 55.4** 80.0 86 100 4.7 10.5 55.4** 80.0 92 100 — — — — 121 150 220 198 242 38.5 293 37.7 220 2 1.0 6.3 7.5 23.5 4.7 10.5 — — 126 150 — — — — 63 80 4.7 10.5 — — 68 80 024 — — 22.5 32.5 63 80 4.7 10.5 22.5 32.5 68 80 400 360 440 21.8 167 17.2 118 2 1.0 3.4 7.5 12.1 38.2 55.1 84 90 4.7 10.5 38.2 55.1 90 90 — — 55.4** 80.0 95 100 4.7 10.5 55.4** 80.0 101 110 — — — — 139 175 220 198 242 45.4 345 38.5 293 2 1.0 6.3 10.0 32.0 4.7 10.5 — — 144 175 — — — — 72 90 4.7 10.5 — — 77 100 028 (Standard — — 22.5 32.5 72 90 Fan) 400 360 440 23.7 198 21.8 167 2 1.0 3.4 10.0 14.0 4.7 10.5 22.5 32.5 77 100 — — 38.2 55.1 86 90 4.7 10.5 38.2 55.1 92 100 — — 55.4** 80.0 98 110 4.7 10.5 55.4** 80.0 103 110 — — — — 80 100 4.7 10.5 — — 85 100 028 — — 22.5 32.5 80 100 (High 4.7 10.5 22.5 32.5 85 100 Static 400 360 440 23.7 198 21.8 167 2 5.0 7.3 10.0 14.0 — — 38.2 55.1 86 100 Fan) 4.7 10.5 38.2 55.1 92 100 — — 55.4** 80.0 98 110 4.7 10.5 55.4** 80.0 103 110 LEGEND EXAMPLE: Supply voltage is 400-3-50. FLA — Full Load Amps AB = 393 v HACR — Heating, Air Conditioning and Refrigeration BC = 403 v IFM — Indoor (Evaporator) Fan Motor AC = 396 v LRA — Locked Rotor Amps MCA — Minimum Circuit Amps 393 + 403 + 396 MOCP — Maximum Overcurrent Protection Average Voltage = NEC — National Electrical Code, U.S.A. 3 OFM — Outdoor (Condenser) Fan Motor 1192 RLA — Rated Load Amps = 3 *Heater capacity (kW) is based on heater voltage of 400 v. If power dis- = 397 tribution voltage to unit varies from rated heater voltage, heater kW Determine maximum deviation from average voltage: will vary accordingly. †Fuse or HACR circuit breaker. (AB) 397 – 393 = 4 v **Heaters are field installed only. (BC) 403 – 397 = 6 v (AC) 397 – 396 = 1 v NOTES: Maximum deviation is 6 v. 1. In compliance with NEC requirements (U.S.A. Standard) for mul- timotor and combination load equipment (refer to NEC Articles 430 Determine percent voltage imbalance: and 440), the overcurrent protective device for the unit shall be 6 % Voltage Imbalance = 100 x fuse or HACR breaker. 397 2. Unbalanced 3-Phase Supply Voltage = 1.5% Never operate a motor where a phase imbalance in supply voltage is greater than 2%. Use the following formula to determine the per- This amount of phase imbalance is satisfactory as it is below the cent of voltage imbalance. maximum allowable 2%. % Voltage Imbalance IMPORTANT: If the supply voltage phase imbalance is more max voltage deviation from average voltage than 2%, contact your local electric utility company immediately. = 100 x average voltage 3. MCA calculation for units with electric heaters over 50 kW = (1.25 x IFM amps) + (1.00 x heater FLA). 33
34 | Typical piping and wiring — 50TJ016-028 (50TJ016 shown) LEGEND NEC — National Electrical Code (U.S.A.) NOTES: 1. Illustration shown is a general guide only and is not intended to include all details for any specific installation. 2. Installation must comply with all applicable codes. 3. A 90-degree elbow must be installed on the supply duct connection for units equipped with electric heat. 34
35 | Typical wiring schematic — 50TJ016-028 (size 024 shown) ELECTRIC HEAT 400 V 400 V Amps kW A 34 23.3 B 57 39.6 C 83 57.4 35
36 | Typical wiring schematic — 50TJ016-028 (size 024 shown) (cont) LEGEND AHA — Adjustable Heat Anticipator OFC — Outdoor-Fan Contactor BRK W/AT — Breaks with Amp Turns OFM — Outdoor-Fan Motor C — Contactor, Compressor OP — Overcurrent Protector CB — Circuit Breaker PL — Plug Assembly CC — Cooling Compensator PRI — Primary CH — Crankcase Heater SR — Solenoid Relay CLO — Compressor Lockout SW — Switch CLS — Cooling Lockout Switch TB — Terminal Block COMP — Compressor Motor TC — Thermostat Cooling CT — Current Transformer TDR — Time-Delay Relay DM — Damper Motor TH — Thermostat Heating EAS — Economizer Actuator Auxiliary TRAN — Transformer Switch U — Unloader EQUIP — Equipment UR — Unloader Relay FL — Fuse Link FLA — Full Load Amps Terminal (Marked) FPT — Freeze Protection Thermostat FU — Fuse Terminal (Unmarked) GND — Ground HC — Heater Contactor Terminal Block HPS — High-Pressure Switch HTR — Heater IFC — Indoor-Fan Contactor Splice IFCB — Indoor-Fan Circuit Breaker IFM — Indoor-Fan Motor Factory Wiring IFR — Indoor-Fan Relay L — Light Field Wiring LLS — Liquid Line Solenoid LOR — Lockout Relay To indicate common LPS — Low-Pressure Switch potential only, not to LS — Limit Switch represent wiring MAT — Mixed-Air Thermostat Option/Accessory Wiring NEUT — Neutral OAT — Outdoor-Air Thermostat NOTES: 5. The CLO locks out the compressor to prevent short cycling on compressor 1. Compressor and/or fan motor(s) thermally protected. Three-phase motors overload and safety devices; before replacing CLO, check these devices. protected against primary single phasing conditions. 6. Number(s) indicates the line location of used contacts. A bracket over 2 2. If any of the original wire furnished must be replaced, it must be replaced numbers signifies a single-pole, double-throw contact. An underlined num- with Type 90° C wire or its equivalent. ber signifies a normally closed contact. Plain (no line) number signifies a 3. Jumpers are omitted when unit is equipped with economizer. normally open contact. 4. IFCB Must Trip Amps are equal to or less than 140% FLA. 36
37 | 37
38 | Typical wiring schematic (cont) NON-FUSED DISCONNECT NOTES: 1. If the Service Option Package is ordered for size 016-028 units, the Non-Fused Disconnect shall be factory-installed. 2. The Disconnect takes the place of TB-1 as shown on the unit wiring diagram label and the component arrangement label. 38
39 | Controls Operating sequence Upon a second-stage call for cooling, compressor no. 1 is energized and mechanical cooling is integrated with Cooling, units without economizer — When thermo- economizer cooling. If the outdoor-air temperature drops stat calls for cooling, terminals G and Y1 are energized. below 10 C (50 F), a cooling lockout switch prevents the The indoor (evaporator) fan contactor (IFC) and compres- compressors from running. sor contactor no. 1 (C1) are energized, and evaporator-fan motor (IFM), compressor no. 1 and condenser fans start. NOTE: In the economizer mode only compressor no. 1 is The condenser-fan motors run continuously while unit is energized. Compressor no. 2 is not capable of operating. cooling. When the thermostat calls for a second stage of When supply-air temperature drops below a fixed set cooling by energizing Y2, compressor contactor no. 2 (C2) point 11.7 C (53 F), the economizer damper modulates to is energized and compressor no. 2 starts. maintain the temperature at the fixed set point. Heating, units without economizer (if accessory or Freeze protection thermostats (FPT) are located on the optional heater is installed) — Upon a call for heating evaporator coil. They detect frost build-up and turn the through terminal W1, IFC and heater contactor no. 1 compressors off, locking them out and requiring a manual (HC1) are energized. On units equipped for 2 stages of reset. Once frost has melted, the compressors can be heat, when additional heat is needed, HC2 is energized reenergized. through W2. Heating, units with economizer — Outdoor-air damp- Cooling, units with economizer — Upon a call for er stays at VENT position while evaporator fan is operat- cooling, when outdoor ambient is above the temperature ing. Refer to Heating, Units Without Economizer (If Acces- control setting, the economizer damper moves to VENT sory or Optional Heater is Installed) section on this page position. The compressors and evaporator and condenser for remainder of operating sequence. fans energize. Upon a first call for cooling, when outdoor ambient is below the temperature control setting, the evaporator fan starts and the economizer opens to maintain 11.7 C (53 F) leaving-air temperature. The compressors remain off. 39
40 | Controls (cont) TYPICAL SMOKE CONTROL/FIRE SHUTDOWN WIRING LEGEND Field Wiring Field-Supplied Switch See Legend on page 36. *Included in power exhaust accessory. OPERATING MODES BP — Building Pressurization: Evaporator fan on, economizer energized to fully open position, power exhaust disabled. E — Evacuation: Evaporator fan off, economizer deenergized to fully closed position, power exhaust on (open). SD — Complete Unit Shutdown: Breaks 24-v power to thermostat. SP — Smoke Purge: Evaporator fan on, economizer energized to fully open position, power exhaust on. 40
41 | 41 GNIRIW SLORTNOC OLLOPA DNA YTILAUQ RIA-ROODNI DNEGEL edixoiD nobraC — OC 2 nommoC — MOC rosneS lioC noisnapxE tceriD — XD gninoitidnoC riA dna ,noitalitneV ,gnitaeH — CAVH ytilauQ riA-roodnI — QAI edoiD gnittimE-thgiL — DEL .deriw eb nac rosnes eno ylnO .ylsuoenatlumis noitcnuf tonnac rosnes ytidimuh dna hctiws sutats retliF* muminiM — .NIM .rosnes OC a sa hcuS† 2 desolC yllamroN — CN .snoitcurtsnI noitallatsnI TVV ro STV rep lortnoC QAI — ”2“ ot noitpo yrailixua teS** tatsomrehT riA-roodtuO — TAO evlaV gnisreveR — .V.R rosneS erutarepmeT riA-ylppuS — TAS erutarepmeT — PMET remrofsnarT — NART metsyS PMET reirraC — STV erutarepmeT dna emuloV elbairaV — ®TVV
42 | Controls (cont) TEMP systems zone systems you require...no more, no less, no compromises. A TEMP System is a network of communicating Carrier TEMP System Thermostats and rooftop, factory-mounted Ideal for department stores, small office buildings, fast Apollo direct digital controls, each serving its own zone food chains, schools, and hotels, a TEMP System is a cost- and heating/cooling unit. Networking allows your building effective way to maintain comfortable building manager to easily access each of your systems from a sin- environments. gle location...whether they are in the same building or lo- NOTE: Unit temperature rise must not be exceeded for cated throughout town. proper unit operation. The TEMP System’s inherently flexible, modular base design supports the exact number of independent, single TEMP SYSTEM THERMOSTAT (WITH TIMECLOCK) TEMP SYSTEM THERMOSTAT (WITHOUT TIMECLOCK) STANDARD UNIT TYPICAL FIELD THERMOSTAT WIRING LEGEND TB — Terminal Block 42
43 | Variable Volume/Variable Temperature VVT® Through the use of communicating electronic controls, Systems VVT Systems are able to provide the comfort of a multiple zone system while using the installation, operating and VVT Systems are dedicated to total building comfort. maintenance economics of single zone equipment... Carrier thermostats, zone dampers, and HVAC equipment virtually putting an end to the cost vs comfort compromise. with factory-mounted direct digital controls continually monitor and adjust their operation to ensure uninterrupted NOTE: Unit temperature rise must not be exceeded for and personalized comfort for all occupants. proper unit operation. 43
44 | Controls (cont) VVT® application guidelines ratings on page 4 for minimum heating cfm required for proper operation of the rooftop heating system. These General — The VVT system is a zoning system that minimum heating airflow levels must be maintained during allows a single-zone heating/cooling system to operate as all phases of heating operation. The heating airflow values a multiple-zone system. For this system to function correct- take precedence over listed minimum cooling airflow val- ly and not adversely affect the reliability of the heating/ ues.) This permits the use of constant volume rooftop units cooling system, the information provided here must be on VVT applications. Without the bypass damper, the re- followed. striction of the zone dampers that are closing at partial There are two parts of the VVT system installation that loads will reduce the airflow through the unit to below the are important for successful operation: the bypass damper minimum levels. and the HVAC (Heating, Ventilation, and Air-Conditioning) The installer is responsible for ensuring that the bypass equipment configuration settings. The following informa- controller is configured and the system is balanced so that tion will provide important details for these two items as the minimum airflow is higher than 40 L/s per kW well as specific instructions for the 50TJ rooftop units. This (300 cfm/ton). To accomplish proper configuration set the information is intended as a supplement to the Installation System Setup Enable Function (Category 5, option 7) to Instructions shipped with both the 33CS system controls ON. This will close the bypass damper and force all of the and the 50TJ rooftop equipment. zone dampers to open. The air balance should be complet- Bypass damper — The bypass damper and controller ed after the zones minimum airflow has been set, verifying serve to accomplish two functions in the VVT system. the total airflow through the equipment is above the mini- First, the bypass damper keeps supply duct pressure and mum airflow level. velocity down at partial load. This permits the VVT system to utilize standard low-velocity, low-pressure supply duct- VVT bypass design layout — Particular attention must be given to bypass duct layout. It has been a source of VVT work, duct insulation, and duct sealing methods. Without system operating problems when neglected. Proper layout the bypass damper, the restriction of the zone dampers consists of the five factors: that are closing at partial loads would cause duct static pressure to climb, adding stress to all supply duct materials. 1. Proper location of the bypass Accompanying velocity and noise would create problems 2. Adequately sizing the bypass in the conditioned space. 3. Avoiding short-circuiting of supply and return air Second, when the bypass damper is set up correctly, it 4. Proper location of the static pickup ensures that the airflow through the HVAC equipment re- mains above the minimum required levels. (See capacity 5. Facilitating the mixing of bypass air with return air VVT BYPASS DESIGN CEILING PLENUM LAYOUT FOR MANUFACTURING OFFICE STATIC PRESSURE SENSOR AND BYPASS DAMPER ACTUATOR ROOFTOP UNIT BYPASS DAMPER WITH SHORT DUCT - SUPPORT PROPERLY AIM BYPASS DAMPER DISCHARGE STATIC AWAY FROM RETURN INLET PRESSURE TUBING 5-CONDUCTOR SHIELDED CABLE (24V) AVOID RETURN GRILLES IN CLOSE PROXIMITY TO BYPASS T BC DISCHARGE AIR PATH MONITOR BYPASS THERMOSTAT CONTROLLER LOCATE PICKUP IN AREA OF LEAST TURBULENCE, 5 DUCT DIAMETERS DOWNSTREAM OF BYPASS TAKEOFF BUT UPSTREAM OF FIRST ZONE TAKEOFF OR MAJOR JUNCTION MOUNT BYPASS CONTROLLER STATIC ON THE WALL NEXT TO THE PRESSURE MONITOR THERMOSTAT PICKUP 44
45 | The recommended location of the bypass damper is for Bypass controller considerations — Besides consider- it to duct the bypass air either into the ceiling plenum or ing the minimum and maximum cfm’s required, as in the into unoccupied spaces. See figure on page 44 for a typi- system design guidelines, the following are a few system cal installation. This method of installation prevents inter- concerns to consider when designing a bypass damper in a ference with intended fresh air intake through the unit and VVT® system. economizer operation. 1. The maximum amount of air being bypassed should It is highly recommended that the bypass damper is not match an equivalent amount of cfm of unconditioned ducted between the supply duct and the return duct as air based on the ability of the system to unload. For shown in the diagram below. This type of installation may example: If the equipment has two compressors and result in the return duct becoming pressurized causing one unloader, then the refrigeration portion of the many problems such as: equipment is capable of unloading to about 25% of unit capacity. Therefore the designer should make (cid:127) Preventing intended fresh intake for ventilation from sure the system will use 25% of the system cfm for entering the unit. comfort conditioning and bypass 75% of the condi- (cid:127) Preventing proper operation of the economizer and tioned air before energizing the compressors. This causing mechanical cooling to energize needlessly. will ensure that the system will have enough return air (cid:127) Preventing proper mixing of bypass air and return air mixing with the bypassed air to keep the compressor resulting in low return temperatures in cooling, and running. Make sure that the compressor does not high return temperature in heating. cycle too frequently based on the leaving air tempera- If the diversity within the space does not vary much, then ture limits since this could lessen the reliability of the bypass can be installed as shown in the diagram below suc- compressors. The heating equipment will only be able cessfully. Care must be taken to ensure that maximum by- to unload 50%. The system may be designed to cycle pass air at part load conditions does not exceed 25% of the based on the leaving air temperature limits depending full load airflow. on the rise designed in the heat exchanger and the amount of outside air being brought in. Although this The bypass junction must be installed with sufficient duct is not efficient, the equipment reliability should not be length between it and the unit to allow complete mixing of a problem. the bypass air an the return air. Without adequate mixing, comfort control will be lost as the equipment will be cycled off and equipment failures may result if left at the extremes. When the HVAC equipment uses an economiz- er, a back draft damper needs to be installed between the connection of the bypass duct and the closet room return air grille. VVT BYPASS DESIGN DUCTED RETURN LAYOUT FOR MANUFACTURING OFFICE LOCATE RETURN/BYPASS JUNCTION A MINIMUM OF 15 FT. FROM UNIT OUTLET ROOFTOP AVOID THE TEMPTATION UNIT TO INSTALL A SHORT-CIRCUIT BYPASS HERE. IT WILL CAUSE RETURN BACK DRAFT NUISANCE TRIPS WITH ZONE DAMPER CAPACITY INTERRUPTION BYPASS DAMPER * STATIC PRESSURE SENSOR AND BYPASS DAMPER ACTUATOR 5-CONDUCTOR S C H A I B E L L E D ( E 2 D 4V) T BC L 5 O D C U A C T T E D P IA IC M K E U T P E I R N S A D R O EA W O N F S T L R E E A A S M T T O U F R B B Y U P L A E S N S CE, TAKEOFF BUT UPSTREAM OF FIRST ZONE TAKEOFF OR MAJOR JUNCTION *SIZE BYPASS DUCT TO HANDLE STATIC STATIC 100% OF BLOCK PEAK CFM AT PRESSURE PRESSURE 1000 FPM OR LESS TUBING PICKUP 45
46 | Controls (cont) 2. Be sure to verify the pressure drop across the bypass Leaving-air temperature (LAT) monitoring must be al- when in full bypass. The bypass should maintain the ways used. This function prevents the HVAC equipment system pressure without causing 100% of the air to from operating in a range that will cause equipment safety be bypassed. Tables are provided in the Comfort Sys- trips, leading to shortened equipment life. tems Controls manual which will indicate the sound The Constant Volume Electric Cooling/Heating table and performance criteria of Carrier dampers. Calcu- provides the recommended cooling and heating limits that late bypass of 2124 L/s (4500 cfm) on a unit with a the monitor thermostat configures for 4.5, First Stage nominal airflow of 2832 L/s (6000 cfm) and external Cooling Limit; 4.6, Second Stage Cooling Limit; 4.7, First static pressure of 0.125 kPa (0.50 in. wg). The Stage Heating Limit; and 4.8, Second Stage Heating ZD-16 has two entries in the table of 1475 and 1574. Limit. Three ZD-16 dampers in parallel could be used for There are tradeoffs involved in the selection of the sys- the job. The 406 mm (16-in.) damper will not operate tem mode demand, monitor thermostat configurations full open to produce these results, so it will be neces- 4.15. Lower setting levels tend to improve comfort but sary to balance the system and set the maximum tend to increase operating costs and reduce equipment re- damper position to achieve these results in the field. liability. Buildings that have large core areas that are likely 3. These airflows were tested at 0.125 kPa (0.50 in. wg) to make a call when others are not should use lower system and provided NC levels of 42 and 44 respectively. A mode demand levels. For buildings with zones that have noise criteria of around 40 would be acceptable for a more similar load patterns from zone to zone, or smaller ducted bypass with internally lined duct but probably zones or more uniformly sized zones, a higher setting not for externally lined ducts since the noise could be should be used. transmitted to the return registers. Duct design is CATEGORY 4.0 HVAC EQUIPMENT — important to consider in bypass design since DEFAULT SETTINGS improper noise levels can require the use of other dampers to achieve the same bypassed airflow with SETTING DESCRIPTION CURRENT DEFAULT reduced noise. For the example above, two 35D, 4.1 Fan Operation Off 406 mm (16-in.) dampers can move the same air at a 4.2 Time Guard® Device between modes On NC level of 29.5 Radiated. These dampers can be 4.3 Time Guard Device Override Off ordered with sound attenuators to lessen radiated 4.4 LAT Monitoring On 4.5 First Stage Cooling Limit (F) 70 F noise also. Use the damper test criteria to make the 4.6 Second Stage Cooling Limit 60 F selection. 4.7 First Stage Heating Limit 97 F 4. If designing a system with an economizer, be sure to 4.8 Second Stage Heating Limit 110 F 4.9 Auxiliary Relay (0=No Control, 0 include power exhaust on the equipment to prevent 1=Occupied Schedule, 2=IAQ, conditioned air from migrating out the return registers 3=Reversing Valve, 4=Economizer) into the space in a over pressure condition. This con- 4.10 Optimize Staging On 4.11 Cooling Temperature Lockout On dition can be identified since the doors will most likely 4.12 Cooling Lockout Set Point 45 F stand open. The same condition can occur if there is 4.13 Heating Temperature Lockout Off a large exhaust system in the building for labs or 4.14 Heating Lockout Set Point 60 F restrooms. 4.15 System Mode Demand 3 4.16 System Mode Re-Select (minutes) 30 Monitor thermostat configuration — The monitor 4.17 Minimum Heat Run Time 5 thermostat controls the operation of its own zone and of 4.18 Minimum Cool Run Time 3 each associated zone controller. The monitor thermostat 4.19 Pre-Occupancy Purge Off 4.20 Fan Switch (0=Thermostat Switch Position, 0 determines system operation from the information re- 1=Fan Switch On, 2=Fan Switch Off) ceived from each device that it controls. The monitor ther- 4.21 Cool Switch (0=Thermostat Switch Position, 0 mostat must be configured for proper control of the sys- 1=Cool Switch Auto, 2=Cool Switch Off) 4.22 Heat Switch (0=Thermostat Switch Position, 0 tem. Part of the configuration is Category 4.0, which deals 1=Heat Switch Auto, 2=Heat Switch Off) with HVAC settings. The Category 4.0 HVAC Equipment table shows the default settings for this category. NOTE: In the majority of cases only categories 4.5, 4.6, 4.7, 4.8 and 4.15 will require changing by the installer. 46
47 | DX coil sensor installation — The use of a DX coil sen- These units use a TXV metering device. sor is recommended. The DX temperature sensor should Electrical connection from the VVT® system to the units be installed in the ductwork as close to the equipment as will be the typical thermostat connections from the relay possible. Care must be taken not to have the sensor within pack to the unit. “line of sight” of the equipment’s heating elements. Radia- Refer to the table below for LAT set points. tion from the heat can cause the sensor to read an elevated reading. CONSTANT VOLUME (CV) The majority of the units referred to by these application ELECTRIC COOLING/HEATING guidelines are two-compressor units. The monitor thermo- CATEGORY 4.0 HVAC SETTINGS (LAT) stat has the ability to read only one DX coil sensor, which UNIT HEATER 4.5 4.6 4.7 4.8 50TJ kW can only be installed within the equipment on a single F C F C F C F C compressor unit. All of the LAT settings have been deter- 22.5 60 15.6 59 15.0 93 33.9 107 41.7 016 38.2 60 15.6 59 15.0 95 35.0 126 52.2 mined assuming supply duct temperatures versus coil tem- 55.4 60 15.6 59 15.0 114 45.6 147 63.9 peratures. Be sure the DX coil sensor option is turned on. 22.5 70 21.1 60 15.6 93 33.9 107 41.7 Category 5.6 under the monitor configurations, should be 024 38.2 70 21.1 60 15.6 103 39.4 126 52.2 ON. 55.4 70 21.1 60 15.6 114 45.6 147 63.9 22.5 70 21.1 59 15.0 90 32.2 100 37.8 50TJ application guidelines — The 50TJ units are 028 38.2 70 21.1 59 15.0 97 36.1 115 46.1 constant volume units and will require the use a bypass 55.4 70 21.1 59 15.0 108 42.2 135 57.8 damper and controller. Refer to page 44 for details regard- LAT — Leaving Air Temperature ing the use and installation of the bypass damper. 47
48 | Application data Ductwork Minimum ambient cooling operation temperature Ductwork should be attached to the curb on all units. Inte- rior installation may proceed before unit is set in place on Units are designed to operate at outdoor temperatures roof. If ductwork will be attached to the unit, do not drill in down to 4.4 C (40 F). To operate at lower outdoor-air tem- condensate drain pan area — leaks may result. See figures peratures, see product ordering data or contact your local on page 49 for information on field-installed concentric Carrier representative for appropriate accessory combina- ductwork when applicable. tions for specific applications. Electric heat Maximum operating outdoor-air temperature On 50TJ016-028 units with electric heat, a field-supplied For cooling, this temperature is 52 C (125 F) for 016 size, 90-degree elbow must be installed on the supply ductwork 52 C (125 F) for 024 size, and 48 C (118 F) for 028 size below the unit discharge connection. (52 C [125 F] with high ambient unit). Refer to the Cool- ing Capacity tables on pages 19-22 for further details. Thru-the-curb service connections Internal unit design Roof curb connections allow field power wires and control wires to enter through the roof curb opening. Due to Carrier’s internal unit design (draw-thru over the motor), air path, and specially designed motors, the full Thermostat horsepower (kilowatts) (maximum continuous bhp [maxi- Use of 2-stage cooling thermostat is recommended for all mum continuous bkW]) listed in the Physical Data table and units. A 2-stage cooling thermostat is required on units the notes following each Fan Performance table can be uti- with accessory economizer to provide integrated cooling. lized with extreme confidence. Heating-to-cooling changeover Using Carrier motors with the values listed in the Physi- cal and Fan Performance Data tables will not result in nui- All units are automatic changeover from heating to cooling sance tripping or premature motor failure. The unit war- when automatic changeover thermostat and subbase are ranty will not be affected. used. Apollo direct digital communicating controls Airflow The Apollo direct digital controls must be used with either Units are draw-thru on cooling and blow-thru on heating. a Carrier master or monitor thermostat. Maximum airflow The following functions (POINTS) can be read by the To minimize the possibility of condensate blow-off from accessory DataPORT™ or DataLINK™ devices. Below are evaporator, airflow through units should not exceed the typical points that can be accessed from a TEMP ther- 67.1 L/s per kW (500 cfm/nominal ton) on size 016 and mostat (33CSTM--01) or TEMP Monitor thermostat 024 units, and 5311 L/s (11,250 cfm) on size 028 units. (33CSTM--01). Points that have read/write capability can be forced by the user. Minimum airflow The minimum airflow for cooling is 40 L/s per kW (300 cfm/nominal ton) on size 016 and 024 units and 38 L/s per kW (280 nominal cfm/ton) on size 028 units. 48
49 | POINTS DISPLAY TABLE VARIABLE DESCRIPTION UNIT DISPLAY POINT NAME READ/WRITE CAPABILITY Zone Temperature °F ZT Yes Duct Temperature °F DT Yes Outside Air Temperature °F OAT Yes Zone Demand °F ZDMD Read Only Demand Type Cool/Heat DMDTYPE Read Only Controller Set Point °F SETPOINT Read Only Occupied Yes/No OCC Yes Damper Position 0-15 DPOS Yes System Cool Stage 1 On/Off C1 Read Only System Cool Stage 2 On/Off C2 Read Only System Heat Stage 1 On/Off H1 Read Only System Heat Stage 2 On/Off H2 Read Only System Fan On/Off FN Yes* Auxiliary Relay On/Off AUX Yes† System Fan Status On/Off SFANS Read Only DX Coil Temperature °F DX Yes Filter Status Clean/Dirty FILS Yes System IAQ Status Normal/Alarm IAQLOG Yes Zone in IAQ Status Yes/No ZONEIAQ Read Only Any Zone in IAQ Yes/No ANYIAQ Read Only Indoor Relative Humidity % RH Yes Outdoor Relative Humidity % OARH Read Only HVAC Usage Meter Minutes UMHVAC Yes Override Usage Meter Minutes UMUO Yes HVAC Override Usage Meter Minutes UMUOSM Yes *Forcing the system fan will cause any energized system stages to turn off. †If Auxiliary Relay is configured as 0 or 1, then the point can be forced with no other effect. Other configurations will cause system stages and fan to turn off. CONCENTRIC DUCT AIR DISTRIBUTION CONCENTRIC DUCT DETAILS 576 1757 1890 (1’-10 11/16”) MAX. (5’-9 3/16”) MAX. (6’-2 3/8”) MAX. 310 132 (1’-0 3/16”) (5 3/16”) 1392 506 (4’-6 13/16”) (1’-7 15/16”) 310 (1’-0 3/16”) B 610 B’ (24”) MIN. A A’ BAFFLE Shaded area indicates block-off panels. NOTE: Do not drill in this area, damage to basepan may result in NOTES: water leak. 1. Dimensions A, A′ and B, B′ are obtained from field-supplied ceiling diffuser. 2. Dimensions are in millimeters. Concentric ducts may only be installed on units without electric heat. Personal injury or unit damage may result. 49
50 | Application data (cont) Condenser coil protection (Enviro-Shield™) E-coated aluminum-fin coils have an extremely flexible and durable epoxy coating uniformly applied to all coil sur- Pre-coated aluminum-fin coils have a durable epoxy- faces. Unlike brittle phenolic dip and bake coatings, E-coat phenolic coating applied to the fin prior to the fin stamping provides superior protection with unmatched flexibility, process to provide protection in mildly corrosive coastal edge coverage, metal adhesion, thermal performance and, environments. Pre-coated coils have an inert barrier be- most importantly, corrosion resistance. E-coated coils pro- tween the aluminum fin and copper tube. This barrier elec- vide this protection since all coil surfaces are completely trically disconnects the dissimilar metals to minimize the encapsulated from environmental contamination. Specify potential for galvanic corrosion. This economical option E-coated aluminum-fin coils for industrial environments provides substantial corrosion protection beyond the with high levels of air pollution. This option also provides standard uncoated coil construction. better protection compared to standard or pre-coated Copper-fin coils provide increased corrosion resistance aluminum-fin coils in industrial environments. in moderate coastal environments where industrial air pol- lution is not present. All copper coils eliminate bi-metallic E-coated copper-fin coils have the same flexible and du- rable epoxy coating as E-coated aluminum-fin coils. How- construction to eliminate the potential for galvanic corro- ever, this option combines the natural salt and environmen- sion. Application in industrial environments is not recom- tal resistance of all-copper construction with the highest mended due to potential attack from sulfur, sulfur oxide, level of corrosion protection. Specify E-coated copper-fin nitrogen oxides, carbon and several other industrial air- coils in the harshest combination of coastal and industrial borne contaminants. In moderate seacoast environments, environments. copper-fin coils have extended life compared to standard or pre-coated aluminum-fin coils. 50
51 | Guide specifications — 50TJ016-028 Packaged Rooftop Electric Cooling Unit with B. Unit Cabinet: Electric or Glycol Heat — Constant Volume 1. Unit cabinet shall be constructed of galvanized Application steel, bonderized and coated with a prepainted baked enamel finish. HVAC Guide Specifications 2. Indoor blower compartment interior surfaces Size Range: 52.8 to 87.9 kW (15 to 25 Tons), shall be insulated with a minimum 1/ -in. Nominal (Cooling) 2 (13 mm) thick, 1 lb (.45 kg) density neoprene 20 to 60 kW (Electric Heat) coated, fiberglass insulation coated on the air 123,000 to 405,000 Btuh side. (Glycol Heating) 3. Cabinet panels shall be easily removable for Carrier Model Numbers: 50TJ servicing. Cabinet panels are a minimum of 20 gage. Panels shall have 1-in. thick, 1.5-lb Part 1 — General density insulation. 1.01 SYSTEM DESCRIPTION 4. Filters shall be accessible through an access Unit is an outdoor rooftop mounted, electrically con- panel. trolled heating and cooling unit utilizing scroll her- 5. Holes shall be provided in the base rails for rig- metic compressors for cooling duty and optional ging shackles to facilitate overhead rigging. electric resistance heaters or glycol coil for heating 6. Unit shall have a factory-installed internal con- duty. Supply air shall be discharged downward or densate drain connection and a sloped conden- horizontally (with horizontal supply/return roof curb sate pan in accordance with ASHRAE assembly), as shown on contract drawings. Standard Standard 62 (U.S.A. Standard). unit shall include a manual outdoor-air inlet. C. Fans: 1.02 QUALITY ASSURANCE 1. Indoor blower (evaporator fan): A. Unit (sizes 016 and 024) shall be rated in accor- a. Fan shall be belt driven. Belt drive shall dance with ARI Standards 270 and 360 and all units include an adjustable pulley. The standard shall be designed in accordance with UL Standard fan drive shall have a factory-installed low- 1995 (U.S.A.). medium static pressure fan drive. The alter- NOTE: The 50TJ028 is beyond the scope of the nate fan drive option shall have a factory- ARI certification program. installed high static pressure fan drive. B. Unit shall be designed to conform to ASHRAE 15. Motors shall be 3-phase and open drip proof C. Unit shall be ETL (U.S.A.) tested and certified in design with class B insulation. accordance with ANSI Z21.47 Standards as a total b. Fan wheel shall be made from steel with a package. corrosion resistant finish. It shall be a D. Roof curb shall be designed to conform to NRCA dynamically balanced, double-inlet type with Standards (U.S.A.). forward-curved blades. E. Insulation and adhesive shall meet NFPA 90A re- 2. Condenser fans shall be of the direct-driven quirements (U.S.A.) for flame spread and smoke propeller type, with corrosion-resistant blades generation. riveted to corrosion-resistant steel supports. They shall be dynamically balanced and F. Unit casing shall be capable of withstanding discharge air upwards. Motors shall be 3-phase 500-hour salt spray exposure per ASTM B117 and open drip proof design with class B (scribed specimen) (U.S.A.). insulation. G. Unit shall be manufactured in a facility registered to 3. Optional condenser fan motors (028 size only) ISO 9002/BS5750, Part 2. shall be 3-phase and totally enclosed with class 1.03 DELIVERY, STORAGE, AND HANDLING F insulation. Unit shall be stored and handled per manufacturer’s D. Compressor(s): recommendations. 1. Fully hermetic Copeland, scroll type, internally protected. Part 2 — Products 2. Factory spring-shock mounted and internally 2.01 EQUIPMENT (STANDARD) spring mounted for vibration isolation. A. General: 3. On electrically and mechanically independent The 50TJ unit shall be a factory assembled, single- refrigerant circuits. piece heating and cooling unit. Contained within the E. Coils: unit enclosure shall be all factory wiring, piping, 1. Standard evaporator and condenser coils shall controls, refrigerant charge (R-22), and special fea- have aluminum plate fins mechanically bonded tures required prior to field start-up. to seamless internally grooved copper tubes with all joints brazed. 51
52 | Guide specifications — 50TJ016-028 (cont) 2. All coils shall be leak tested at 1034 kPa Coil construction shall be copper fins mechani- (150 psig) and pressure tested at 3103 kPa cally bonded to copper tubes. (450 psig). F. Refrigerant Components: 3. Optional pre-coated aluminum-fin coils shall Refrigerant circuit components shall include: have a durable epoxy-phenolic coating to pro- 1. Thermostatic expansion valve (TXV). vide protection in mildly corrosive coastal envi- ronments. Coating shall be applied to the 2. Filter driers. aluminum fin stock prior to the fin stamping 3. Gage port and connections on suction, dis- process to create an inert barrier between the charge, and liquid lines. aluminum fin and copper tube. Epoxy-phenolic G. Filter Section: barrier shall minimize galvanic action between Standard filter section shall consist of 2 sizes of dissimilar metals. factory-installed 51 mm (2-in.) thick throwaway 4. Optional copper-fin coils shall be constructed of fiberglass filters (8 to 10% efficiency, when clean) of copper-fins mechanically bonded to copper- commercially available sizes. tubes and copper tube sheets. Galvanized steel H. Controls and Safeties: tube sheets shall not be acceptable. A polymer strip shall prevent coil assembly from contacting 1. Unit Controls: sheet metal coil pan to minimize potential for a. Economizer control (optional). galvanic corrosion between the coil and pan. All b. Capacity control (2-step). copper construction shall provide protection in c. Unit shall be complete with self-contained moderate coastal environments. low-voltage control circuit. 5. Optional E-coated aluminum-fin coils shall have 2. Safeties: a flexible epoxy polymer coating uniformly applied to all coil surface areas without mate- a. Unit shall incorporate a solid-state compres- rial bridging between fins. Coating process shall sor lockout which provides reset capability at ensure complete coil encapsulation. Color shall the space thermostat, should any of the fol- be high gloss black with gloss requirements of lowing safety devices trip and shut off 60° of 65 to 90% per ASTM D523-89. Uni- compressor: form dry film thickness from 0.8 to 1.2 mil on 1) Compressor lockout protection provided all surface areas including fin edges. Superior for either internal or external overload. hardness characteristics of 2H per ASTM 2) Low-pressure switch, cutout at 186 kPa D3363-92A and cross hatch adhesion of 4B- (27 psig). 5B per ASTM D3359-93. Impact resistance 3) Freezestats (evaporator coil), dual. shall be up to 160 in./lb (ASTM D2794-93). 4) High-pressure switch, cutout at 2951 kPa Humidity and water immersion resistance shall (426 psig). be up to a minimum of 1000 and 250 hours b. Supply-air thermostat shall be located in the respectively (ASTM D2247-92 and ASTM unit. D870-92). Corrosion durability shall be con- firmed through testing to no less than 1000 c. Heating section shall be provided with the hours salt spray per ASTM B117-90. Coil con- following minimum protections: struction shall be aluminum fins mechanically 1) High-temperature limit switch. bonded to copper tubes. 2) Overcurrent protection. 6. Optional E-coated copper-fin coils shall have a I. Operating Characteristics: flexible epoxy polymer coating uniformly 1. Unit shall be capable of starting and running at applied to all coil surface areas without material 52 C (125 F) for 016 size, 52 C (125 F) for bridging between fins. Coating process shall 024 size, and 48 C (118 F) for 028 size, ambi- ensure complete coil encapsulation. Color shall ent outdoor temperature per maximum load cri- be high gloss black with gloss requirements of teria of ARI Standard 360. 60° of 65 to 90% per ASTM D523-89. 2. Unit with standard controls will operate in cool- Uniform dry film thickness from 0.8 to 1.2 mil ing down to an outdoor ambient temperature of on all surface areas including fin edges. 4.4 C (40 F). Superior hardness characteristics of 2H per ASTM D3363-92A and cross hatch adhesion 3. Unit shall be provided with fan time delay to of 4B-5B per ASTM D3359-93. Impact resis- prevent cold air delivery. tance shall be up to 160 in./lb (ASTM D2794- J. Electrical Requirements: 93). Humidity and water immersion resistance All unit power wiring shall enter unit cabinet at a sin- shall be up to a minimum of 1000 and gle location. 250 hours respectively (ASTM D2247-92 and ASTM D870-92). Corrosion durability shall be confirmed through testing to no less than 1000 hours salt spray per ASTM B117-90. 52
53 | K. Motors: e. Equipped with a mixed-air sensor that con- trols the economizer to a 30.5 C (55 F) con- 1. Compressor motors shall be cooled by refriger- trol point. ant gas passing through motor windings and shall have line break thermal and current over- f. Outdoor air opening is 450.85 mm x load protection. 1813.05 mm (17.75-in. x 71.38-in.), and 2. All fan motors shall have permanently lubri- 0.82 m2 (8.8 ft2). cated, sealed bearings and inherent automatic- g. Damper motor is 24-v, spring-return type reset thermal overload protection or manual design (close on loss of power). reset calibrated circuit breakers. 5. Two-Position Damper: 3. All indoor-fan motors 5 hp and larger shall Two-position damper package shall include sin- meet the minimum efficiency requirements as gle blade damper and motor. Admits up to 25% established by the Energy Policy Act of 1992 outdoor air, and shall close upon unit shutoff. (EPACT) (U.S.A.) effective October 24, 1997. Outdoor air opening is 96.52 mm x 965.20 L. Special Features: mm (3.80-in. x 31.00-in.), and 7599.98 mm2 Certain features are not applicable when the fea- (117.8 in.2). tures designated * are specified. For assistance in 6. Accessory Compressor Cycle Delay: amending the specifications, contact your local Compressor shall be prevented from restarting Carrier Sales Office. for a minimum of 5 minutes after shutdown. * 1. Direct Digital Communicating Controls: * 7. Thermostats and Subbases: a. Shall be available as a factory-installed To provide staged heating and cooling in addi- option. tion to automatic (or manual) changeover and b. Shall actively monitor all modes of opera- fan control. tion, as well as evaporator-fan status, filter * 8. Barometric Relief Damper Package: status, indoor-air quality, supply-air tempera- a. Package shall include damper, seals, hard- ture, and outdoor-air temperature. ware, and hoods to relieve excess internal c. Shall work with Carrier TEMP and VVT® pressure. (variable volume and temperature) systems. b. Damper shall close due to gravity upon unit d. Shall have built-in diagnostics for thermostat shutdown. commands for both staged heating and cool- * 9. Power Exhaust: ing, evaporator-fan operation, and econo- mizer operation. Package shall include an exhaust (propeller style) fan, 0.37 kW (1/ Hp) motor, and damper e. Shall be equipped with a 5-minute time 2 for vertical flow units with economizer to con- delay between modes of operation. trol overpressurization of building. 2. Roof Curbs (Horizontal and Vertical): *10. Head Pressure Control Package: a. Formed of 16-gage galvanized steel with Consists of an accessory outdoor-air package wood nailer strip and shall be capable of and a solid-state control with condenser coil supporting entire unit weight. temperature sensor for controlling condenser- b. Permits installing and securing ductwork to fan motor speed to maintain condensing tem- curb prior to mounting unit on the curb. perature between 32.2 C (90 F) and 43.3 C 3. Horizontal Adapter Roof Curb: (100 F) at outdoor ambient temperature down Includes factory-assembled adapter and duct to –28.9 C (–20 F). and substantially improves evaporator fan static 11. Low-Ambient Kits: performance. When used, allows units to operate at lower * 4. Integrated Economizer: outdoor ambient temperatures. a. Integrated type capable of simultaneous *12. Enthalpy Sensor: economizer and compressor operation to a. For use with economizer only. provide cooling with outdoor air. b. Capable of comparing heat content (temper- b. Equipped with low-leakage dampers not to ature and humidity) of outdoor air and exceed 3% leakage, at 249 Pa (1.0 in. wg) indoor air and controlling economizer cut-in pressure differential. point at the most economical level. c. Capable of introducing up to 100% outdoor NOTE: Two accessory enthalpy sensors are air. required for differential enthalpy control. d. Equipped with dry-bulb temperature control *13. Electronic Programmable Thermostat: to govern economizer changeover. Capable of using deluxe full-featured electronic thermostat. 53
54 | Guide specifications — 50TJ016-028 (cont) 14. Winter Start Time-Delay Relay: access door. Shall be accessible from outside the unit and shall provide power off lockout Used in conjunction with the accessory low- capability. ambient kit or head pressure control device, permits operation in cooling at lower outdoor 16. Electric Heater Package: ambient temperatures. See product ordering Fully assembled for installation. The packages data for more information. are designed in accordance with UL standards 15. Service Option Package: and all units feature a single point connection. NOTE: These items can be ordered as one 17. Glycol Coil: package or separately. Coil shall be 2-row copper tube (1/ -in. OD) with 2 a. Hinged access panels for the filter, compres- aluminum plate fins (590 fins/m; 15 fins/in.) and sors, evaporator fan, and control box areas. (41.28 mm; 1.625 in. OD) copper headers. Input Filter hinged access panels permit tool-less and output connections shall be (41.28 mm; entry for changing filters. Evaporator fan 1.625 in. ODM) copper stubs for sweat connec- hinged access panel shall be field-convertible tions. Coil shall be furnished with suitable support to a tool-less entry by removing and discard- rails, end plates, and hardware for ready field ing screws. Each external hinged access installation in heater compartment. panel shall be permanently attached to the 18. Alternate Drive: rooftop unit. Shall provide higher static drive capability to b. Non-fused disconnect switch: Shall be fac- enhance evaporator-fan performance rpm tory-installed, internally-mounted, NEC and range. UL approved non-fuse switch shall provide 19. Hail Guard, Condenser Coil Grille: unit power shutoff. The control access door shall be interlocked with the non-fused dis- Shall protect the condenser coil from hail, flying connect. The disconnect switch must be in debris, and damage by large objects without the OFF position to open the control box increasing unit clearances. 54
55 | 55
56 | Carrier Corporation (cid:127) Syracuse, New York 13221 12-00 Manufacturer reserves the right to discontinue, or change at any time, specifications or designs without notice and without incurring obligations. Book 1 New Book 1 Pg 56 Catalog No. 005-001 Printed in U.S.A. F orm 5 0TJ-C11PD Tab 1b Tab OP2b Replaces: 50TJ-C10PD

## Extracted_Tables
source_page | table_no | page_title | row_no | column_no | cell_value
4 | 1 | Capacity ratings | 1 | 1 | MINIMUM
4 | 1 | Capacity ratings | 2 | 1 | L/s
4 | 1 | Capacity ratings | 2 | 2 | cfm
4 | 1 | Capacity ratings | 2 | 3 | L/s
4 | 1 | Capacity ratings | 3 | 1 | 2125
4 | 1 | Capacity ratings | 3 | 2 | 4500
4 | 1 | Capacity ratings | 3 | 3 | 3525
4 | 1 | Capacity ratings | 4 | 1 | 2800
4 | 1 | Capacity ratings | 4 | 2 | 6000
4 | 1 | Capacity ratings | 4 | 3 | 4800
4 | 1 | Capacity ratings | 5 | 1 | 3300
4 | 1 | Capacity ratings | 5 | 2 | 7000
4 | 1 | Capacity ratings | 5 | 3 | 5300
4 | 2 | Capacity ratings | 1 | 1 | HEATER kW Unit Voltage
4 | 2 | Capacity ratings | 1 | 4 | HEATER STAGES
4 | 2 | Capacity ratings | 1 | 5 | % HEAT PER STAGE
4 | 2 | Capacity ratings | 1 | 6 | MAXIMUM STAGES*
4 | 2 | Capacity ratings | 2 | 1 | 380
4 | 2 | Capacity ratings | 2 | 2 | 400
4 | 2 | Capacity ratings | 2 | 3 | 416
4 | 2 | Capacity ratings | 2 | 7 | L/s
4 | 2 | Capacity ratings | 3 | 1 | 20.3
4 | 2 | Capacity ratings | 3 | 2 | 22.5
4 | 2 | Capacity ratings | 3 | 3 | 24.3
4 | 2 | Capacity ratings | 3 | 4 | 2
4 | 2 | Capacity ratings | 3 | 5 | 50/50
4 | 2 | Capacity ratings | 3 | 6 | 2
4 | 2 | Capacity ratings | 3 | 7 | 2124
4 | 2 | Capacity ratings | 4 | 1 | 34.5
4 | 2 | Capacity ratings | 4 | 2 | 38.2
4 | 2 | Capacity ratings | 4 | 3 | 41.1
4 | 2 | Capacity ratings | 4 | 4 | 2
4 | 2 | Capacity ratings | 4 | 5 | 67/33
4 | 2 | Capacity ratings | 4 | 6 | 3
4 | 2 | Capacity ratings | 5 | 1 | 50
4 | 2 | Capacity ratings | 5 | 2 | 55.4
4 | 2 | Capacity ratings | 5 | 3 | 59.7
4 | 2 | Capacity ratings | 5 | 4 | 2
4 | 2 | Capacity ratings | 5 | 5 | 50/50
4 | 2 | Capacity ratings | 5 | 6 | 4
4 | 2 | Capacity ratings | 6 | 1 | 20.3
4 | 2 | Capacity ratings | 6 | 2 | 22.5
4 | 2 | Capacity ratings | 6 | 3 | 24.3
4 | 2 | Capacity ratings | 6 | 4 | 2
4 | 2 | Capacity ratings | 6 | 5 | 50/50
4 | 2 | Capacity ratings | 6 | 6 | 2
4 | 2 | Capacity ratings | 6 | 7 | 2832
4 | 2 | Capacity ratings | 7 | 1 | 34.5
4 | 2 | Capacity ratings | 7 | 2 | 38.2
4 | 2 | Capacity ratings | 7 | 3 | 41.1
4 | 2 | Capacity ratings | 7 | 4 | 2
4 | 2 | Capacity ratings | 7 | 5 | 67/33
4 | 2 | Capacity ratings | 7 | 6 | 3
4 | 2 | Capacity ratings | 8 | 1 | 50
4 | 2 | Capacity ratings | 8 | 2 | 55.4
4 | 2 | Capacity ratings | 8 | 3 | 59.7
4 | 2 | Capacity ratings | 8 | 4 | 2
4 | 2 | Capacity ratings | 8 | 5 | 50/50
4 | 2 | Capacity ratings | 8 | 6 | 4
4 | 2 | Capacity ratings | 9 | 1 | 20.3
4 | 2 | Capacity ratings | 9 | 2 | 22.5
4 | 2 | Capacity ratings | 9 | 3 | 24.3
4 | 2 | Capacity ratings | 9 | 4 | 2
4 | 2 | Capacity ratings | 9 | 5 | 50/50
4 | 2 | Capacity ratings | 9 | 6 | 2
4 | 2 | Capacity ratings | 9 | 7 | 3303
4 | 2 | Capacity ratings | 10 | 1 | 34.5
4 | 2 | Capacity ratings | 10 | 2 | 38.2
4 | 2 | Capacity ratings | 10 | 3 | 41.1
4 | 2 | Capacity ratings | 10 | 4 | 2
4 | 2 | Capacity ratings | 10 | 5 | 67/33
4 | 2 | Capacity ratings | 10 | 6 | 3
4 | 2 | Capacity ratings | 11 | 1 | 50
4 | 2 | Capacity ratings | 11 | 2 | 55.4
4 | 2 | Capacity ratings | 11 | 3 | 59.7
4 | 2 | Capacity ratings | 11 | 4 | 2
4 | 2 | Capacity ratings | 11 | 5 | 50/50
4 | 2 | Capacity ratings | 11 | 6 | 4
5 | 1 | Physical data — SI | 1 | 1 | 16
5 | 1 | Physical data — SI | 1 | 2 | 24
5 | 1 | Physical data — SI | 1 | 3 | 028 (Standard)
5 | 1 | Physical data — SI | 2 | 1 | 52.8
5 | 1 | Physical data — SI | 2 | 2 | 70.3
5 | 1 | Physical data — SI | 2 | 3 | 87.9
6 | 1 | Physical data — English | 1 | 1 | 16
6 | 1 | Physical data — English | 1 | 2 | 24
6 | 1 | Physical data — English | 1 | 3 | 028 (Standard)
6 | 1 | Physical data — English | 2 | 1 | 15
6 | 1 | Physical data — English | 2 | 2 | 20
6 | 1 | Physical data — English | 2 | 3 | 25
7 | 1 | Physical data (cont) | 1 | 1 | 16
7 | 1 | Physical data (cont) | 1 | 3 | 24
7 | 1 | Physical data (cont) | 2 | 1 | lb
7 | 1 | Physical data (cont) | 2 | 2 | kg
7 | 1 | Physical data (cont) | 2 | 3 | lb
7 | 1 | Physical data (cont) | 2 | 4 | kg
7 | 1 | Physical data (cont) | 2 | 5 | lb
7 | 1 | Physical data (cont) | 3 | 1 | 1560
7 | 1 | Physical data (cont) | 3 | 2 | 708
7 | 1 | Physical data (cont) | 3 | 3 | 1800
7 | 1 | Physical data (cont) | 3 | 4 | 816
7 | 1 | Physical data (cont) | 3 | 5 | 1950
7 | 2 | Physical data (cont) | 1 | 1 | 16
7 | 2 | Physical data (cont) | 1 | 3 | 24
7 | 2 | Physical data (cont) | 2 | 1 | lb
7 | 2 | Physical data (cont) | 2 | 2 | kg
7 | 2 | Physical data (cont) | 2 | 3 | lb
7 | 2 | Physical data (cont) | 2 | 4 | kg
7 | 2 | Physical data (cont) | 2 | 5 | lb
7 | 2 | Physical data (cont) | 3 | 1 | 50
7 | 2 | Physical data (cont) | 3 | 2 | 23
7 | 2 | Physical data (cont) | 3 | 3 | 50
7 | 2 | Physical data (cont) | 3 | 4 | 23
7 | 2 | Physical data (cont) | 3 | 5 | 50
7 | 2 | Physical data (cont) | 4 | 1 | 150
7 | 2 | Physical data (cont) | 4 | 2 | 68
7 | 2 | Physical data (cont) | 4 | 3 | 150
7 | 2 | Physical data (cont) | 4 | 4 | 68
7 | 2 | Physical data (cont) | 4 | 5 | 150
7 | 2 | Physical data (cont) | 5 | 1 | 280
7 | 2 | Physical data (cont) | 5 | 2 | 127
7 | 2 | Physical data (cont) | 5 | 3 | 280
7 | 2 | Physical data (cont) | 5 | 4 | 127
7 | 2 | Physical data (cont) | 5 | 5 | 280
7 | 2 | Physical data (cont) | 6 | 1 | 110
7 | 2 | Physical data (cont) | 6 | 2 | 50
7 | 2 | Physical data (cont) | 6 | 3 | 110
7 | 2 | Physical data (cont) | 6 | 4 | 50
7 | 2 | Physical data (cont) | 6 | 5 | 110
7 | 2 | Physical data (cont) | 7 | 1 | 50
7 | 2 | Physical data (cont) | 7 | 2 | 23
7 | 2 | Physical data (cont) | 7 | 3 | 50
7 | 2 | Physical data (cont) | 7 | 4 | 23
7 | 2 | Physical data (cont) | 7 | 5 | 50
7 | 2 | Physical data (cont) | 8 | 1 | 85
7 | 2 | Physical data (cont) | 8 | 2 | 39
7 | 2 | Physical data (cont) | 8 | 3 | 85
7 | 2 | Physical data (cont) | 8 | 4 | 39
7 | 2 | Physical data (cont) | 8 | 5 | 85
7 | 2 | Physical data (cont) | 9 | 1 | 200
7 | 2 | Physical data (cont) | 9 | 2 | 91
7 | 2 | Physical data (cont) | 9 | 3 | 200
7 | 2 | Physical data (cont) | 9 | 4 | 91
7 | 2 | Physical data (cont) | 9 | 5 | 200
7 | 2 | Physical data (cont) | 10 | 1 | 250
7 | 2 | Physical data (cont) | 10 | 2 | 113
7 | 2 | Physical data (cont) | 10 | 3 | 250
7 | 2 | Physical data (cont) | 10 | 4 | 113
7 | 2 | Physical data (cont) | 10 | 5 | 250
7 | 2 | Physical data (cont) | 11 | 1 | 343
7 | 2 | Physical data (cont) | 11 | 2 | 156
7 | 2 | Physical data (cont) | 11 | 3 | 343
7 | 2 | Physical data (cont) | 11 | 4 | 156
7 | 2 | Physical data (cont) | 11 | 5 | 343
7 | 2 | Physical data (cont) | 12 | 1 | 60
7 | 2 | Physical data (cont) | 12 | 2 | 27
7 | 2 | Physical data (cont) | 12 | 3 | 60
7 | 2 | Physical data (cont) | 12 | 4 | 27
7 | 2 | Physical data (cont) | 12 | 5 | 60
7 | 2 | Physical data (cont) | 13 | 1 | 144
7 | 2 | Physical data (cont) | 13 | 2 | 65
7 | 2 | Physical data (cont) | 13 | 3 | 144
7 | 2 | Physical data (cont) | 13 | 4 | 65
7 | 2 | Physical data (cont) | 13 | 5 | 144
8 | 1 | Options and accessories | 1 | 1 | OPTION*
8 | 1 | Options and accessories | 2 | 1 | X
8 | 1 | Options and accessories | 3 | 1 | X
8 | 1 | Options and accessories | 4 | 1 | X
8 | 1 | Options and accessories | 5 | 1 | X
8 | 1 | Options and accessories | 6 | 1 | X
8 | 1 | Options and accessories | 8 | 1 | X
8 | 2 | Options and accessories | 2 | 1 | HEAD PRESSURE CONTROL The 50TJ016-028 standard units are designed to operate in cooling at out- door temperatures down to 40 F (4.4 C). With accessory Motormaster III con- trol (condenser fan speed modulation) units can operate at outdoor temperatures down to –20 F (–28.9 C). The head pressure controls, which mount in the condenser section, control the condenser-fan motor to maintain correct condensing temperature. Refer to product ordering data or contact your local Carrier representative for appropriate accessory combinations for desired outdoor ambient temperature operation. MOTORMASTER III CONTROL
9 | 1 | FACTORY-INSTALLED APOLLO ACCUSENSOR™ III | 1 | 1 | FACTORY-INSTALLED APOLLO ACCUSENSOR™ III COMMUNICATING CONTROLS (Enthalpy and Differential Enthalpy Control) + Accusensor economizer controls help provide efficient, economical economizer operation. The unit economizer provides the decision- making function internally, and requires one Accusensor III sensor for solid-state enthalpy sensing. A second Accusensor III sensor The Apollo direct digital controls are designed exclusively by provides information for comparison of outdoor temperature and Carrier, and are used to actively monitor and control all modes of humidity to return-air temperature and humidity and determines the operation as well as to monitor evaporator-fan status, filter status, most economical mixture of air (purchased in addition to first solid- supply-air temperature, outdoor-air temperature, and indoor-air state enthalpy sensor for differential enthalpy sensing for all units). quality. They are designed to work in conjunction with Carrier TEMP and VVT® (Variable Volume/Variable Temperature) system thermostats. CARRIER COMMERCIAL THERMOSTAT ELECTRONIC PROGRAMMABLE THERMOSTAT Carrier’s electronic programmable thermostat provides efficient temperature control by allowing you to program heating and cooling setbacks and set ups with provi- Designed specifically for use with Carrier commercial systems, this sions for weekends and holidays. Accessory remote Carrier programmable thermostat features LED occupied/unoccupied sensing package is also available to provide tamper- displays and setback mode which can override continuous fan operation. proof control in high traffic spaces. Used in conjunction with factory-installed Apollo control, this thermostat provides a 5-minute recycle timer between modes of operation for short-cycle protection. TIME GUARD® II CONTROL Time Guard II Control automatically prevents compressor from restarting for at least 5 minutes after a shutdown. Accessory pre- vents short cycling of compressor if thermostat is changed rapidly. Time Guard II control mounts in the control compartment of unit.
10 | 1 | Options and accessories (cont) | 1 | 1 | Standard, on-Corrosive
10 | 1 | Options and accessories (cont) | 1 | 2 | Mild Coastal
10 | 1 | Options and accessories (cont) | 1 | 3 | Moderate Coastal
10 | 1 | Options and accessories (cont) | 1 | 4 | Severe Coastal
10 | 1 | Options and accessories (cont) | 1 | 5 | Industrial
10 | 1 | Options and accessories (cont) | 2 | 1 | X
10 | 1 | Options and accessories (cont) | 3 | 2 | X
10 | 1 | Options and accessories (cont) | 4 | 3 | X
10 | 1 | Options and accessories (cont) | 5 | 5 | X
10 | 1 | Options and accessories (cont) | 6 | 4 | X
11 | 1 | SERVICE OPTION PACKAGE* | 1 | 1 | SERVICE OPTION PACKAGE* UNIT-MOUNTED DISCONNECT HINGED ACCESS PANEL (CONTROL BOX SHOWN) Factory-installed, internally-mounted, NEC (National Electrical Code, U.S.A.) and UL (Underwriters’ Laboratories, U.S.A.) approved non-fused switch provides unit power shutoff with disconnect lockout protection capability. The control box access door is interlocked with the non-fused disconnect. The non-fused disconnect must be in the OFF position to open this door. The switch is accessible from out- side the unit. *These options are also available individually through the DEC.
13 | 1 | Base unit dimensions — 50TJ024,028 | 2 | 1 | LEGEND KO — Knockout NOTES: 1. Dimensions in ( ) are in millimeters. 2. Center of gravity. 3. Direction of airflow. 4. Ductwork to be attached to accessory roof 5. Minimum clearance: a. Rear: 7′-0″ (2134) for coil removal. Thi can be reduced to 4′-0″ (1219) if condi coil removal from the top. b. Left side: 4′-0″ (1219) for proper con airflow. c. Front: 4′-0″ (1219) for control box acces d. Right side: 4′-0″ (1219) for proper o damper and power exhaust (if so equip e. Top: 6′-0″ (1829) to assure proper co operation. f. Local codes or jurisdiction may prevail. 6. With the exception of clearance for the con and the damper/power exhaust as stated i removable fence or barricade requires no c 7. Dimensions are from outside of corner 0′-5/16 ″ (8) on each side for top cover drip e 8. A 90 degree elbow must be installed on ductwork below the unit discharge
13 | 3 | Base unit dimensions — 50TJ024,028 | 1 | 1 | CORNER WEIGHT*
13 | 3 | Base unit dimensions — 50TJ024,028 | 2 | 1 | A
13 | 3 | Base unit dimensions — 50TJ024,028 | 2 | 3 | B
13 | 3 | Base unit dimensions — 50TJ024,028 | 2 | 5 | C
13 | 3 | Base unit dimensions — 50TJ024,028 | 2 | 7 | D
13 | 3 | Base unit dimensions — 50TJ024,028 | 2 | 9 | X
13 | 3 | Base unit dimensions — 50TJ024,028 | 3 | 1 | Lb
13 | 3 | Base unit dimensions — 50TJ024,028 | 3 | 2 | Kg
13 | 3 | Base unit dimensions — 50TJ024,028 | 3 | 3 | Lb
13 | 3 | Base unit dimensions — 50TJ024,028 | 3 | 4 | Kg
13 | 3 | Base unit dimensions — 50TJ024,028 | 3 | 5 | Lb
13 | 3 | Base unit dimensions — 50TJ024,028 | 3 | 6 | Kg
13 | 3 | Base unit dimensions — 50TJ024,028 | 3 | 7 | Lb
13 | 3 | Base unit dimensions — 50TJ024,028 | 3 | 8 | Kg
13 | 3 | Base unit dimensions — 50TJ024,028 | 3 | 9 | Ft-in.
13 | 3 | Base unit dimensions — 50TJ024,028 | 3 | 10 | mm
13 | 3 | Base unit dimensions — 50TJ024,028 | 3 | 11 | Ft-in.
13 | 3 | Base unit dimensions — 50TJ024,028 | 4 | 1 | 423
13 | 3 | Base unit dimensions — 50TJ024,028 | 4 | 2 | 192
13 | 3 | Base unit dimensions — 50TJ024,028 | 4 | 3 | 412
13 | 3 | Base unit dimensions — 50TJ024,028 | 4 | 4 | 185
13 | 3 | Base unit dimensions — 50TJ024,028 | 4 | 5 | 490
13 | 3 | Base unit dimensions — 50TJ024,028 | 4 | 6 | 220
13 | 3 | Base unit dimensions — 50TJ024,028 | 4 | 7 | 475
13 | 3 | Base unit dimensions — 50TJ024,028 | 4 | 8 | 213
13 | 3 | Base unit dimensions — 50TJ024,028 | 4 | 9 | 3-3
13 | 3 | Base unit dimensions — 50TJ024,028 | 4 | 10 | 991
13 | 3 | Base unit dimensions — 50TJ024,028 | 4 | 11 | 3-7
13 | 3 | Base unit dimensions — 50TJ024,028 | 5 | 1 | 441
13 | 3 | Base unit dimensions — 50TJ024,028 | 5 | 2 | 200
13 | 3 | Base unit dimensions — 50TJ024,028 | 5 | 3 | 416
13 | 3 | Base unit dimensions — 50TJ024,028 | 5 | 4 | 189
13 | 3 | Base unit dimensions — 50TJ024,028 | 5 | 5 | 533
13 | 3 | Base unit dimensions — 50TJ024,028 | 5 | 6 | 242
13 | 3 | Base unit dimensions — 50TJ024,028 | 5 | 7 | 560
13 | 3 | Base unit dimensions — 50TJ024,028 | 5 | 8 | 254
13 | 3 | Base unit dimensions — 50TJ024,028 | 5 | 9 | 3-1
13 | 3 | Base unit dimensions — 50TJ024,028 | 5 | 10 | 940
13 | 3 | Base unit dimensions — 50TJ024,028 | 5 | 11 | 3-6
13 | 3 | Base unit dimensions — 50TJ024,028 | 6 | 1 | 441
13 | 3 | Base unit dimensions — 50TJ024,028 | 6 | 2 | 200
13 | 3 | Base unit dimensions — 50TJ024,028 | 6 | 3 | 416
13 | 3 | Base unit dimensions — 50TJ024,028 | 6 | 4 | 189
13 | 3 | Base unit dimensions — 50TJ024,028 | 6 | 5 | 553
13 | 3 | Base unit dimensions — 50TJ024,028 | 6 | 6 | 251
13 | 3 | Base unit dimensions — 50TJ024,028 | 6 | 7 | 580
13 | 3 | Base unit dimensions — 50TJ024,028 | 6 | 8 | 263
13 | 3 | Base unit dimensions — 50TJ024,028 | 6 | 9 | 3-1
13 | 3 | Base unit dimensions — 50TJ024,028 | 6 | 10 | 940
13 | 3 | Base unit dimensions — 50TJ024,028 | 6 | 11 | 3-6
14 | 1 | Accessory dimensions | 1 | 1 | NOTES: 1. Roof curb accessory is shipped unassembled. 2. Insulated panels, 1″ thick neoprene coated, 11/ lb density.
14 | 1 | Accessory dimensions | 2 | 2 | OTES: 1. Roof curb accessory is shipped unassembled. 2. Insulated panels, 1″ thick neoprene coated, 11/ lb density.
14 | 2 | Accessory dimensions | 1 | 1 | CURB HEIGHT
14 | 2 | Accessory dimensions | 2 | 1 | 1′-2″ (305)
14 | 2 | Accessory dimensions | 3 | 1 | 2′-0″ (610)
14 | 2 | Accessory dimensions | 4 | 1 | 2′-0″ (610)
14 | 3 | Accessory dimensions | 1 | 1 | A
14 | 3 | Accessory dimensions | 2 | 1 | DEG.
14 | 3 | Accessory dimensions | 2 | 2 | IN.
14 | 3 | Accessory dimensions | 2 | 3 | DEG.
14 | 3 | Accessory dimensions | 3 | 1 | .28
14 | 3 | Accessory dimensions | 3 | 2 | .45
14 | 3 | Accessory dimensions | 3 | 3 | .28
15 | 1 | HORIZONTAL SUPPLY/RETURN ADAPTER INSTALLATION | 1 | 1 | HORIZONTAL SUPPLY/RETURN ADAPTER INSTALLATION NOTE: CRRFCURB013A00 is a fully factory preassembled horizontal adapter and includes an insulated high static regain transition duct which substantially improves fan static performance. The Barometric Relief Damper and Power Exhaust accessories are not available with the horizontal adapter. ACCESSORY CURB DESCRIPTION PACKAGE NO. HEIGHT 1′-11″ Pre-Assembled, High Static, CRRFCURB013A00 (584) Horizontal Adapter
15 | 1 | HORIZONTAL SUPPLY/RETURN ADAPTER INSTALLATION | 3 | 1 | BAROMETRIC RELIEF/POWER EXHAUST 2'-1 5/8" (650.9) 2'-2 1/16" (662) 1'-6 5/16" (465.1)
15 | 2 | HORIZONTAL SUPPLY/RETURN ADAPTER INSTALLATION | 1 | 1 | CURB HEIGHT
15 | 2 | HORIZONTAL SUPPLY/RETURN ADAPTER INSTALLATION | 2 | 1 | 1′-11″ (584)
16 | 1 | Accessory dimensions (cont) | 1 | 1 | FACTORY-INSTALLED NON-FUSED DISCONNECT COMPRESSOR TOP CONTROL BOX DISCONNECT SECTION DOOR SECTION DOOR HANDLE 2'-5 1/4" (743) FRONT VIEW 1'-1 11/16" (347)
19 | 1 | Performance data | 1 | 1 | 2124/0.12
19 | 1 | Performance data | 1 | 2 | 2478/0.14
19 | 1 | Performance data | 1 | 3 | 2832/0.15
19 | 1 | Performance data | 1 | 4 | 3186/0.17
19 | 2 | Performance data | 1 | 2 | 17
19 | 2 | Performance data | 1 | 3 | 19
19 | 2 | Performance data | 1 | 4 | 22
19 | 2 | Performance data | 1 | 5 | 17
19 | 2 | Performance data | 1 | 6 | 19
19 | 2 | Performance data | 1 | 7 | 22
19 | 2 | Performance data | 1 | 8 | 17
19 | 2 | Performance data | 1 | 9 | 19
19 | 2 | Performance data | 1 | 10 | 22
19 | 2 | Performance data | 1 | 11 | 17
19 | 2 | Performance data | 1 | 12 | 19
19 | 2 | Performance data | 1 | 13 | 22
19 | 2 | Performance data | 1 | 14 | 17
19 | 2 | Performance data | 1 | 15 | 19
19 | 2 | Performance data | 2 | 1 | TC SHC kW
19 | 2 | Performance data | 2 | 2 | 49.0 41.6 11.3
19 | 2 | Performance data | 2 | 3 | 53.3 35.5 11.7
19 | 2 | Performance data | 2 | 4 | 58.7 28.8 13.3
19 | 2 | Performance data | 2 | 5 | 50.3 45.1 11.5
19 | 2 | Performance data | 2 | 6 | 54.9 37.8 11.9
19 | 2 | Performance data | 2 | 7 | 60.3 30.6 13.4
19 | 2 | Performance data | 2 | 8 | 51.8 47.5 11.6
19 | 2 | Performance data | 2 | 9 | 56.5 40.1 12.0
19 | 2 | Performance data | 2 | 10 | 61.3 32.0 13.5
19 | 2 | Performance data | 2 | 11 | 52.8 50.2 11.7
19 | 2 | Performance data | 2 | 12 | 57.1 43.1 12.0
19 | 2 | Performance data | 2 | 13 | 61.9 34.7 13.6
19 | 2 | Performance data | 2 | 14 | 53.9 52.7 11.7
19 | 2 | Performance data | 2 | 15 | 57.6 45.2 12.1
19 | 2 | Performance data | 3 | 1 | TC SHC kW
19 | 2 | Performance data | 3 | 2 | 47.6 40.8 12.7
19 | 2 | Performance data | 3 | 3 | 51.7 34.7 13.0
19 | 2 | Performance data | 3 | 4 | 56.5 28.2 14.7
19 | 2 | Performance data | 3 | 5 | 49.0 44.0 12.8
19 | 2 | Performance data | 3 | 6 | 53.3 37.1 13.2
19 | 2 | Performance data | 3 | 7 | 58.1 29.7 14.9
19 | 2 | Performance data | 3 | 8 | 50.2 46.7 12.9
19 | 2 | Performance data | 3 | 9 | 54.4 39.3 13.3
19 | 2 | Performance data | 3 | 10 | 59.7 31.2 15.0
19 | 2 | Performance data | 3 | 11 | 51.2 49.4 13.0
19 | 2 | Performance data | 3 | 12 | 55.5 41.4 13.4
19 | 2 | Performance data | 3 | 13 | 60.3 33.1 15.1
19 | 2 | Performance data | 3 | 14 | 52.1 51.7 13.1
19 | 2 | Performance data | 3 | 15 | 56.0 44.2 13.5
19 | 2 | Performance data | 4 | 1 | TC SHC kW
19 | 2 | Performance data | 4 | 2 | 46.0 40.0 14.1
19 | 2 | Performance data | 4 | 3 | 50.1 33.8 14.5
19 | 2 | Performance data | 4 | 4 | 54.9 27.4 16.3
19 | 2 | Performance data | 4 | 5 | 47.4 43.1 14.3
19 | 2 | Performance data | 4 | 6 | 51.5 36.2 14.6
19 | 2 | Performance data | 4 | 7 | 56.5 28.9 16.5
19 | 2 | Performance data | 4 | 8 | 48.5 45.9 14.4
19 | 2 | Performance data | 4 | 9 | 52.6 38.5 14.7
19 | 2 | Performance data | 4 | 10 | 57.6 30.3 16.6
19 | 2 | Performance data | 4 | 11 | 49.4 48.5 14.5
19 | 2 | Performance data | 4 | 12 | 53.3 40.6 14.9
19 | 2 | Performance data | 4 | 13 | 58.7 31.5 16.7
19 | 2 | Performance data | 4 | 14 | 50.4 50.4 14.6
19 | 2 | Performance data | 4 | 15 | 54.4 42.8 15.0
19 | 2 | Performance data | 5 | 1 | TC SHC kW
19 | 2 | Performance data | 5 | 2 | 43.5 38.2 15.7
19 | 2 | Performance data | 5 | 3 | 47.3 32.4 16.2
19 | 2 | Performance data | 5 | 4 | 51.8 26.2 18.1
19 | 2 | Performance data | 5 | 5 | 44.7 41.2 15.9
19 | 2 | Performance data | 5 | 6 | 48.5 34.7 16.3
19 | 2 | Performance data | 5 | 7 | 52.9 27.6 18.3
19 | 2 | Performance data | 5 | 8 | 45.7 44.0 16.0
19 | 2 | Performance data | 5 | 9 | 49.5 36.8 16.4
19 | 2 | Performance data | 5 | 10 | 53.9 28.9 18.4
19 | 2 | Performance data | 5 | 11 | 46.6 46.4 16.1
19 | 2 | Performance data | 5 | 12 | 50.3 38.9 16.5
19 | 2 | Performance data | 5 | 13 | 55.0 30.0 18.5
19 | 2 | Performance data | 5 | 14 | 47.7 47.9 16.2
19 | 2 | Performance data | 5 | 15 | 51.0 41.0 16.6
19 | 2 | Performance data | 6 | 1 | TC SHC kW
19 | 2 | Performance data | 6 | 2 | 40.8 36.5 17.4
19 | 2 | Performance data | 6 | 3 | 44.4 31.0 17.9
19 | 2 | Performance data | 6 | 4 | 48.7 24.9 18.4
19 | 2 | Performance data | 6 | 5 | 41.9 39.5 17.6
19 | 2 | Performance data | 6 | 6 | 45.5 33.2 18.0
19 | 2 | Performance data | 6 | 7 | 49.9 26.3 18.6
19 | 2 | Performance data | 6 | 8 | 42.7 42.2 17.7
19 | 2 | Performance data | 6 | 9 | 46.4 35.3 18.1
19 | 2 | Performance data | 6 | 10 | 50.5 27.6 18.7
19 | 2 | Performance data | 6 | 11 | 43.9 44.1 17.9
19 | 2 | Performance data | 6 | 12 | 47.1 37.2 18.3
19 | 2 | Performance data | 6 | 13 | 51.0 28.7 18.7
19 | 2 | Performance data | 6 | 14 | 44.9 45.2 18.0
19 | 2 | Performance data | 6 | 15 | 47.6 39.2 18.3
19 | 2 | Performance data | 7 | 1 | TC SHC kW
19 | 2 | Performance data | 7 | 2 | 39.0 35.4 18.4
19 | 2 | Performance data | 7 | 3 | 42.4 30.0 18.9
19 | 2 | Performance data | 7 | 4 | 46.6 24.0 19.4
19 | 2 | Performance data | 7 | 5 | 40.0 38.3 18.5
19 | 2 | Performance data | 7 | 6 | 43.5 32.1 19.0
19 | 2 | Performance data | 7 | 7 | 47.7 25.3 19.6
19 | 2 | Performance data | 7 | 8 | 40.9 40.7 18.7
19 | 2 | Performance data | 7 | 9 | 44.3 34.3 19.1
19 | 2 | Performance data | 7 | 10 | 48.4 26.7 19.8
19 | 2 | Performance data | 7 | 11 | 42.0 42.3 18.8
19 | 2 | Performance data | 7 | 12 | 45.0 36.3 19.2
19 | 2 | Performance data | 7 | 13 | 48.8 27.8 19.8
19 | 2 | Performance data | 7 | 14 | 43.0 43.4 18.9
19 | 2 | Performance data | 7 | 15 | 45.5 37.9 19.3
19 | 2 | Performance data | 8 | 1 | TC SHC kW
19 | 2 | Performance data | 8 | 2 | 37.2 34.2 19.3
19 | 2 | Performance data | 8 | 3 | 40.5 29.0 19.7
19 | 2 | Performance data | 8 | 4 | 44.2 23.8 20.3
19 | 2 | Performance data | 8 | 5 | 38.1 36.9 19.4
19 | 2 | Performance data | 8 | 6 | 41.4 31.1 19.9
19 | 2 | Performance data | 8 | 7 | — — —
19 | 2 | Performance data | 8 | 8 | 39.1 39.2 19.6
19 | 2 | Performance data | 8 | 9 | 42.2 33.1 20.1
19 | 2 | Performance data | 8 | 10 | — — —
19 | 2 | Performance data | 8 | 11 | 40.2 40.5 19.7
19 | 2 | Performance data | 8 | 12 | 42.9 35.0 20.1
19 | 2 | Performance data | 8 | 13 | — — —
19 | 2 | Performance data | 8 | 14 | 41.2 41.5 19.9
19 | 2 | Performance data | 8 | 15 | 43.3 36.6 20.1
19 | 3 | Performance data | 1 | 1 | 2832/0.075
19 | 3 | Performance data | 1 | 2 | 3304/0.085
19 | 3 | Performance data | 1 | 3 | 3776/0.100
19 | 3 | Performance data | 1 | 4 | 4248/0.110
19 | 4 | Performance data | 1 | 2 | 17
19 | 4 | Performance data | 1 | 3 | 19
19 | 4 | Performance data | 1 | 4 | 22
19 | 4 | Performance data | 1 | 5 | 17
19 | 4 | Performance data | 1 | 6 | 19
19 | 4 | Performance data | 1 | 7 | 22
19 | 4 | Performance data | 1 | 8 | 17
19 | 4 | Performance data | 1 | 9 | 19
19 | 4 | Performance data | 1 | 10 | 22
19 | 4 | Performance data | 1 | 11 | 17
19 | 4 | Performance data | 1 | 12 | 19
19 | 4 | Performance data | 1 | 13 | 22
19 | 4 | Performance data | 1 | 14 | 17
19 | 4 | Performance data | 1 | 15 | 19
19 | 4 | Performance data | 2 | 1 | TC SHC kW
19 | 4 | Performance data | 2 | 2 | 64.3 55.1 15.1
19 | 4 | Performance data | 2 | 3 | 70.9 46.5 15.6
19 | 4 | Performance data | 2 | 4 | 76.9 36.9 16.5
19 | 4 | Performance data | 2 | 5 | 65.9 59.5 15.2
19 | 4 | Performance data | 2 | 6 | 72.7 49.7 15.8
19 | 4 | Performance data | 2 | 7 | 78.8 38.9 16.7
19 | 4 | Performance data | 2 | 8 | 67.2 63.6 15.4
19 | 4 | Performance data | 2 | 9 | 74.1 53.0 15.9
19 | 4 | Performance data | 2 | 10 | 80.3 40.8 16.9
19 | 4 | Performance data | 2 | 11 | 68.4 67.2 15.5
19 | 4 | Performance data | 2 | 12 | 75.0 56.0 16.0
19 | 4 | Performance data | 2 | 13 | 81.3 42.8 17.0
19 | 4 | Performance data | 2 | 14 | 69.7 69.6 15.7
19 | 4 | Performance data | 2 | 15 | 75.8 59.1 16.1
19 | 4 | Performance data | 3 | 1 | TC SHC kW
19 | 4 | Performance data | 3 | 2 | 62.1 54.0 16.7
19 | 4 | Performance data | 3 | 3 | 68.5 45.4 17.2
19 | 4 | Performance data | 3 | 4 | 74.3 36.0 18.2
19 | 4 | Performance data | 3 | 5 | 63.6 58.4 16.9
19 | 4 | Performance data | 3 | 6 | 70.2 48.8 17.4
19 | 4 | Performance data | 3 | 7 | 76.1 38.0 18.5
19 | 4 | Performance data | 3 | 8 | 64.9 62.4 17.0
19 | 4 | Performance data | 3 | 9 | 71.4 51.9 17.6
19 | 4 | Performance data | 3 | 10 | 77.5 39.9 18.6
19 | 4 | Performance data | 3 | 11 | 66.0 65.6 17.2
19 | 4 | Performance data | 3 | 12 | 72.3 54.8 17.7
19 | 4 | Performance data | 3 | 13 | 78.5 41.7 18.7
19 | 4 | Performance data | 3 | 14 | 67.8 67.6 17.4
19 | 4 | Performance data | 3 | 15 | 73.1 57.9 17.8
19 | 4 | Performance data | 4 | 1 | TC SHC kW
19 | 4 | Performance data | 4 | 2 | 59.8 53.0 18.5
19 | 4 | Performance data | 4 | 3 | 65.9 44.4 19.0
19 | 4 | Performance data | 4 | 4 | 71.6 35.0 20.1
19 | 4 | Performance data | 4 | 5 | 61.2 57.1 18.7
19 | 4 | Performance data | 4 | 6 | 67.4 47.7 19.2
19 | 4 | Performance data | 4 | 7 | 73.2 37.0 20.3
19 | 4 | Performance data | 4 | 8 | 62.4 61.0 18.8
19 | 4 | Performance data | 4 | 9 | 68.6 50.7 19.3
19 | 4 | Performance data | 4 | 10 | 74.4 38.9 20.4
19 | 4 | Performance data | 4 | 11 | 63.8 63.7 19.0
19 | 4 | Performance data | 4 | 12 | 69.4 53.6 19.4
19 | 4 | Performance data | 4 | 13 | 75.3 40.6 20.5
19 | 4 | Performance data | 4 | 14 | 65.3 65.1 19.1
19 | 4 | Performance data | 4 | 15 | 70.0 56.7 19.5
19 | 4 | Performance data | 5 | 1 | TC SHC kW
19 | 4 | Performance data | 5 | 2 | 57.0 51.6 20.3
19 | 4 | Performance data | 5 | 3 | 63.0 43.3 20.8
19 | 4 | Performance data | 5 | 4 | 68.5 33.9 22.0
19 | 4 | Performance data | 5 | 5 | 58.4 55.8 20.5
19 | 4 | Performance data | 5 | 6 | 64.4 46.5 21.0
19 | 4 | Performance data | 5 | 7 | 70.0 35.9 22.2
19 | 4 | Performance data | 5 | 8 | 59.7 59.3 20.6
19 | 4 | Performance data | 5 | 9 | 65.3 49.4 21.1
19 | 4 | Performance data | 5 | 10 | 71.1 37.7 22.3
19 | 4 | Performance data | 5 | 11 | 61.4 61.3 20.8
19 | 4 | Performance data | 5 | 12 | 66.1 52.6 21.2
19 | 4 | Performance data | 5 | 13 | 71.9 39.5 22.4
19 | 4 | Performance data | 5 | 14 | 62.8 62.6 21.0
19 | 4 | Performance data | 5 | 15 | 66.7 55.4 21.3
19 | 4 | Performance data | 6 | 1 | TC SHC kW
19 | 4 | Performance data | 6 | 2 | 54.2 50.2 22.1
19 | 4 | Performance data | 6 | 3 | 59.9 42.0 22.7
19 | 4 | Performance data | 6 | 4 | 65.2 32.8 23.9
19 | 4 | Performance data | 6 | 5 | 55.6 54.3 22.3
19 | 4 | Performance data | 6 | 6 | 61.2 45.3 22.8
19 | 4 | Performance data | 6 | 7 | 66.6 34.7 24.1
19 | 4 | Performance data | 6 | 8 | 57.1 56.9 22.5
19 | 4 | Performance data | 6 | 9 | 62.1 48.3 23.0
19 | 4 | Performance data | 6 | 10 | 67.6 36.5 24.2
19 | 4 | Performance data | 6 | 11 | 58.7 58.6 22.7
19 | 4 | Performance data | 6 | 12 | 62.7 51.1 23.1
19 | 4 | Performance data | 6 | 13 | 68.3 38.3 24.3
19 | 4 | Performance data | 6 | 14 | 60.0 59.8 22.9
19 | 4 | Performance data | 6 | 15 | 63.2 53.7 23.2
19 | 4 | Performance data | 7 | 1 | TC SHC kW
19 | 4 | Performance data | 7 | 2 | 51.2 48.7 24.0
19 | 4 | Performance data | 7 | 3 | 56.6 40.7 24.6
19 | 4 | Performance data | 7 | 4 | — — —
19 | 4 | Performance data | 7 | 5 | 52.7 52.3 24.2
19 | 4 | Performance data | 7 | 6 | 57.6 43.8 24.7
19 | 4 | Performance data | 7 | 7 | — — —
19 | 4 | Performance data | 7 | 8 | 54.3 54.2 24.4
19 | 4 | Performance data | 7 | 9 | 58.4 47.0 24.9
19 | 4 | Performance data | 7 | 10 | — — —
19 | 4 | Performance data | 7 | 11 | 55.9 55.7 24.6
19 | 4 | Performance data | 7 | 12 | 59.0 49.6 25.0
19 | 4 | Performance data | 7 | 13 | — — —
19 | 4 | Performance data | 7 | 14 | 57.0 56.9 24.8
19 | 4 | Performance data | 7 | 15 | 59.4 52.1 25.0
20 | 1 | Performance data (cont) | 1 | 1 | 3304/0.05
20 | 1 | Performance data (cont) | 1 | 2 | 3776/0.06
20 | 1 | Performance data (cont) | 1 | 3 | 4248/0.07
20 | 1 | Performance data (cont) | 1 | 4 | 4720/0.08
20 | 2 | Performance data (cont) | 1 | 2 | 17
20 | 2 | Performance data (cont) | 1 | 3 | 19
20 | 2 | Performance data (cont) | 1 | 4 | 22
20 | 2 | Performance data (cont) | 1 | 5 | 17
20 | 2 | Performance data (cont) | 1 | 6 | 19
20 | 2 | Performance data (cont) | 1 | 7 | 22
20 | 2 | Performance data (cont) | 1 | 8 | 17
20 | 2 | Performance data (cont) | 1 | 9 | 19
20 | 2 | Performance data (cont) | 1 | 10 | 22
20 | 2 | Performance data (cont) | 1 | 11 | 17
20 | 2 | Performance data (cont) | 1 | 12 | 19
20 | 2 | Performance data (cont) | 1 | 13 | 22
20 | 2 | Performance data (cont) | 1 | 14 | 17
20 | 2 | Performance data (cont) | 1 | 15 | 19
20 | 2 | Performance data (cont) | 2 | 1 | TC SHC kW
20 | 2 | Performance data (cont) | 2 | 2 | 79.4 67.7 20.1
20 | 2 | Performance data (cont) | 2 | 3 | 87.6 57.2 20.8
20 | 2 | Performance data (cont) | 2 | 4 | 96.5 46.5 21.6
20 | 2 | Performance data (cont) | 2 | 5 | 81.2 72.6 20.3
20 | 2 | Performance data (cont) | 2 | 6 | 89.6 60.7 21.0
20 | 2 | Performance data (cont) | 2 | 7 | 98.6 48.4 21.8
20 | 2 | Performance data (cont) | 2 | 8 | 82.7 77.5 20.4
20 | 2 | Performance data (cont) | 2 | 9 | 91.0 64.4 21.2
20 | 2 | Performance data (cont) | 2 | 10 | 100.3 51.2 22.0
20 | 2 | Performance data (cont) | 2 | 11 | 83.9 81.7 20.6
20 | 2 | Performance data (cont) | 2 | 12 | 91.9 68.7 21.3
20 | 2 | Performance data (cont) | 2 | 13 | 101.6 53.3 22.2
20 | 2 | Performance data (cont) | 2 | 14 | 85.7 85.6 20.8
20 | 2 | Performance data (cont) | 2 | 15 | 93.4 72.6 21.5
20 | 2 | Performance data (cont) | 3 | 1 | TC SHC kW
20 | 2 | Performance data (cont) | 3 | 2 | 76.6 66.5 22.2
20 | 2 | Performance data (cont) | 3 | 3 | 84.5 55.9 23.0
20 | 2 | Performance data (cont) | 3 | 4 | 93.1 45.0 23.8
20 | 2 | Performance data (cont) | 3 | 5 | 78.3 71.2 22.4
20 | 2 | Performance data (cont) | 3 | 6 | 86.4 59.4 23.2
20 | 2 | Performance data (cont) | 3 | 7 | 95.0 47.4 24.0
20 | 2 | Performance data (cont) | 3 | 8 | 79.8 75.6 22.6
20 | 2 | Performance data (cont) | 3 | 9 | 88.0 62.9 23.4
20 | 2 | Performance data (cont) | 3 | 10 | 96.6 49.4 24.2
20 | 2 | Performance data (cont) | 3 | 11 | 81.0 79.7 22.8
20 | 2 | Performance data (cont) | 3 | 12 | 89.1 66.4 23.5
20 | 2 | Performance data (cont) | 3 | 13 | 98.1 51.6 24.4
20 | 2 | Performance data (cont) | 3 | 14 | 83.1 83.0 23.0
20 | 2 | Performance data (cont) | 3 | 15 | 90.4 70.5 23.7
20 | 2 | Performance data (cont) | 4 | 1 | TC SHC kW
20 | 2 | Performance data (cont) | 4 | 2 | 73.7 65.0 24.6
20 | 2 | Performance data (cont) | 4 | 3 | 81.2 54.6 25.3
20 | 2 | Performance data (cont) | 4 | 4 | 89.4 44.0 26.1
20 | 2 | Performance data (cont) | 4 | 5 | 75.2 69.7 24.7
20 | 2 | Performance data (cont) | 4 | 6 | 83.0 58.1 25.5
20 | 2 | Performance data (cont) | 4 | 7 | 91.1 46.0 26.3
20 | 2 | Performance data (cont) | 4 | 8 | 76.7 74.1 24.9
20 | 2 | Performance data (cont) | 4 | 9 | 84.2 61.8 25.7
20 | 2 | Performance data (cont) | 4 | 10 | 92.7 48.1 26.5
20 | 2 | Performance data (cont) | 4 | 11 | 78.1 77.7 25.1
20 | 2 | Performance data (cont) | 4 | 12 | 85.5 64.8 25.8
20 | 2 | Performance data (cont) | 4 | 13 | 94.0 50.1 26.7
20 | 2 | Performance data (cont) | 4 | 14 | 80.3 80.2 25.4
20 | 2 | Performance data (cont) | 4 | 15 | 86.6 68.9 26.0
20 | 2 | Performance data (cont) | 5 | 1 | TC SHC kW
20 | 2 | Performance data (cont) | 5 | 2 | 70.5 63.3 27.0
20 | 2 | Performance data (cont) | 5 | 3 | 77.8 53.3 27.8
20 | 2 | Performance data (cont) | 5 | 4 | 85.4 42.6 28.6
20 | 2 | Performance data (cont) | 5 | 5 | 71.9 68.0 27.2
20 | 2 | Performance data (cont) | 5 | 6 | 79.2 56.5 28.0
20 | 2 | Performance data (cont) | 5 | 7 | 87.2 44.7 28.8
20 | 2 | Performance data (cont) | 5 | 8 | 73.5 72.0 27.4
20 | 2 | Performance data (cont) | 5 | 9 | 80.4 60.1 28.1
20 | 2 | Performance data (cont) | 5 | 10 | 88.6 46.6 29.0
20 | 2 | Performance data (cont) | 5 | 11 | 75.0 75.0 27.6
20 | 2 | Performance data (cont) | 5 | 12 | 81.4 63.3 28.3
20 | 2 | Performance data (cont) | 5 | 13 | 89.6 48.8 29.2
20 | 2 | Performance data (cont) | 5 | 14 | 77.2 77.1 27.9
20 | 2 | Performance data (cont) | 5 | 15 | 82.5 67.2 28.4
20 | 2 | Performance data (cont) | 6 | 1 | TC SHC kW
20 | 2 | Performance data (cont) | 6 | 2 | 67.1 61.9 29.5
20 | 2 | Performance data (cont) | 6 | 3 | 74.0 51.8 30.3
20 | 2 | Performance data (cont) | 6 | 4 | 81.2 41.0 31.1
20 | 2 | Performance data (cont) | 6 | 5 | 68.4 66.2 29.7
20 | 2 | Performance data (cont) | 6 | 6 | 75.3 55.0 30.5
20 | 2 | Performance data (cont) | 6 | 7 | 82.5 43.1 31.3
20 | 2 | Performance data (cont) | 6 | 8 | 70.0 69.8 30.0
20 | 2 | Performance data (cont) | 6 | 9 | 76.4 58.4 30.7
20 | 2 | Performance data (cont) | 6 | 10 | 83.6 44.9 31.5
20 | 2 | Performance data (cont) | 6 | 11 | 71.9 71.8 30.2
20 | 2 | Performance data (cont) | 6 | 12 | 77.3 61.7 30.8
20 | 2 | Performance data (cont) | 6 | 13 | — — —
20 | 2 | Performance data (cont) | 6 | 14 | 73.8 73.8 30.5
20 | 2 | Performance data (cont) | 6 | 15 | 78.2 65.4 31.0
20 | 2 | Performance data (cont) | 7 | 1 | TC SHC kW
20 | 2 | Performance data (cont) | 7 | 2 | 66.1 61.4 30.3
20 | 2 | Performance data (cont) | 7 | 3 | 72.7 51.3 31.1
20 | 2 | Performance data (cont) | 7 | 4 | — — —
20 | 2 | Performance data (cont) | 7 | 5 | 67.4 65.6 30.5
20 | 2 | Performance data (cont) | 7 | 6 | 73.9 54.5 31.2
20 | 2 | Performance data (cont) | 7 | 7 | — — —
20 | 2 | Performance data (cont) | 7 | 8 | 68.9 68.8 30.7
20 | 2 | Performance data (cont) | 7 | 9 | 74.8 57.8 31.4
20 | 2 | Performance data (cont) | 7 | 10 | — — —
20 | 2 | Performance data (cont) | 7 | 11 | 70.6 70.5 31.0
20 | 2 | Performance data (cont) | 7 | 12 | 75.5 61.1 31.5
20 | 2 | Performance data (cont) | 7 | 13 | — — —
20 | 2 | Performance data (cont) | 7 | 14 | 72.4 72.4 31.2
20 | 2 | Performance data (cont) | 7 | 15 | — — —
20 | 2 | Performance data (cont) | 8 | 1 | TC SHC kW
20 | 2 | Performance data (cont) | 8 | 2 | 65.2 60.9 30.8
20 | 2 | Performance data (cont) | 8 | 3 | — — —
20 | 2 | Performance data (cont) | 8 | 4 | — — —
20 | 2 | Performance data (cont) | 8 | 5 | 66.6 65.2 31.0
20 | 2 | Performance data (cont) | 8 | 6 | — — —
20 | 2 | Performance data (cont) | 8 | 7 | — — —
20 | 2 | Performance data (cont) | 8 | 8 | 68.4 68.4 31.3
20 | 2 | Performance data (cont) | 8 | 9 | — — —
20 | 2 | Performance data (cont) | 8 | 10 | — — —
20 | 2 | Performance data (cont) | 8 | 11 | 70.0 70.0 31.5
20 | 2 | Performance data (cont) | 8 | 12 | — — —
20 | 2 | Performance data (cont) | 8 | 13 | — — —
20 | 2 | Performance data (cont) | 8 | 14 | — — —
20 | 2 | Performance data (cont) | 8 | 15 | — — —
20 | 3 | Performance data (cont) | 1 | 1 | 3304/0.05
20 | 3 | Performance data (cont) | 1 | 2 | 3776/0.06
20 | 3 | Performance data (cont) | 1 | 3 | 4248/0.07
20 | 3 | Performance data (cont) | 1 | 4 | 4720/0.08
20 | 4 | Performance data (cont) | 1 | 2 | 17
20 | 4 | Performance data (cont) | 1 | 3 | 19
20 | 4 | Performance data (cont) | 1 | 4 | 22
20 | 4 | Performance data (cont) | 1 | 5 | 17
20 | 4 | Performance data (cont) | 1 | 6 | 19
20 | 4 | Performance data (cont) | 1 | 7 | 22
20 | 4 | Performance data (cont) | 1 | 8 | 17
20 | 4 | Performance data (cont) | 1 | 9 | 19
20 | 4 | Performance data (cont) | 1 | 10 | 22
20 | 4 | Performance data (cont) | 1 | 11 | 17
20 | 4 | Performance data (cont) | 1 | 12 | 19
20 | 4 | Performance data (cont) | 1 | 13 | 22
20 | 4 | Performance data (cont) | 1 | 14 | 17
20 | 4 | Performance data (cont) | 1 | 15 | 19
20 | 4 | Performance data (cont) | 2 | 1 | TC SHC kW
20 | 4 | Performance data (cont) | 2 | 2 | 82.3 69.1 18.2
20 | 4 | Performance data (cont) | 2 | 3 | 90.8 58.8 18.8
20 | 4 | Performance data (cont) | 2 | 4 | 100.5 47.8 19.4
20 | 4 | Performance data (cont) | 2 | 5 | 84.4 74.1 18.4
20 | 4 | Performance data (cont) | 2 | 6 | 93.2 62.6 19.0
20 | 4 | Performance data (cont) | 2 | 7 | 102.8 50.3 19.6
20 | 4 | Performance data (cont) | 2 | 8 | 85.6 79.7 18.5
20 | 4 | Performance data (cont) | 2 | 9 | 94.6 66.9 19.1
20 | 4 | Performance data (cont) | 2 | 10 | 104.0 54.3 19.7
20 | 4 | Performance data (cont) | 2 | 11 | 87.3 83.2 18.6
20 | 4 | Performance data (cont) | 2 | 12 | 95.8 70.2 19.2
20 | 4 | Performance data (cont) | 2 | 13 | 105.8 56.6 19.9
20 | 4 | Performance data (cont) | 2 | 14 | 89.1 87.9 18.8
20 | 4 | Performance data (cont) | 2 | 15 | 97.3 75.3 19.4
20 | 4 | Performance data (cont) | 3 | 1 | TC SHC kW
20 | 4 | Performance data (cont) | 3 | 2 | 79.7 68.0 20.3
20 | 4 | Performance data (cont) | 3 | 3 | 87.9 57.4 20.8
20 | 4 | Performance data (cont) | 3 | 4 | 97.3 46.6 21.5
20 | 4 | Performance data (cont) | 3 | 5 | 81.7 73.0 20.4
20 | 4 | Performance data (cont) | 3 | 6 | 90.5 61.1 21.0
20 | 4 | Performance data (cont) | 3 | 7 | 99.6 49.1 21.7
20 | 4 | Performance data (cont) | 3 | 8 | 83.2 77.6 20.6
20 | 4 | Performance data (cont) | 3 | 9 | 92.0 65.0 21.2
20 | 4 | Performance data (cont) | 3 | 10 | 101.7 51.4 21.8
20 | 4 | Performance data (cont) | 3 | 11 | 84.7 81.7 20.8
20 | 4 | Performance data (cont) | 3 | 12 | 93.2 68.0 21.4
20 | 4 | Performance data (cont) | 3 | 13 | 102.8 53.7 22.0
20 | 4 | Performance data (cont) | 3 | 14 | 86.7 85.8 20.9
20 | 4 | Performance data (cont) | 3 | 15 | 94.3 73.2 21.4
20 | 4 | Performance data (cont) | 4 | 1 | TC SHC kW
20 | 4 | Performance data (cont) | 4 | 2 | 76.8 66.5 22.6
20 | 4 | Performance data (cont) | 4 | 3 | 85.3 56.2 23.1
20 | 4 | Performance data (cont) | 4 | 4 | 93.8 45.6 23.7
20 | 4 | Performance data (cont) | 4 | 5 | 78.5 71.5 22.6
20 | 4 | Performance data (cont) | 4 | 6 | 87.0 59.7 23.3
20 | 4 | Performance data (cont) | 4 | 7 | 95.8 47.8 23.9
20 | 4 | Performance data (cont) | 4 | 8 | 80.3 75.6 22.8
20 | 4 | Performance data (cont) | 4 | 9 | 88.5 63.1 23.4
20 | 4 | Performance data (cont) | 4 | 10 | 97.6 49.9 24.1
20 | 4 | Performance data (cont) | 4 | 11 | 81.7 79.4 23.0
20 | 4 | Performance data (cont) | 4 | 12 | 90.0 66.6 23.6
20 | 4 | Performance data (cont) | 4 | 13 | 99.0 52.0 24.2
20 | 4 | Performance data (cont) | 4 | 14 | 83.5 82.9 23.1
20 | 4 | Performance data (cont) | 4 | 15 | 91.1 70.6 23.6
20 | 4 | Performance data (cont) | 5 | 1 | TC SHC kW
20 | 4 | Performance data (cont) | 5 | 2 | 73.8 65.1 24.9
20 | 4 | Performance data (cont) | 5 | 3 | 81.7 54.7 25.5
20 | 4 | Performance data (cont) | 5 | 4 | 90.0 44.2 26.1
20 | 4 | Performance data (cont) | 5 | 5 | 75.6 69.6 25.0
20 | 4 | Performance data (cont) | 5 | 6 | 83.5 58.5 25.7
20 | 4 | Performance data (cont) | 5 | 7 | 91.7 46.4 26.3
20 | 4 | Performance data (cont) | 5 | 8 | 77.1 74.1 25.2
20 | 4 | Performance data (cont) | 5 | 9 | 85.0 61.6 25.8
20 | 4 | Performance data (cont) | 5 | 10 | 93.5 48.4 26.5
20 | 4 | Performance data (cont) | 5 | 11 | 78.5 77.4 25.3
20 | 4 | Performance data (cont) | 5 | 12 | 86.1 65.0 25.9
20 | 4 | Performance data (cont) | 5 | 13 | 94.6 50.5 26.5
20 | 4 | Performance data (cont) | 5 | 14 | 80.9 80.6 25.5
20 | 4 | Performance data (cont) | 5 | 15 | 87.0 69.4 26.0
20 | 4 | Performance data (cont) | 6 | 1 | TC SHC kW
20 | 4 | Performance data (cont) | 6 | 2 | 70.3 63.5 27.3
20 | 4 | Performance data (cont) | 6 | 3 | 77.9 53.3 27.9
20 | 4 | Performance data (cont) | 6 | 4 | 85.6 42.7 28.5
20 | 4 | Performance data (cont) | 6 | 5 | 72.1 68.0 27.5
20 | 4 | Performance data (cont) | 6 | 6 | 79.7 57.0 28.1
20 | 4 | Performance data (cont) | 6 | 7 | 87.6 44.8 28.7
20 | 4 | Performance data (cont) | 6 | 8 | 73.8 71.8 27.7
20 | 4 | Performance data (cont) | 6 | 9 | 80.9 60.4 28.3
20 | 4 | Performance data (cont) | 6 | 10 | 88.8 47.0 28.9
20 | 4 | Performance data (cont) | 6 | 11 | 75.6 75.0 27.8
20 | 4 | Performance data (cont) | 6 | 12 | 81.7 63.5 28.3
20 | 4 | Performance data (cont) | 6 | 13 | 90.2 49.5 28.9
20 | 4 | Performance data (cont) | 6 | 14 | 77.6 77.4 28.0
20 | 4 | Performance data (cont) | 6 | 15 | 82.9 67.8 28.5
20 | 4 | Performance data (cont) | 7 | 1 | TC SHC kW
20 | 4 | Performance data (cont) | 7 | 2 | 67.0 61.8 29.9
20 | 4 | Performance data (cont) | 7 | 3 | 73.8 51.9 30.4
20 | 4 | Performance data (cont) | 7 | 4 | 81.5 41.2 31.1
20 | 4 | Performance data (cont) | 7 | 5 | 68.6 66.1 30.0
20 | 4 | Performance data (cont) | 7 | 6 | 75.6 55.4 30.6
20 | 4 | Performance data (cont) | 7 | 7 | 82.9 43.2 31.2
20 | 4 | Performance data (cont) | 7 | 8 | 70.3 69.1 30.2
20 | 4 | Performance data (cont) | 7 | 9 | 76.5 58.5 30.7
20 | 4 | Performance data (cont) | 7 | 10 | 84.1 45.3 31.3
20 | 4 | Performance data (cont) | 7 | 11 | 71.8 71.8 30.4
20 | 4 | Performance data (cont) | 7 | 12 | 77.4 61.6 30.7
20 | 4 | Performance data (cont) | 7 | 13 | 85.3 47.1 31.5
20 | 4 | Performance data (cont) | 7 | 14 | 73.8 73.8 30.6
20 | 4 | Performance data (cont) | 7 | 15 | 77.9 65.6 30.9
21 | 1 | COOLING CAPACITIES — ENGLISH | 1 | 1 | 4500/0.12
21 | 1 | COOLING CAPACITIES — ENGLISH | 1 | 2 | 5250/0.14
21 | 1 | COOLING CAPACITIES — ENGLISH | 1 | 3 | 6000/0.15
21 | 1 | COOLING CAPACITIES — ENGLISH | 1 | 4 | 6750/0.17
21 | 2 | COOLING CAPACITIES — ENGLISH | 1 | 2 | 62
21 | 2 | COOLING CAPACITIES — ENGLISH | 1 | 3 | 67
21 | 2 | COOLING CAPACITIES — ENGLISH | 1 | 4 | 72
21 | 2 | COOLING CAPACITIES — ENGLISH | 1 | 5 | 62
21 | 2 | COOLING CAPACITIES — ENGLISH | 1 | 6 | 67
21 | 2 | COOLING CAPACITIES — ENGLISH | 1 | 7 | 72
21 | 2 | COOLING CAPACITIES — ENGLISH | 1 | 8 | 62
21 | 2 | COOLING CAPACITIES — ENGLISH | 1 | 9 | 67
21 | 2 | COOLING CAPACITIES — ENGLISH | 1 | 10 | 72
21 | 2 | COOLING CAPACITIES — ENGLISH | 1 | 11 | 62
21 | 2 | COOLING CAPACITIES — ENGLISH | 1 | 12 | 67
21 | 2 | COOLING CAPACITIES — ENGLISH | 1 | 13 | 72
21 | 2 | COOLING CAPACITIES — ENGLISH | 1 | 14 | 62
21 | 2 | COOLING CAPACITIES — ENGLISH | 1 | 15 | 67
21 | 2 | COOLING CAPACITIES — ENGLISH | 2 | 1 | TC SHC kW
21 | 2 | COOLING CAPACITIES — ENGLISH | 2 | 2 | 167 142 11.3
21 | 2 | COOLING CAPACITIES — ENGLISH | 2 | 3 | 182 121 11.7
21 | 2 | COOLING CAPACITIES — ENGLISH | 2 | 4 | 200 98 13.3
21 | 2 | COOLING CAPACITIES — ENGLISH | 2 | 5 | 172 154 11.5
21 | 2 | COOLING CAPACITIES — ENGLISH | 2 | 6 | 188 129 11.9
21 | 2 | COOLING CAPACITIES — ENGLISH | 2 | 7 | 206 104 13.4
21 | 2 | COOLING CAPACITIES — ENGLISH | 2 | 8 | 177 162 11.6
21 | 2 | COOLING CAPACITIES — ENGLISH | 2 | 9 | 193 137 12.0
21 | 2 | COOLING CAPACITIES — ENGLISH | 2 | 10 | 209 109 13.5
21 | 2 | COOLING CAPACITIES — ENGLISH | 2 | 11 | 180 171 11.7
21 | 2 | COOLING CAPACITIES — ENGLISH | 2 | 12 | 195 147 12.0
21 | 2 | COOLING CAPACITIES — ENGLISH | 2 | 13 | 211 118 13.6
21 | 2 | COOLING CAPACITIES — ENGLISH | 2 | 14 | 184 180 11.7
21 | 2 | COOLING CAPACITIES — ENGLISH | 2 | 15 | 197 154 12.1
21 | 2 | COOLING CAPACITIES — ENGLISH | 3 | 1 | TC SHC kW
21 | 2 | COOLING CAPACITIES — ENGLISH | 3 | 2 | 162 139 12.7
21 | 2 | COOLING CAPACITIES — ENGLISH | 3 | 3 | 177 118 13.0
21 | 2 | COOLING CAPACITIES — ENGLISH | 3 | 4 | 193 96 14.7
21 | 2 | COOLING CAPACITIES — ENGLISH | 3 | 5 | 167 150 12.8
21 | 2 | COOLING CAPACITIES — ENGLISH | 3 | 6 | 182 126 13.2
21 | 2 | COOLING CAPACITIES — ENGLISH | 3 | 7 | 198 101 14.9
21 | 2 | COOLING CAPACITIES — ENGLISH | 3 | 8 | 171 159 12.9
21 | 2 | COOLING CAPACITIES — ENGLISH | 3 | 9 | 186 134 13.3
21 | 2 | COOLING CAPACITIES — ENGLISH | 3 | 10 | 204 107 15.0
21 | 2 | COOLING CAPACITIES — ENGLISH | 3 | 11 | 175 168 13.0
21 | 2 | COOLING CAPACITIES — ENGLISH | 3 | 12 | 189 141 13.4
21 | 2 | COOLING CAPACITIES — ENGLISH | 3 | 13 | 206 113 15.1
21 | 2 | COOLING CAPACITIES — ENGLISH | 3 | 14 | 178 176 13.1
21 | 2 | COOLING CAPACITIES — ENGLISH | 3 | 15 | 191 151 13.5
21 | 2 | COOLING CAPACITIES — ENGLISH | 4 | 1 | TC SHC kW
21 | 2 | COOLING CAPACITIES — ENGLISH | 4 | 2 | 157 137 14.1
21 | 2 | COOLING CAPACITIES — ENGLISH | 4 | 3 | 171 115 14.5
21 | 2 | COOLING CAPACITIES — ENGLISH | 4 | 4 | 188 94 16.3
21 | 2 | COOLING CAPACITIES — ENGLISH | 4 | 5 | 162 147 14.3
21 | 2 | COOLING CAPACITIES — ENGLISH | 4 | 6 | 176 124 14.6
21 | 2 | COOLING CAPACITIES — ENGLISH | 4 | 7 | 193 99 16.5
21 | 2 | COOLING CAPACITIES — ENGLISH | 4 | 8 | 165 157 14.4
21 | 2 | COOLING CAPACITIES — ENGLISH | 4 | 9 | 180 131 14.7
21 | 2 | COOLING CAPACITIES — ENGLISH | 4 | 10 | 197 103 16.6
21 | 2 | COOLING CAPACITIES — ENGLISH | 4 | 11 | 169 166 14.5
21 | 2 | COOLING CAPACITIES — ENGLISH | 4 | 12 | 182 139 14.9
21 | 2 | COOLING CAPACITIES — ENGLISH | 4 | 13 | 200 108 16.7
21 | 2 | COOLING CAPACITIES — ENGLISH | 4 | 14 | 172 172 14.6
21 | 2 | COOLING CAPACITIES — ENGLISH | 4 | 15 | 186 146 15.0
21 | 2 | COOLING CAPACITIES — ENGLISH | 5 | 1 | TC SHC kW
21 | 2 | COOLING CAPACITIES — ENGLISH | 5 | 2 | 148 130 15.7
21 | 2 | COOLING CAPACITIES — ENGLISH | 5 | 3 | 162 111 16.2
21 | 2 | COOLING CAPACITIES — ENGLISH | 5 | 4 | 177 89 18.1
21 | 2 | COOLING CAPACITIES — ENGLISH | 5 | 5 | 153 140 15.9
21 | 2 | COOLING CAPACITIES — ENGLISH | 5 | 6 | 166 119 16.3
21 | 2 | COOLING CAPACITIES — ENGLISH | 5 | 7 | 180 94 18.3
21 | 2 | COOLING CAPACITIES — ENGLISH | 5 | 8 | 156 150 16.0
21 | 2 | COOLING CAPACITIES — ENGLISH | 5 | 9 | 169 126 16.4
21 | 2 | COOLING CAPACITIES — ENGLISH | 5 | 10 | 184 99 18.4
21 | 2 | COOLING CAPACITIES — ENGLISH | 5 | 11 | 159 158 16.1
21 | 2 | COOLING CAPACITIES — ENGLISH | 5 | 12 | 172 133 16.5
21 | 2 | COOLING CAPACITIES — ENGLISH | 5 | 13 | 188 103 18.5
21 | 2 | COOLING CAPACITIES — ENGLISH | 5 | 14 | 163 163 16.2
21 | 2 | COOLING CAPACITIES — ENGLISH | 5 | 15 | 174 140 16.6
21 | 2 | COOLING CAPACITIES — ENGLISH | 6 | 1 | TC SHC kW
21 | 2 | COOLING CAPACITIES — ENGLISH | 6 | 2 | 139 125 17.4
21 | 2 | COOLING CAPACITIES — ENGLISH | 6 | 3 | 152 106 17.9
21 | 2 | COOLING CAPACITIES — ENGLISH | 6 | 4 | 166 85 18.4
21 | 2 | COOLING CAPACITIES — ENGLISH | 6 | 5 | 143 135 17.6
21 | 2 | COOLING CAPACITIES — ENGLISH | 6 | 6 | 155 113 18.0
21 | 2 | COOLING CAPACITIES — ENGLISH | 6 | 7 | 170 90 18.6
21 | 2 | COOLING CAPACITIES — ENGLISH | 6 | 8 | 146 144 17.7
21 | 2 | COOLING CAPACITIES — ENGLISH | 6 | 9 | 158 121 18.1
21 | 2 | COOLING CAPACITIES — ENGLISH | 6 | 10 | 173 94 18.7
21 | 2 | COOLING CAPACITIES — ENGLISH | 6 | 11 | 150 150 17.9
21 | 2 | COOLING CAPACITIES — ENGLISH | 6 | 12 | 161 127 18.3
21 | 2 | COOLING CAPACITIES — ENGLISH | 6 | 13 | 174 98 18.7
21 | 2 | COOLING CAPACITIES — ENGLISH | 6 | 14 | 153 154 18.0
21 | 2 | COOLING CAPACITIES — ENGLISH | 6 | 15 | 163 134 18.3
21 | 2 | COOLING CAPACITIES — ENGLISH | 7 | 1 | TC SHC kW
21 | 2 | COOLING CAPACITIES — ENGLISH | 7 | 2 | 133 121 18.4
21 | 2 | COOLING CAPACITIES — ENGLISH | 7 | 3 | 145 102 18.9
21 | 2 | COOLING CAPACITIES — ENGLISH | 7 | 4 | 159 82 19.4
21 | 2 | COOLING CAPACITIES — ENGLISH | 7 | 5 | 136 131 18.5
21 | 2 | COOLING CAPACITIES — ENGLISH | 7 | 6 | 148 110 19.0
21 | 2 | COOLING CAPACITIES — ENGLISH | 7 | 7 | 163 86 19.6
21 | 2 | COOLING CAPACITIES — ENGLISH | 7 | 8 | 140 139 18.7
21 | 2 | COOLING CAPACITIES — ENGLISH | 7 | 9 | 151 117 19.1
21 | 2 | COOLING CAPACITIES — ENGLISH | 7 | 10 | 165 91 19.8
21 | 2 | COOLING CAPACITIES — ENGLISH | 7 | 11 | 143 144 18.8
21 | 2 | COOLING CAPACITIES — ENGLISH | 7 | 12 | 154 124 19.2
21 | 2 | COOLING CAPACITIES — ENGLISH | 7 | 13 | 166 95 19.8
21 | 2 | COOLING CAPACITIES — ENGLISH | 7 | 14 | 147 148 18.9
21 | 2 | COOLING CAPACITIES — ENGLISH | 7 | 15 | 155 129 19.3
21 | 2 | COOLING CAPACITIES — ENGLISH | 8 | 1 | TC SHC kW
21 | 2 | COOLING CAPACITIES — ENGLISH | 8 | 2 | 127 117 19.3
21 | 2 | COOLING CAPACITIES — ENGLISH | 8 | 3 | 138 99 19.7
21 | 2 | COOLING CAPACITIES — ENGLISH | 8 | 4 | 151 81 20.3
21 | 2 | COOLING CAPACITIES — ENGLISH | 8 | 5 | 130 126 19.4
21 | 2 | COOLING CAPACITIES — ENGLISH | 8 | 6 | 141 106 19.9
21 | 2 | COOLING CAPACITIES — ENGLISH | 8 | 7 | — — —
21 | 2 | COOLING CAPACITIES — ENGLISH | 8 | 8 | 134 134 19.6
21 | 2 | COOLING CAPACITIES — ENGLISH | 8 | 9 | 144 113 20.1
21 | 2 | COOLING CAPACITIES — ENGLISH | 8 | 10 | — — —
21 | 2 | COOLING CAPACITIES — ENGLISH | 8 | 11 | 137 138 19.7
21 | 2 | COOLING CAPACITIES — ENGLISH | 8 | 12 | 146 119 20.1
21 | 2 | COOLING CAPACITIES — ENGLISH | 8 | 13 | — — —
21 | 2 | COOLING CAPACITIES — ENGLISH | 8 | 14 | 140 142 19.9
21 | 2 | COOLING CAPACITIES — ENGLISH | 8 | 15 | 148 125 20.1
21 | 3 | COOLING CAPACITIES — ENGLISH | 1 | 1 | 6000/0.075
21 | 3 | COOLING CAPACITIES — ENGLISH | 1 | 2 | 7000/0.085
21 | 3 | COOLING CAPACITIES — ENGLISH | 1 | 3 | 8000/0.10
21 | 3 | COOLING CAPACITIES — ENGLISH | 1 | 4 | 9000/0.11
21 | 4 | COOLING CAPACITIES — ENGLISH | 1 | 2 | 62
21 | 4 | COOLING CAPACITIES — ENGLISH | 1 | 3 | 67
21 | 4 | COOLING CAPACITIES — ENGLISH | 1 | 4 | 72
21 | 4 | COOLING CAPACITIES — ENGLISH | 1 | 5 | 62
21 | 4 | COOLING CAPACITIES — ENGLISH | 1 | 6 | 67
21 | 4 | COOLING CAPACITIES — ENGLISH | 1 | 7 | 72
21 | 4 | COOLING CAPACITIES — ENGLISH | 1 | 8 | 62
21 | 4 | COOLING CAPACITIES — ENGLISH | 1 | 9 | 67
21 | 4 | COOLING CAPACITIES — ENGLISH | 1 | 10 | 72
21 | 4 | COOLING CAPACITIES — ENGLISH | 1 | 11 | 62
21 | 4 | COOLING CAPACITIES — ENGLISH | 1 | 12 | 67
21 | 4 | COOLING CAPACITIES — ENGLISH | 1 | 13 | 72
21 | 4 | COOLING CAPACITIES — ENGLISH | 1 | 14 | 62
21 | 4 | COOLING CAPACITIES — ENGLISH | 1 | 15 | 67
21 | 4 | COOLING CAPACITIES — ENGLISH | 2 | 1 | TC SHC kW
21 | 4 | COOLING CAPACITIES — ENGLISH | 2 | 2 | 219.5 188.0 15.1
21 | 4 | COOLING CAPACITIES — ENGLISH | 2 | 3 | 242.0 158.6 15.6
21 | 4 | COOLING CAPACITIES — ENGLISH | 2 | 4 | 262.6 125.9 16.5
21 | 4 | COOLING CAPACITIES — ENGLISH | 2 | 5 | 224.9 203.2 15.2
21 | 4 | COOLING CAPACITIES — ENGLISH | 2 | 6 | 248.0 169.6 15.8
21 | 4 | COOLING CAPACITIES — ENGLISH | 2 | 7 | 268.8 132.7 16.7
21 | 4 | COOLING CAPACITIES — ENGLISH | 2 | 8 | 229.2 217.0 15.4
21 | 4 | COOLING CAPACITIES — ENGLISH | 2 | 9 | 252.8 180.7 15.9
21 | 4 | COOLING CAPACITIES — ENGLISH | 2 | 10 | 274.0 139.3 16.9
21 | 4 | COOLING CAPACITIES — ENGLISH | 2 | 11 | 233.3 229.5 15.5
21 | 4 | COOLING CAPACITIES — ENGLISH | 2 | 12 | 256.1 191.1 16.0
21 | 4 | COOLING CAPACITIES — ENGLISH | 2 | 13 | 277.5 146.1 17.0
21 | 4 | COOLING CAPACITIES — ENGLISH | 2 | 14 | 238.0 237.6 15.7
21 | 4 | COOLING CAPACITIES — ENGLISH | 2 | 15 | 258.8 201.7 16.1
21 | 4 | COOLING CAPACITIES — ENGLISH | 3 | 1 | TC SHC kW
21 | 4 | COOLING CAPACITIES — ENGLISH | 3 | 2 | 211.9 184.5 16.7
21 | 4 | COOLING CAPACITIES — ENGLISH | 3 | 3 | 233.6 154.9 17.2
21 | 4 | COOLING CAPACITIES — ENGLISH | 3 | 4 | 253.5 122.7 18.2
21 | 4 | COOLING CAPACITIES — ENGLISH | 3 | 5 | 217.1 199.3 16.9
21 | 4 | COOLING CAPACITIES — ENGLISH | 3 | 6 | 239.6 166.7 17.4
21 | 4 | COOLING CAPACITIES — ENGLISH | 3 | 7 | 259.8 129.6 18.5
21 | 4 | COOLING CAPACITIES — ENGLISH | 3 | 8 | 221.4 212.9 17.0
21 | 4 | COOLING CAPACITIES — ENGLISH | 3 | 9 | 243.8 177.0 17.6
21 | 4 | COOLING CAPACITIES — ENGLISH | 3 | 10 | 264.6 136.1 18.6
21 | 4 | COOLING CAPACITIES — ENGLISH | 3 | 11 | 225.2 224.0 17.2
21 | 4 | COOLING CAPACITIES — ENGLISH | 3 | 12 | 246.8 187.2 17.7
21 | 4 | COOLING CAPACITIES — ENGLISH | 3 | 13 | 267.9 142.3 18.7
21 | 4 | COOLING CAPACITIES — ENGLISH | 3 | 14 | 231.3 230.7 17.4
21 | 4 | COOLING CAPACITIES — ENGLISH | 3 | 15 | 249.5 197.6 17.8
21 | 4 | COOLING CAPACITIES — ENGLISH | 4 | 1 | TC SHC kW
21 | 4 | COOLING CAPACITIES — ENGLISH | 4 | 2 | 204.1 180.8 18.5
21 | 4 | COOLING CAPACITIES — ENGLISH | 4 | 3 | 224.9 151.7 19.0
21 | 4 | COOLING CAPACITIES — ENGLISH | 4 | 4 | 244.2 119.4 20.1
21 | 4 | COOLING CAPACITIES — ENGLISH | 4 | 5 | 208.8 194.9 18.7
21 | 4 | COOLING CAPACITIES — ENGLISH | 4 | 6 | 229.9 162.7 19.2
21 | 4 | COOLING CAPACITIES — ENGLISH | 4 | 7 | 249.8 126.3 20.3
21 | 4 | COOLING CAPACITIES — ENGLISH | 4 | 8 | 213.0 208.3 18.8
21 | 4 | COOLING CAPACITIES — ENGLISH | 4 | 9 | 234.0 173.2 19.3
21 | 4 | COOLING CAPACITIES — ENGLISH | 4 | 10 | 253.9 132.7 20.4
21 | 4 | COOLING CAPACITIES — ENGLISH | 4 | 11 | 217.6 217.2 19.0
21 | 4 | COOLING CAPACITIES — ENGLISH | 4 | 12 | 236.8 183.0 19.4
21 | 4 | COOLING CAPACITIES — ENGLISH | 4 | 13 | 256.9 138.7 20.5
21 | 4 | COOLING CAPACITIES — ENGLISH | 4 | 14 | 222.9 222.4 19.1
21 | 4 | COOLING CAPACITIES — ENGLISH | 4 | 15 | 239.1 193.4 19.5
21 | 4 | COOLING CAPACITIES — ENGLISH | 5 | 1 | TC SHC kW
21 | 4 | COOLING CAPACITIES — ENGLISH | 5 | 2 | 194.5 176.2 20.3
21 | 4 | COOLING CAPACITIES — ENGLISH | 5 | 3 | 215.0 147.8 20.8
21 | 4 | COOLING CAPACITIES — ENGLISH | 5 | 4 | 233.7 115.7 22.0
21 | 4 | COOLING CAPACITIES — ENGLISH | 5 | 5 | 199.5 190.4 20.5
21 | 4 | COOLING CAPACITIES — ENGLISH | 5 | 6 | 219.8 158.7 21.0
21 | 4 | COOLING CAPACITIES — ENGLISH | 5 | 7 | 238.9 122.5 22.2
21 | 4 | COOLING CAPACITIES — ENGLISH | 5 | 8 | 203.8 202.5 20.6
21 | 4 | COOLING CAPACITIES — ENGLISH | 5 | 9 | 223.0 168.7 21.1
21 | 4 | COOLING CAPACITIES — ENGLISH | 5 | 10 | 242.7 128.8 22.3
21 | 4 | COOLING CAPACITIES — ENGLISH | 5 | 11 | 209.6 209.3 20.8
21 | 4 | COOLING CAPACITIES — ENGLISH | 5 | 12 | 225.6 179.6 21.2
21 | 4 | COOLING CAPACITIES — ENGLISH | 5 | 13 | 245.5 134.9 22.4
21 | 4 | COOLING CAPACITIES — ENGLISH | 5 | 14 | 214.3 213.8 21.0
21 | 4 | COOLING CAPACITIES — ENGLISH | 5 | 15 | 227.6 189.0 21.3
21 | 4 | COOLING CAPACITIES — ENGLISH | 6 | 1 | TC SHC kW
21 | 4 | COOLING CAPACITIES — ENGLISH | 6 | 2 | 185.1 171.5 22.1
21 | 4 | COOLING CAPACITIES — ENGLISH | 6 | 3 | 204.6 143.3 22.7
21 | 4 | COOLING CAPACITIES — ENGLISH | 6 | 4 | 222.6 111.9 23.9
21 | 4 | COOLING CAPACITIES — ENGLISH | 6 | 5 | 189.8 185.2 22.3
21 | 4 | COOLING CAPACITIES — ENGLISH | 6 | 6 | 208.9 154.7 22.8
21 | 4 | COOLING CAPACITIES — ENGLISH | 6 | 7 | 227.3 118.5 24.1
21 | 4 | COOLING CAPACITIES — ENGLISH | 6 | 8 | 194.8 194.3 22.5
21 | 4 | COOLING CAPACITIES — ENGLISH | 6 | 9 | 211.8 164.9 23.0
21 | 4 | COOLING CAPACITIES — ENGLISH | 6 | 10 | 230.6 124.5 24.2
21 | 4 | COOLING CAPACITIES — ENGLISH | 6 | 11 | 200.4 199.9 22.7
21 | 4 | COOLING CAPACITIES — ENGLISH | 6 | 12 | 214.0 174.3 23.1
21 | 4 | COOLING CAPACITIES — ENGLISH | 6 | 13 | 233.2 130.7 24.3
21 | 4 | COOLING CAPACITIES — ENGLISH | 6 | 14 | 204.6 204.2 22.9
21 | 4 | COOLING CAPACITIES — ENGLISH | 6 | 15 | 215.8 183.3 23.2
21 | 4 | COOLING CAPACITIES — ENGLISH | 7 | 1 | TC SHC kW
21 | 4 | COOLING CAPACITIES — ENGLISH | 7 | 2 | 174.9 166.2 24.0
21 | 4 | COOLING CAPACITIES — ENGLISH | 7 | 3 | 193.1 138.7 24.6
21 | 4 | COOLING CAPACITIES — ENGLISH | 7 | 4 | — — —
21 | 4 | COOLING CAPACITIES — ENGLISH | 7 | 5 | 179.9 178.5 24.2
21 | 4 | COOLING CAPACITIES — ENGLISH | 7 | 6 | 196.7 149.5 24.7
21 | 4 | COOLING CAPACITIES — ENGLISH | 7 | 7 | — — —
21 | 4 | COOLING CAPACITIES — ENGLISH | 7 | 8 | 185.3 184.9 24.4
21 | 4 | COOLING CAPACITIES — ENGLISH | 7 | 9 | 199.5 160.3 24.9
21 | 4 | COOLING CAPACITIES — ENGLISH | 7 | 10 | — — —
21 | 4 | COOLING CAPACITIES — ENGLISH | 7 | 11 | 190.6 190.2 24.6
21 | 4 | COOLING CAPACITIES — ENGLISH | 7 | 12 | 201.4 169.4 25.0
21 | 4 | COOLING CAPACITIES — ENGLISH | 7 | 13 | — — —
21 | 4 | COOLING CAPACITIES — ENGLISH | 7 | 14 | 194.7 194.0 24.8
21 | 4 | COOLING CAPACITIES — ENGLISH | 7 | 15 | 202.8 177.7 25.0
22 | 1 | Performance data (cont) | 1 | 1 | 7000/0.05
22 | 1 | Performance data (cont) | 1 | 2 | 8000/0.06
22 | 1 | Performance data (cont) | 1 | 3 | 9000/0.07
22 | 1 | Performance data (cont) | 1 | 4 | 10,000/0.08
22 | 2 | Performance data (cont) | 1 | 2 | 62
22 | 2 | Performance data (cont) | 1 | 3 | 67
22 | 2 | Performance data (cont) | 1 | 4 | 72
22 | 2 | Performance data (cont) | 1 | 5 | 62
22 | 2 | Performance data (cont) | 1 | 6 | 67
22 | 2 | Performance data (cont) | 1 | 7 | 72
22 | 2 | Performance data (cont) | 1 | 8 | 62
22 | 2 | Performance data (cont) | 1 | 9 | 67
22 | 2 | Performance data (cont) | 1 | 10 | 72
22 | 2 | Performance data (cont) | 1 | 11 | 62
22 | 2 | Performance data (cont) | 1 | 12 | 67
22 | 2 | Performance data (cont) | 1 | 13 | 72
22 | 2 | Performance data (cont) | 1 | 14 | 62
22 | 2 | Performance data (cont) | 1 | 15 | 67
22 | 2 | Performance data (cont) | 2 | 1 | TC SHC kW
22 | 2 | Performance data (cont) | 2 | 2 | 270.9 231.2 20.1
22 | 2 | Performance data (cont) | 2 | 3 | 298.9 195.1 20.8
22 | 2 | Performance data (cont) | 2 | 4 | 329.5 158.8 21.6
22 | 2 | Performance data (cont) | 2 | 5 | 277.1 247.7 20.3
22 | 2 | Performance data (cont) | 2 | 6 | 305.7 207.1 21.0
22 | 2 | Performance data (cont) | 2 | 7 | 336.5 165.1 21.8
22 | 2 | Performance data (cont) | 2 | 8 | 282.2 264.4 20.4
22 | 2 | Performance data (cont) | 2 | 9 | 310.5 219.8 21.2
22 | 2 | Performance data (cont) | 2 | 10 | 342.2 174.6 22.0
22 | 2 | Performance data (cont) | 2 | 11 | 286.2 278.8 20.6
22 | 2 | Performance data (cont) | 2 | 12 | 313.6 234.5 21.3
22 | 2 | Performance data (cont) | 2 | 13 | 346.8 181.9 22.2
22 | 2 | Performance data (cont) | 2 | 14 | 292.5 292.1 20.8
22 | 2 | Performance data (cont) | 2 | 15 | 318.6 247.9 21.5
22 | 2 | Performance data (cont) | 3 | 1 | TC SHC kW
22 | 2 | Performance data (cont) | 3 | 2 | 261.5 226.8 22.2
22 | 2 | Performance data (cont) | 3 | 3 | 288.5 190.8 23.0
22 | 2 | Performance data (cont) | 3 | 4 | 317.7 153.6 23.8
22 | 2 | Performance data (cont) | 3 | 5 | 267.1 243.1 22.4
22 | 2 | Performance data (cont) | 3 | 6 | 295.0 202.9 23.2
22 | 2 | Performance data (cont) | 3 | 7 | 324.2 161.9 24.0
22 | 2 | Performance data (cont) | 3 | 8 | 272.5 257.9 22.6
22 | 2 | Performance data (cont) | 3 | 9 | 300.2 214.6 23.4
22 | 2 | Performance data (cont) | 3 | 10 | 329.8 168.8 24.2
22 | 2 | Performance data (cont) | 3 | 11 | 276.5 272.2 22.8
22 | 2 | Performance data (cont) | 3 | 12 | 304.2 226.7 23.5
22 | 2 | Performance data (cont) | 3 | 13 | 334.8 176.0 24.4
22 | 2 | Performance data (cont) | 3 | 14 | 283.5 283.3 23.0
22 | 2 | Performance data (cont) | 3 | 15 | 308.4 240.5 23.7
22 | 2 | Performance data (cont) | 4 | 1 | TC SHC kW
22 | 2 | Performance data (cont) | 4 | 2 | 251.5 221.8 24.6
22 | 2 | Performance data (cont) | 4 | 3 | 277.2 186.4 25.3
22 | 2 | Performance data (cont) | 4 | 4 | 305.1 150.1 26.1
22 | 2 | Performance data (cont) | 4 | 5 | 256.6 237.9 24.7
22 | 2 | Performance data (cont) | 4 | 6 | 283.3 198.3 25.5
22 | 2 | Performance data (cont) | 4 | 7 | 311.0 157.1 26.3
22 | 2 | Performance data (cont) | 4 | 8 | 261.9 252.7 24.9
22 | 2 | Performance data (cont) | 4 | 9 | 287.3 211.0 25.7
22 | 2 | Performance data (cont) | 4 | 10 | 316.5 164.2 26.5
22 | 2 | Performance data (cont) | 4 | 11 | 266.4 265.2 25.1
22 | 2 | Performance data (cont) | 4 | 12 | 291.9 221.3 25.8
22 | 2 | Performance data (cont) | 4 | 13 | 320.8 171.0 26.7
22 | 2 | Performance data (cont) | 4 | 14 | 274.0 273.7 25.4
22 | 2 | Performance data (cont) | 4 | 15 | 295.4 235.0 26.0
22 | 2 | Performance data (cont) | 5 | 1 | TC SHC kW
22 | 2 | Performance data (cont) | 5 | 2 | 240.6 215.9 27.0
22 | 2 | Performance data (cont) | 5 | 3 | 265.7 181.8 27.8
22 | 2 | Performance data (cont) | 5 | 4 | 291.4 145.2 28.6
22 | 2 | Performance data (cont) | 5 | 5 | 245.5 231.9 27.2
22 | 2 | Performance data (cont) | 5 | 6 | 270.5 192.9 28.0
22 | 2 | Performance data (cont) | 5 | 7 | 297.8 152.5 28.8
22 | 2 | Performance data (cont) | 5 | 8 | 250.7 245.8 27.4
22 | 2 | Performance data (cont) | 5 | 9 | 274.6 205.0 28.1
22 | 2 | Performance data (cont) | 5 | 10 | 302.2 159.2 29.0
22 | 2 | Performance data (cont) | 5 | 11 | 256.0 255.9 27.6
22 | 2 | Performance data (cont) | 5 | 12 | 277.9 216.1 28.3
22 | 2 | Performance data (cont) | 5 | 13 | 305.7 166.5 29.2
22 | 2 | Performance data (cont) | 5 | 14 | 263.4 263.2 27.9
22 | 2 | Performance data (cont) | 5 | 15 | 281.4 229.5 28.4
22 | 2 | Performance data (cont) | 6 | 1 | TC SHC kW
22 | 2 | Performance data (cont) | 6 | 2 | 229.0 211.2 29.5
22 | 2 | Performance data (cont) | 6 | 3 | 252.4 176.8 30.3
22 | 2 | Performance data (cont) | 6 | 4 | 277.3 140.0 31.1
22 | 2 | Performance data (cont) | 6 | 5 | 233.5 225.9 29.7
22 | 2 | Performance data (cont) | 6 | 6 | 256.9 187.6 30.5
22 | 2 | Performance data (cont) | 6 | 7 | 281.5 147.1 31.3
22 | 2 | Performance data (cont) | 6 | 8 | 239.0 238.3 30.0
22 | 2 | Performance data (cont) | 6 | 9 | 260.6 199.4 30.7
22 | 2 | Performance data (cont) | 6 | 10 | 285.4 153.4 31.5
22 | 2 | Performance data (cont) | 6 | 11 | 245.2 245.0 30.2
22 | 2 | Performance data (cont) | 6 | 12 | 263.7 210.6 30.8
22 | 2 | Performance data (cont) | 6 | 13 | — — —
22 | 2 | Performance data (cont) | 6 | 14 | 252.0 251.9 30.5
22 | 2 | Performance data (cont) | 6 | 15 | 267.0 223.2 31.0
22 | 2 | Performance data (cont) | 7 | 1 | TC SHC kW
22 | 2 | Performance data (cont) | 7 | 2 | 225.6 209.6 30.3
22 | 2 | Performance data (cont) | 7 | 3 | 248.0 175.1 31.1
22 | 2 | Performance data (cont) | 7 | 4 | — — —
22 | 2 | Performance data (cont) | 7 | 5 | 230.0 223.9 30.5
22 | 2 | Performance data (cont) | 7 | 6 | 252.3 186.0 31.2
22 | 2 | Performance data (cont) | 7 | 7 | — — —
22 | 2 | Performance data (cont) | 7 | 8 | 235.1 234.7 30.7
22 | 2 | Performance data (cont) | 7 | 9 | 255.3 197.4 31.4
22 | 2 | Performance data (cont) | 7 | 10 | — — —
22 | 2 | Performance data (cont) | 7 | 11 | 240.9 240.5 31.0
22 | 2 | Performance data (cont) | 7 | 12 | 257.5 208.6 31.5
22 | 2 | Performance data (cont) | 7 | 13 | — — —
22 | 2 | Performance data (cont) | 7 | 14 | 247.2 247.1 31.2
22 | 2 | Performance data (cont) | 7 | 15 | — — —
22 | 2 | Performance data (cont) | 8 | 1 | TC SHC kW
22 | 2 | Performance data (cont) | 8 | 2 | 222.6 208.0 30.8
22 | 2 | Performance data (cont) | 8 | 3 | — — —
22 | 2 | Performance data (cont) | 8 | 4 | — — —
22 | 2 | Performance data (cont) | 8 | 5 | 227.4 222.5 31.0
22 | 2 | Performance data (cont) | 8 | 6 | — — —
22 | 2 | Performance data (cont) | 8 | 7 | — — —
22 | 2 | Performance data (cont) | 8 | 8 | 233.6 233.3 31.3
22 | 2 | Performance data (cont) | 8 | 9 | — — —
22 | 2 | Performance data (cont) | 8 | 10 | — — —
22 | 2 | Performance data (cont) | 8 | 11 | 239.0 239.0 31.5
22 | 2 | Performance data (cont) | 8 | 12 | — — —
22 | 2 | Performance data (cont) | 8 | 13 | — — —
22 | 2 | Performance data (cont) | 8 | 14 | — — —
22 | 2 | Performance data (cont) | 8 | 15 | — — —
22 | 3 | Performance data (cont) | 1 | 1 | 7000/0.05
22 | 3 | Performance data (cont) | 1 | 2 | 8000/0.06
22 | 3 | Performance data (cont) | 1 | 3 | 9000/0.07
22 | 3 | Performance data (cont) | 1 | 4 | 10,000/0.08
22 | 4 | Performance data (cont) | 1 | 2 | 62
22 | 4 | Performance data (cont) | 1 | 3 | 67
22 | 4 | Performance data (cont) | 1 | 4 | 72
22 | 4 | Performance data (cont) | 1 | 5 | 62
22 | 4 | Performance data (cont) | 1 | 6 | 67
22 | 4 | Performance data (cont) | 1 | 7 | 72
22 | 4 | Performance data (cont) | 1 | 8 | 62
22 | 4 | Performance data (cont) | 1 | 9 | 67
22 | 4 | Performance data (cont) | 1 | 10 | 72
22 | 4 | Performance data (cont) | 1 | 11 | 62
22 | 4 | Performance data (cont) | 1 | 12 | 67
22 | 4 | Performance data (cont) | 1 | 13 | 72
22 | 4 | Performance data (cont) | 1 | 14 | 62
22 | 4 | Performance data (cont) | 1 | 15 | 67
22 | 4 | Performance data (cont) | 2 | 1 | TC SHC kW
22 | 4 | Performance data (cont) | 2 | 2 | 281 236 18.2
22 | 4 | Performance data (cont) | 2 | 3 | 310 201 18.8
22 | 4 | Performance data (cont) | 2 | 4 | 343 163 19.4
22 | 4 | Performance data (cont) | 2 | 5 | 288 253 18.4
22 | 4 | Performance data (cont) | 2 | 6 | 318 214 19.0
22 | 4 | Performance data (cont) | 2 | 7 | 351 172 19.6
22 | 4 | Performance data (cont) | 2 | 8 | 292 272 18.5
22 | 4 | Performance data (cont) | 2 | 9 | 323 228 19.1
22 | 4 | Performance data (cont) | 2 | 10 | 355 185 19.7
22 | 4 | Performance data (cont) | 2 | 11 | 298 284 18.6
22 | 4 | Performance data (cont) | 2 | 12 | 327 240 19.2
22 | 4 | Performance data (cont) | 2 | 13 | 361 193 19.9
22 | 4 | Performance data (cont) | 2 | 14 | 304 300 18.8
22 | 4 | Performance data (cont) | 2 | 15 | 332 257 19.4
22 | 4 | Performance data (cont) | 3 | 1 | TC SHC kW
22 | 4 | Performance data (cont) | 3 | 2 | 272 232 20.3
22 | 4 | Performance data (cont) | 3 | 3 | 300 196 20.8
22 | 4 | Performance data (cont) | 3 | 4 | 332 159 21.5
22 | 4 | Performance data (cont) | 3 | 5 | 279 249 20.4
22 | 4 | Performance data (cont) | 3 | 6 | 309 209 21.0
22 | 4 | Performance data (cont) | 3 | 7 | 340 168 21.7
22 | 4 | Performance data (cont) | 3 | 8 | 284 265 20.6
22 | 4 | Performance data (cont) | 3 | 9 | 314 222 21.2
22 | 4 | Performance data (cont) | 3 | 10 | 347 176 21.8
22 | 4 | Performance data (cont) | 3 | 11 | 289 279 20.8
22 | 4 | Performance data (cont) | 3 | 12 | 318 232 21.4
22 | 4 | Performance data (cont) | 3 | 13 | 351 183 22.0
22 | 4 | Performance data (cont) | 3 | 14 | 296 293 20.9
22 | 4 | Performance data (cont) | 3 | 15 | 322 250 21.4
22 | 4 | Performance data (cont) | 4 | 1 | TC SHC kW
22 | 4 | Performance data (cont) | 4 | 2 | 262 227 22.6
22 | 4 | Performance data (cont) | 4 | 3 | 291 192 23.1
22 | 4 | Performance data (cont) | 4 | 4 | 320 156 23.7
22 | 4 | Performance data (cont) | 4 | 5 | 268 244 22.6
22 | 4 | Performance data (cont) | 4 | 6 | 297 204 23.3
22 | 4 | Performance data (cont) | 4 | 7 | 327 163 23.9
22 | 4 | Performance data (cont) | 4 | 8 | 274 258 22.8
22 | 4 | Performance data (cont) | 4 | 9 | 302 216 23.4
22 | 4 | Performance data (cont) | 4 | 10 | 333 170 24.1
22 | 4 | Performance data (cont) | 4 | 11 | 279 271 23.0
22 | 4 | Performance data (cont) | 4 | 12 | 307 227 23.6
22 | 4 | Performance data (cont) | 4 | 13 | 338 178 24.2
22 | 4 | Performance data (cont) | 4 | 14 | 285 283 23.1
22 | 4 | Performance data (cont) | 4 | 15 | 311 241 23.6
22 | 4 | Performance data (cont) | 5 | 1 | TC SHC kW
22 | 4 | Performance data (cont) | 5 | 2 | 252 222 24.9
22 | 4 | Performance data (cont) | 5 | 3 | 279 187 25.5
22 | 4 | Performance data (cont) | 5 | 4 | 307 151 26.1
22 | 4 | Performance data (cont) | 5 | 5 | 258 238 25.0
22 | 4 | Performance data (cont) | 5 | 6 | 285 200 25.7
22 | 4 | Performance data (cont) | 5 | 7 | 313 158 26.3
22 | 4 | Performance data (cont) | 5 | 8 | 263 253 25.2
22 | 4 | Performance data (cont) | 5 | 9 | 290 210 25.8
22 | 4 | Performance data (cont) | 5 | 10 | 319 165 26.5
22 | 4 | Performance data (cont) | 5 | 11 | 268 264 25.3
22 | 4 | Performance data (cont) | 5 | 12 | 294 222 25.9
22 | 4 | Performance data (cont) | 5 | 13 | 323 172 26.5
22 | 4 | Performance data (cont) | 5 | 14 | 276 275 25.5
22 | 4 | Performance data (cont) | 5 | 15 | 297 237 26.0
22 | 4 | Performance data (cont) | 6 | 1 | TC SHC kW
22 | 4 | Performance data (cont) | 6 | 2 | 240 217 27.3
22 | 4 | Performance data (cont) | 6 | 3 | 266 182 27.9
22 | 4 | Performance data (cont) | 6 | 4 | 292 146 28.5
22 | 4 | Performance data (cont) | 6 | 5 | 246 232 27.5
22 | 4 | Performance data (cont) | 6 | 6 | 272 194 28.1
22 | 4 | Performance data (cont) | 6 | 7 | 299 153 28.7
22 | 4 | Performance data (cont) | 6 | 8 | 252 245 27.7
22 | 4 | Performance data (cont) | 6 | 9 | 276 206 28.3
22 | 4 | Performance data (cont) | 6 | 10 | 303 160 28.9
22 | 4 | Performance data (cont) | 6 | 11 | 258 256 27.8
22 | 4 | Performance data (cont) | 6 | 12 | 279 217 28.3
22 | 4 | Performance data (cont) | 6 | 13 | 308 169 28.9
22 | 4 | Performance data (cont) | 6 | 14 | 265 264 28.0
22 | 4 | Performance data (cont) | 6 | 15 | 283 231 28.5
22 | 4 | Performance data (cont) | 7 | 1 | TC SHC kW
22 | 4 | Performance data (cont) | 7 | 2 | 229 211 29.9
22 | 4 | Performance data (cont) | 7 | 3 | 252 177 30.4
22 | 4 | Performance data (cont) | 7 | 4 | 278 141 31.1
22 | 4 | Performance data (cont) | 7 | 5 | 234 226 30.0
22 | 4 | Performance data (cont) | 7 | 6 | 258 189 30.6
22 | 4 | Performance data (cont) | 7 | 7 | 283 148 31.2
22 | 4 | Performance data (cont) | 7 | 8 | 240 236 30.2
22 | 4 | Performance data (cont) | 7 | 9 | 261 200 30.7
22 | 4 | Performance data (cont) | 7 | 10 | 287 155 31.3
22 | 4 | Performance data (cont) | 7 | 11 | 245 245 30.4
22 | 4 | Performance data (cont) | 7 | 12 | 264 210 30.7
22 | 4 | Performance data (cont) | 7 | 13 | 291 161 31.5
22 | 4 | Performance data (cont) | 7 | 14 | 252 252 30.6
22 | 4 | Performance data (cont) | 7 | 15 | 266 224 30.9
23 | 1 | GLYCOL HEATING PERFORMANCE | 1 | 1 | 4400
23 | 1 | GLYCOL HEATING PERFORMANCE | 1 | 2 | 5400
23 | 2 | GLYCOL HEATING PERFORMANCE | 1 | 2 | 25
23 | 2 | GLYCOL HEATING PERFORMANCE | 1 | 5 | 50
23 | 2 | GLYCOL HEATING PERFORMANCE | 1 | 8 | 25
23 | 2 | GLYCOL HEATING PERFORMANCE | 1 | 11 | 50
23 | 2 | GLYCOL HEATING PERFORMANCE | 1 | 14 | 25
23 | 2 | GLYCOL HEATING PERFORMANCE | 2 | 1 | Ewt
23 | 2 | GLYCOL HEATING PERFORMANCE | 2 | 2 | Cap
23 | 2 | GLYCOL HEATING PERFORMANCE | 2 | 3 | Gpm
23 | 2 | GLYCOL HEATING PERFORMANCE | 2 | 4 | Ldb
23 | 2 | GLYCOL HEATING PERFORMANCE | 2 | 5 | Cap
23 | 2 | GLYCOL HEATING PERFORMANCE | 2 | 6 | Gpm
23 | 2 | GLYCOL HEATING PERFORMANCE | 2 | 7 | Ldb
23 | 2 | GLYCOL HEATING PERFORMANCE | 2 | 8 | Cap
23 | 2 | GLYCOL HEATING PERFORMANCE | 2 | 9 | Gpm
23 | 2 | GLYCOL HEATING PERFORMANCE | 2 | 10 | Ldb
23 | 2 | GLYCOL HEATING PERFORMANCE | 2 | 11 | Cap
23 | 2 | GLYCOL HEATING PERFORMANCE | 2 | 12 | Gpm
23 | 2 | GLYCOL HEATING PERFORMANCE | 2 | 13 | Ldb
23 | 2 | GLYCOL HEATING PERFORMANCE | 2 | 14 | Cap
23 | 2 | GLYCOL HEATING PERFORMANCE | 2 | 15 | Gpm
23 | 2 | GLYCOL HEATING PERFORMANCE | 2 | 16 | Ldb
23 | 2 | GLYCOL HEATING PERFORMANCE | 2 | 17 | Cap
23 | 2 | GLYCOL HEATING PERFORMANCE | 2 | 18 | Gpm
23 | 2 | GLYCOL HEATING PERFORMANCE | 3 | 1 | 200
23 | 2 | GLYCOL HEATING PERFORMANCE | 3 | 2 | 310
23 | 2 | GLYCOL HEATING PERFORMANCE | 3 | 3 | 33
23 | 2 | GLYCOL HEATING PERFORMANCE | 3 | 4 | 120
23 | 2 | GLYCOL HEATING PERFORMANCE | 3 | 5 | 293
23 | 2 | GLYCOL HEATING PERFORMANCE | 3 | 6 | 33
23 | 2 | GLYCOL HEATING PERFORMANCE | 3 | 7 | 116
23 | 2 | GLYCOL HEATING PERFORMANCE | 3 | 8 | 347
23 | 2 | GLYCOL HEATING PERFORMANCE | 3 | 9 | 37
23 | 2 | GLYCOL HEATING PERFORMANCE | 3 | 10 | 115
23 | 2 | GLYCOL HEATING PERFORMANCE | 3 | 11 | 327
23 | 2 | GLYCOL HEATING PERFORMANCE | 3 | 12 | 37
23 | 2 | GLYCOL HEATING PERFORMANCE | 3 | 13 | 111
23 | 2 | GLYCOL HEATING PERFORMANCE | 3 | 14 | 405
23 | 2 | GLYCOL HEATING PERFORMANCE | 3 | 15 | 43
23 | 2 | GLYCOL HEATING PERFORMANCE | 3 | 16 | 107
23 | 2 | GLYCOL HEATING PERFORMANCE | 3 | 17 | 381
23 | 2 | GLYCOL HEATING PERFORMANCE | 3 | 18 | 43
23 | 2 | GLYCOL HEATING PERFORMANCE | 4 | 1 | 180
23 | 2 | GLYCOL HEATING PERFORMANCE | 4 | 2 | 255
23 | 2 | GLYCOL HEATING PERFORMANCE | 4 | 3 | 27
23 | 2 | GLYCOL HEATING PERFORMANCE | 4 | 4 | 108
23 | 2 | GLYCOL HEATING PERFORMANCE | 4 | 5 | 237
23 | 2 | GLYCOL HEATING PERFORMANCE | 4 | 6 | 27
23 | 2 | GLYCOL HEATING PERFORMANCE | 4 | 7 | 105
23 | 2 | GLYCOL HEATING PERFORMANCE | 4 | 8 | 285
23 | 2 | GLYCOL HEATING PERFORMANCE | 4 | 9 | 30
23 | 2 | GLYCOL HEATING PERFORMANCE | 4 | 10 | 104
23 | 2 | GLYCOL HEATING PERFORMANCE | 4 | 11 | 264
23 | 2 | GLYCOL HEATING PERFORMANCE | 4 | 12 | 30
23 | 2 | GLYCOL HEATING PERFORMANCE | 4 | 13 | 101
23 | 2 | GLYCOL HEATING PERFORMANCE | 4 | 14 | 332
23 | 2 | GLYCOL HEATING PERFORMANCE | 4 | 15 | 35
23 | 2 | GLYCOL HEATING PERFORMANCE | 4 | 16 | 98
23 | 2 | GLYCOL HEATING PERFORMANCE | 4 | 17 | 306
23 | 2 | GLYCOL HEATING PERFORMANCE | 4 | 18 | 35
23 | 2 | GLYCOL HEATING PERFORMANCE | 5 | 1 | 160
23 | 2 | GLYCOL HEATING PERFORMANCE | 5 | 2 | 200
23 | 2 | GLYCOL HEATING PERFORMANCE | 5 | 3 | 21
23 | 2 | GLYCOL HEATING PERFORMANCE | 5 | 4 | 97
23 | 2 | GLYCOL HEATING PERFORMANCE | 5 | 5 | 181
23 | 2 | GLYCOL HEATING PERFORMANCE | 5 | 6 | 21
23 | 2 | GLYCOL HEATING PERFORMANCE | 5 | 7 | 93
23 | 2 | GLYCOL HEATING PERFORMANCE | 5 | 8 | 223
23 | 2 | GLYCOL HEATING PERFORMANCE | 5 | 9 | 24
23 | 2 | GLYCOL HEATING PERFORMANCE | 5 | 10 | 94
23 | 2 | GLYCOL HEATING PERFORMANCE | 5 | 11 | 202
23 | 2 | GLYCOL HEATING PERFORMANCE | 5 | 12 | 23
23 | 2 | GLYCOL HEATING PERFORMANCE | 5 | 13 | 90
23 | 2 | GLYCOL HEATING PERFORMANCE | 5 | 14 | 259
23 | 2 | GLYCOL HEATING PERFORMANCE | 5 | 15 | 27
23 | 2 | GLYCOL HEATING PERFORMANCE | 5 | 16 | 89
23 | 2 | GLYCOL HEATING PERFORMANCE | 5 | 17 | 233
23 | 2 | GLYCOL HEATING PERFORMANCE | 5 | 18 | 27
23 | 2 | GLYCOL HEATING PERFORMANCE | 6 | 1 | 200
23 | 2 | GLYCOL HEATING PERFORMANCE | 6 | 2 | 274
23 | 2 | GLYCOL HEATING PERFORMANCE | 6 | 3 | 29
23 | 2 | GLYCOL HEATING PERFORMANCE | 6 | 4 | 127
23 | 2 | GLYCOL HEATING PERFORMANCE | 6 | 5 | 257
23 | 2 | GLYCOL HEATING PERFORMANCE | 6 | 6 | 29
23 | 2 | GLYCOL HEATING PERFORMANCE | 6 | 7 | 124
23 | 2 | GLYCOL HEATING PERFORMANCE | 6 | 8 | 306
23 | 2 | GLYCOL HEATING PERFORMANCE | 6 | 9 | 32
23 | 2 | GLYCOL HEATING PERFORMANCE | 6 | 10 | 123
23 | 2 | GLYCOL HEATING PERFORMANCE | 6 | 11 | 287
23 | 2 | GLYCOL HEATING PERFORMANCE | 6 | 12 | 33
23 | 2 | GLYCOL HEATING PERFORMANCE | 6 | 13 | 119
23 | 2 | GLYCOL HEATING PERFORMANCE | 6 | 14 | 357
23 | 2 | GLYCOL HEATING PERFORMANCE | 6 | 15 | 38
23 | 2 | GLYCOL HEATING PERFORMANCE | 6 | 16 | 116
23 | 2 | GLYCOL HEATING PERFORMANCE | 6 | 17 | 333
23 | 2 | GLYCOL HEATING PERFORMANCE | 6 | 18 | 38
23 | 2 | GLYCOL HEATING PERFORMANCE | 7 | 1 | 180
23 | 2 | GLYCOL HEATING PERFORMANCE | 7 | 2 | 218
23 | 2 | GLYCOL HEATING PERFORMANCE | 7 | 3 | 23
23 | 2 | GLYCOL HEATING PERFORMANCE | 7 | 4 | 116
23 | 2 | GLYCOL HEATING PERFORMANCE | 7 | 5 | 201
23 | 2 | GLYCOL HEATING PERFORMANCE | 7 | 6 | 23
23 | 2 | GLYCOL HEATING PERFORMANCE | 7 | 7 | 112
23 | 2 | GLYCOL HEATING PERFORMANCE | 7 | 8 | 244
23 | 2 | GLYCOL HEATING PERFORMANCE | 7 | 9 | 26
23 | 2 | GLYCOL HEATING PERFORMANCE | 7 | 10 | 112
23 | 2 | GLYCOL HEATING PERFORMANCE | 7 | 11 | 224
23 | 2 | GLYCOL HEATING PERFORMANCE | 7 | 12 | 26
23 | 2 | GLYCOL HEATING PERFORMANCE | 7 | 13 | 109
23 | 2 | GLYCOL HEATING PERFORMANCE | 7 | 14 | 284
23 | 2 | GLYCOL HEATING PERFORMANCE | 7 | 15 | 30
23 | 2 | GLYCOL HEATING PERFORMANCE | 7 | 16 | 107
23 | 2 | GLYCOL HEATING PERFORMANCE | 7 | 17 | 259
23 | 2 | GLYCOL HEATING PERFORMANCE | 7 | 18 | 30
23 | 2 | GLYCOL HEATING PERFORMANCE | 8 | 1 | 160
23 | 2 | GLYCOL HEATING PERFORMANCE | 8 | 2 | 164
23 | 2 | GLYCOL HEATING PERFORMANCE | 8 | 3 | 17
23 | 2 | GLYCOL HEATING PERFORMANCE | 8 | 4 | 104
23 | 2 | GLYCOL HEATING PERFORMANCE | 8 | 5 | 146
23 | 2 | GLYCOL HEATING PERFORMANCE | 8 | 6 | 17
23 | 2 | GLYCOL HEATING PERFORMANCE | 8 | 7 | 100
23 | 2 | GLYCOL HEATING PERFORMANCE | 8 | 8 | 183
23 | 2 | GLYCOL HEATING PERFORMANCE | 8 | 9 | 19
23 | 2 | GLYCOL HEATING PERFORMANCE | 8 | 10 | 101
23 | 2 | GLYCOL HEATING PERFORMANCE | 8 | 11 | 162
23 | 2 | GLYCOL HEATING PERFORMANCE | 8 | 12 | 19
23 | 2 | GLYCOL HEATING PERFORMANCE | 8 | 13 | 98
23 | 2 | GLYCOL HEATING PERFORMANCE | 8 | 14 | 212
23 | 2 | GLYCOL HEATING PERFORMANCE | 8 | 15 | 22
23 | 2 | GLYCOL HEATING PERFORMANCE | 8 | 16 | 97
23 | 2 | GLYCOL HEATING PERFORMANCE | 8 | 17 | 187
23 | 2 | GLYCOL HEATING PERFORMANCE | 8 | 18 | 22
23 | 2 | GLYCOL HEATING PERFORMANCE | 9 | 1 | 200
23 | 2 | GLYCOL HEATING PERFORMANCE | 9 | 2 | 249
23 | 2 | GLYCOL HEATING PERFORMANCE | 9 | 3 | 26
23 | 2 | GLYCOL HEATING PERFORMANCE | 9 | 4 | 132
23 | 2 | GLYCOL HEATING PERFORMANCE | 9 | 5 | 233
23 | 2 | GLYCOL HEATING PERFORMANCE | 9 | 6 | 27
23 | 2 | GLYCOL HEATING PERFORMANCE | 9 | 7 | 129
23 | 2 | GLYCOL HEATING PERFORMANCE | 9 | 8 | 279
23 | 2 | GLYCOL HEATING PERFORMANCE | 9 | 9 | 30
23 | 2 | GLYCOL HEATING PERFORMANCE | 9 | 10 | 128
23 | 2 | GLYCOL HEATING PERFORMANCE | 9 | 11 | 260
23 | 2 | GLYCOL HEATING PERFORMANCE | 9 | 12 | 30
23 | 2 | GLYCOL HEATING PERFORMANCE | 9 | 13 | 125
23 | 2 | GLYCOL HEATING PERFORMANCE | 9 | 14 | 325
23 | 2 | GLYCOL HEATING PERFORMANCE | 9 | 15 | 34
23 | 2 | GLYCOL HEATING PERFORMANCE | 9 | 16 | 122
23 | 2 | GLYCOL HEATING PERFORMANCE | 9 | 17 | 302
23 | 2 | GLYCOL HEATING PERFORMANCE | 9 | 18 | 34
23 | 2 | GLYCOL HEATING PERFORMANCE | 10 | 1 | 180
23 | 2 | GLYCOL HEATING PERFORMANCE | 10 | 2 | 194
23 | 2 | GLYCOL HEATING PERFORMANCE | 10 | 3 | 21
23 | 2 | GLYCOL HEATING PERFORMANCE | 10 | 4 | 121
23 | 2 | GLYCOL HEATING PERFORMANCE | 10 | 5 | 177
23 | 2 | GLYCOL HEATING PERFORMANCE | 10 | 6 | 20
23 | 2 | GLYCOL HEATING PERFORMANCE | 10 | 7 | 117
23 | 2 | GLYCOL HEATING PERFORMANCE | 10 | 8 | 217
23 | 2 | GLYCOL HEATING PERFORMANCE | 10 | 9 | 23
23 | 2 | GLYCOL HEATING PERFORMANCE | 10 | 10 | 117
23 | 2 | GLYCOL HEATING PERFORMANCE | 10 | 11 | 197
23 | 2 | GLYCOL HEATING PERFORMANCE | 10 | 12 | 23
23 | 2 | GLYCOL HEATING PERFORMANCE | 10 | 13 | 114
23 | 2 | GLYCOL HEATING PERFORMANCE | 10 | 14 | 252
23 | 2 | GLYCOL HEATING PERFORMANCE | 10 | 15 | 26
23 | 2 | GLYCOL HEATING PERFORMANCE | 10 | 16 | 113
23 | 2 | GLYCOL HEATING PERFORMANCE | 10 | 17 | 228
23 | 2 | GLYCOL HEATING PERFORMANCE | 10 | 18 | 27
23 | 2 | GLYCOL HEATING PERFORMANCE | 11 | 1 | 160
23 | 2 | GLYCOL HEATING PERFORMANCE | 11 | 2 | 140
23 | 2 | GLYCOL HEATING PERFORMANCE | 11 | 3 | 15
23 | 2 | GLYCOL HEATING PERFORMANCE | 11 | 4 | 109
23 | 2 | GLYCOL HEATING PERFORMANCE | 11 | 5 | 123
23 | 2 | GLYCOL HEATING PERFORMANCE | 11 | 6 | 14
23 | 2 | GLYCOL HEATING PERFORMANCE | 11 | 7 | 106
23 | 2 | GLYCOL HEATING PERFORMANCE | 11 | 8 | 156
23 | 2 | GLYCOL HEATING PERFORMANCE | 11 | 9 | 16
23 | 2 | GLYCOL HEATING PERFORMANCE | 11 | 10 | 107
23 | 2 | GLYCOL HEATING PERFORMANCE | 11 | 11 | 136
23 | 2 | GLYCOL HEATING PERFORMANCE | 11 | 12 | 16
23 | 2 | GLYCOL HEATING PERFORMANCE | 11 | 13 | 103
23 | 2 | GLYCOL HEATING PERFORMANCE | 11 | 14 | 180
23 | 2 | GLYCOL HEATING PERFORMANCE | 11 | 15 | 18
23 | 2 | GLYCOL HEATING PERFORMANCE | 11 | 16 | 103
23 | 2 | GLYCOL HEATING PERFORMANCE | 11 | 17 | 156
23 | 2 | GLYCOL HEATING PERFORMANCE | 11 | 18 | 19
23 | 3 | GLYCOL HEATING PERFORMANCE | 1 | 2 | 25
23 | 3 | GLYCOL HEATING PERFORMANCE | 2 | 1 | Ewt
23 | 3 | GLYCOL HEATING PERFORMANCE | 2 | 2 | Cap
23 | 3 | GLYCOL HEATING PERFORMANCE | 2 | 3 | Gpm
23 | 3 | GLYCOL HEATING PERFORMANCE | 2 | 4 | Ldb
23 | 3 | GLYCOL HEATING PERFORMANCE | 2 | 5 | Cap
23 | 3 | GLYCOL HEATING PERFORMANCE | 2 | 6 | Gpm
23 | 3 | GLYCOL HEATING PERFORMANCE | 3 | 1 | 200
23 | 3 | GLYCOL HEATING PERFORMANCE | 3 | 2 | 453
23 | 3 | GLYCOL HEATING PERFORMANCE | 3 | 3 | 48
23 | 3 | GLYCOL HEATING PERFORMANCE | 3 | 4 | 102
23 | 3 | GLYCOL HEATING PERFORMANCE | 3 | 5 | 425
23 | 3 | GLYCOL HEATING PERFORMANCE | 3 | 6 | 48
23 | 3 | GLYCOL HEATING PERFORMANCE | 4 | 1 | 180
23 | 3 | GLYCOL HEATING PERFORMANCE | 4 | 2 | 371
23 | 3 | GLYCOL HEATING PERFORMANCE | 4 | 3 | 39
23 | 3 | GLYCOL HEATING PERFORMANCE | 4 | 4 | 93
23 | 3 | GLYCOL HEATING PERFORMANCE | 4 | 5 | 342
23 | 3 | GLYCOL HEATING PERFORMANCE | 4 | 6 | 39
23 | 3 | GLYCOL HEATING PERFORMANCE | 5 | 1 | 160
23 | 3 | GLYCOL HEATING PERFORMANCE | 5 | 2 | 290
23 | 3 | GLYCOL HEATING PERFORMANCE | 5 | 3 | 31
23 | 3 | GLYCOL HEATING PERFORMANCE | 5 | 4 | 85
23 | 3 | GLYCOL HEATING PERFORMANCE | 5 | 5 | 260
23 | 3 | GLYCOL HEATING PERFORMANCE | 5 | 6 | 30
23 | 3 | GLYCOL HEATING PERFORMANCE | 6 | 1 | 200
23 | 3 | GLYCOL HEATING PERFORMANCE | 6 | 2 | 400
23 | 3 | GLYCOL HEATING PERFORMANCE | 6 | 3 | 42
23 | 3 | GLYCOL HEATING PERFORMANCE | 6 | 4 | 111
23 | 3 | GLYCOL HEATING PERFORMANCE | 6 | 5 | 372
23 | 3 | GLYCOL HEATING PERFORMANCE | 6 | 6 | 42
23 | 3 | GLYCOL HEATING PERFORMANCE | 7 | 1 | 180
23 | 3 | GLYCOL HEATING PERFORMANCE | 7 | 2 | 317
23 | 3 | GLYCOL HEATING PERFORMANCE | 7 | 3 | 34
23 | 3 | GLYCOL HEATING PERFORMANCE | 7 | 4 | 103
23 | 3 | GLYCOL HEATING PERFORMANCE | 7 | 5 | 287
23 | 3 | GLYCOL HEATING PERFORMANCE | 7 | 6 | 33
23 | 3 | GLYCOL HEATING PERFORMANCE | 8 | 1 | 160
23 | 3 | GLYCOL HEATING PERFORMANCE | 8 | 2 | 237
23 | 3 | GLYCOL HEATING PERFORMANCE | 8 | 3 | 25
23 | 3 | GLYCOL HEATING PERFORMANCE | 8 | 4 | 94
23 | 3 | GLYCOL HEATING PERFORMANCE | 8 | 5 | 208
23 | 3 | GLYCOL HEATING PERFORMANCE | 8 | 6 | 24
23 | 3 | GLYCOL HEATING PERFORMANCE | 9 | 1 | 200
23 | 3 | GLYCOL HEATING PERFORMANCE | 9 | 2 | 364
23 | 3 | GLYCOL HEATING PERFORMANCE | 9 | 3 | 39
23 | 3 | GLYCOL HEATING PERFORMANCE | 9 | 4 | 118
23 | 3 | GLYCOL HEATING PERFORMANCE | 9 | 5 | 337
23 | 3 | GLYCOL HEATING PERFORMANCE | 9 | 6 | 38
23 | 3 | GLYCOL HEATING PERFORMANCE | 10 | 1 | 180
23 | 3 | GLYCOL HEATING PERFORMANCE | 10 | 2 | 281
23 | 3 | GLYCOL HEATING PERFORMANCE | 10 | 3 | 30
23 | 3 | GLYCOL HEATING PERFORMANCE | 10 | 4 | 109
23 | 3 | GLYCOL HEATING PERFORMANCE | 10 | 5 | 254
23 | 3 | GLYCOL HEATING PERFORMANCE | 10 | 6 | 29
23 | 3 | GLYCOL HEATING PERFORMANCE | 11 | 1 | 160
23 | 3 | GLYCOL HEATING PERFORMANCE | 11 | 2 | 201
23 | 3 | GLYCOL HEATING PERFORMANCE | 11 | 3 | 21
23 | 3 | GLYCOL HEATING PERFORMANCE | 11 | 4 | 101
23 | 3 | GLYCOL HEATING PERFORMANCE | 11 | 5 | 173
23 | 3 | GLYCOL HEATING PERFORMANCE | 11 | 6 | 20
23 | 4 | GLYCOL HEATING PERFORMANCE | 1 | 1 | 4000
23 | 4 | GLYCOL HEATING PERFORMANCE | 1 | 3 | 5000
23 | 4 | GLYCOL HEATING PERFORMANCE | 1 | 5 | 6000
23 | 4 | GLYCOL HEATING PERFORMANCE | 1 | 7 | 8000
23 | 4 | GLYCOL HEATING PERFORMANCE | 2 | 1 | Gpm
23 | 4 | GLYCOL HEATING PERFORMANCE | 2 | 2 | ∆∆∆∆ P*
23 | 4 | GLYCOL HEATING PERFORMANCE | 2 | 3 | Gpm
23 | 4 | GLYCOL HEATING PERFORMANCE | 2 | 4 | ∆∆∆∆ P*
23 | 4 | GLYCOL HEATING PERFORMANCE | 2 | 5 | Gpm
23 | 4 | GLYCOL HEATING PERFORMANCE | 2 | 6 | ∆∆∆∆ P*
23 | 4 | GLYCOL HEATING PERFORMANCE | 2 | 7 | Gpm
23 | 4 | GLYCOL HEATING PERFORMANCE | 2 | 8 | ∆∆∆∆ P*
23 | 4 | GLYCOL HEATING PERFORMANCE | 2 | 9 | Gpm
23 | 4 | GLYCOL HEATING PERFORMANCE | 3 | 1 | 27
23 | 4 | GLYCOL HEATING PERFORMANCE | 3 | 2 | 1.2
23 | 4 | GLYCOL HEATING PERFORMANCE | 3 | 3 | 31
23 | 4 | GLYCOL HEATING PERFORMANCE | 3 | 4 | 1.5
23 | 4 | GLYCOL HEATING PERFORMANCE | 3 | 5 | 35
23 | 4 | GLYCOL HEATING PERFORMANCE | 3 | 6 | 1.8
23 | 4 | GLYCOL HEATING PERFORMANCE | 3 | 7 | 41
23 | 4 | GLYCOL HEATING PERFORMANCE | 3 | 8 | 2.4
23 | 4 | GLYCOL HEATING PERFORMANCE | 3 | 9 | 47
23 | 4 | GLYCOL HEATING PERFORMANCE | 4 | 1 | 22
23 | 4 | GLYCOL HEATING PERFORMANCE | 4 | 2 | 0.9
23 | 4 | GLYCOL HEATING PERFORMANCE | 4 | 3 | 25
23 | 4 | GLYCOL HEATING PERFORMANCE | 4 | 4 | 1.1
23 | 4 | GLYCOL HEATING PERFORMANCE | 4 | 5 | 27
23 | 4 | GLYCOL HEATING PERFORMANCE | 4 | 6 | 1.3
23 | 4 | GLYCOL HEATING PERFORMANCE | 4 | 7 | 32
23 | 4 | GLYCOL HEATING PERFORMANCE | 4 | 8 | 1.6
23 | 4 | GLYCOL HEATING PERFORMANCE | 4 | 9 | 36
23 | 4 | GLYCOL HEATING PERFORMANCE | 5 | 1 | 16
23 | 4 | GLYCOL HEATING PERFORMANCE | 5 | 2 | 0.6
23 | 4 | GLYCOL HEATING PERFORMANCE | 5 | 3 | 19
23 | 4 | GLYCOL HEATING PERFORMANCE | 5 | 4 | 0.7
23 | 4 | GLYCOL HEATING PERFORMANCE | 5 | 5 | 20
23 | 4 | GLYCOL HEATING PERFORMANCE | 5 | 6 | 0.8
23 | 4 | GLYCOL HEATING PERFORMANCE | 5 | 7 | 24
23 | 4 | GLYCOL HEATING PERFORMANCE | 5 | 8 | 1
23 | 4 | GLYCOL HEATING PERFORMANCE | 5 | 9 | 27
24 | 1 | Performance data (cont) | 1 | 1 | 50
24 | 1 | Performance data (cont) | 1 | 4 | 100
24 | 1 | Performance data (cont) | 1 | 7 | 149
24 | 1 | Performance data (cont) | 1 | 10 | 199
24 | 1 | Performance data (cont) | 1 | 13 | 249
24 | 1 | Performance data (cont) | 2 | 1 | r/s
24 | 1 | Performance data (cont) | 2 | 2 | BkW
24 | 1 | Performance data (cont) | 2 | 3 | kW
24 | 1 | Performance data (cont) | 2 | 4 | r/s
24 | 1 | Performance data (cont) | 2 | 5 | BkW
24 | 1 | Performance data (cont) | 2 | 6 | kW
24 | 1 | Performance data (cont) | 2 | 7 | r/s
24 | 1 | Performance data (cont) | 2 | 8 | BkW
24 | 1 | Performance data (cont) | 2 | 9 | kW
24 | 1 | Performance data (cont) | 2 | 10 | r/s
24 | 1 | Performance data (cont) | 2 | 11 | BkW
24 | 1 | Performance data (cont) | 2 | 12 | kW
24 | 1 | Performance data (cont) | 2 | 13 | r/s
24 | 1 | Performance data (cont) | 2 | 14 | BkW
24 | 1 | Performance data (cont) | 2 | 15 | kW
24 | 1 | Performance data (cont) | 2 | 16 | r/s
24 | 1 | Performance data (cont) | 2 | 17 | BkW
24 | 1 | Performance data (cont) | 3 | 1 | 11.4 11.9 12.4 13.0 13.5 14.1 14.6 15.2 15.8 16.3 16.9
24 | 1 | Performance data (cont) | 3 | 2 | 0.95 1.09 1.24 1.40 1.58 1.77 1.98 2.20 2.44 2.69 2.95
24 | 1 | Performance data (cont) | 3 | 3 | 1.10 1.26 1.44 1.64 1.84 2.07 2.31 2.57 2.84 3.13 3.44
24 | 1 | Performance data (cont) | 3 | 4 | 13.2 13.6 14.1 14.5 15.0 15.5 16.0 16.5 17.0 17.6 18.1
24 | 1 | Performance data (cont) | 3 | 5 | 1.10 1.24 1.40 1.57 1.75 1.95 2.16 2.39 2.62 2.88 3.15
24 | 1 | Performance data (cont) | 3 | 6 | 1.28 1.45 1.63 1.83 2.04 2.27 2.52 2.78 3.06 3.36 3.67
24 | 1 | Performance data (cont) | 3 | 7 | 14.8 15.2 15.6 16.0 16.4 16.9 17.3 17.8 18.3 18.8 —
24 | 1 | Performance data (cont) | 3 | 8 | 1.26 1.41 1.57 1.74 1.93 2.13 2.34 2.57 2.81 3.07 —
24 | 1 | Performance data (cont) | 3 | 9 | 1.47 1.64 1.83 2.03 2.25 2.48 2.73 2.99 3.28 3.58 —
24 | 1 | Performance data (cont) | 3 | 10 | 16.3 16.6 17.0 17.3 17.7 18.1 18.5 19.0 19.4 — —
24 | 1 | Performance data (cont) | 3 | 11 | 1.42 1.57 1.73 1.91 2.10 2.30 2.52 2.75 3.00 — —
24 | 1 | Performance data (cont) | 3 | 12 | 1.65 1.83 2.02 2.23 2.45 2.69 2.94 3.21 3.50 — —
24 | 1 | Performance data (cont) | 3 | 13 | 17.7 18.0 18.3 18.6 19.0 19.3 19.7 20.1 20.5 — —
24 | 1 | Performance data (cont) | 3 | 14 | 1.58 1.73 1.90 2.08 2.28 2.48 2.70 2.94 3.19 — —
24 | 1 | Performance data (cont) | 3 | 15 | 1.84 2.02 2.22 2.43 2.65 2.89 3.15 3.43 3.72 — —
24 | 1 | Performance data (cont) | 3 | 16 | 19.0 19.2 19.5 19.8 20.1 20.5 20.8 21.2 — — —
24 | 1 | Performance data (cont) | 3 | 17 | 1.75 1.90 2.07 2.26 2.45 2.66 2.89 3.13 — — —
24 | 2 | Performance data (cont) | 1 | 1 | 349
24 | 2 | Performance data (cont) | 1 | 4 | 399
24 | 2 | Performance data (cont) | 1 | 7 | 448
24 | 2 | Performance data (cont) | 1 | 10 | 473
24 | 2 | Performance data (cont) | 2 | 1 | r/s
24 | 2 | Performance data (cont) | 2 | 2 | BkW
24 | 2 | Performance data (cont) | 2 | 3 | kW
24 | 2 | Performance data (cont) | 2 | 4 | r/s
24 | 2 | Performance data (cont) | 2 | 5 | BkW
24 | 2 | Performance data (cont) | 2 | 6 | kW
24 | 2 | Performance data (cont) | 2 | 7 | r/s
24 | 2 | Performance data (cont) | 2 | 8 | BkW
24 | 2 | Performance data (cont) | 2 | 9 | kW
24 | 2 | Performance data (cont) | 2 | 10 | r/s
24 | 2 | Performance data (cont) | 2 | 11 | BkW
24 | 2 | Performance data (cont) | 2 | 12 | kW
24 | 2 | Performance data (cont) | 2 | 13 | r/s
24 | 2 | Performance data (cont) | 2 | 14 | BkW
24 | 2 | Performance data (cont) | 3 | 1 | 20.2 20.5 20.7 21.0 21.3 21.6 21.9 — — — —
24 | 2 | Performance data (cont) | 3 | 2 | 1.91 2.07 2.25 2.43 2.63 2.84 3.07 — — — —
24 | 2 | Performance data (cont) | 3 | 3 | 2.23 2.42 2.62 2.83 3.07 3.32 3.58 — — — —
24 | 2 | Performance data (cont) | 3 | 4 | 21.4 21.6 21.8 22.1 22.4 22.7 — — — — —
24 | 2 | Performance data (cont) | 3 | 5 | 2.08 2.25 2.42 2.61 2.81 3.03 — — — — —
24 | 2 | Performance data (cont) | 3 | 6 | 2.43 2.62 2.82 3.04 3.28 3.53 — — — — —
24 | 2 | Performance data (cont) | 3 | 7 | 22.6 22.7 22.9 23.2 23.4 23.7 — — — — —
24 | 2 | Performance data (cont) | 3 | 8 | 2.26 2.42 2.60 2.79 3.00 3.21 — — — — —
24 | 2 | Performance data (cont) | 3 | 9 | 2.63 2.82 3.03 3.25 3.49 3.75 — — — — —
24 | 2 | Performance data (cont) | 3 | 10 | 23.1 23.3 23.5 23.7 23.9 — — — — — —
24 | 2 | Performance data (cont) | 3 | 11 | 2.35 2.51 2.69 2.88 3.09 — — — — — —
24 | 2 | Performance data (cont) | 3 | 12 | 2.74 2.93 3.14 3.36 3.60 — — — — — —
24 | 2 | Performance data (cont) | 3 | 13 | 23.6 23.8 24.0 24.2 24.4 — — — — — —
24 | 2 | Performance data (cont) | 3 | 14 | 2.44 2.60 2.78 2.97 3.18 — — — — — —
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 1 | 1 | 50
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 1 | 4 | 100
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 1 | 7 | 149
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 1 | 10 | 199
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 1 | 13 | 249
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 1 | 16 | 299
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 1 | 19 | 349
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 1 | r/s
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 2 | BkW
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 3 | kW
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 4 | r/s
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 5 | BkW
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 6 | kW
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 7 | r/s
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 8 | BkW
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 9 | kW
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 10 | r/s
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 11 | BkW
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 12 | kW
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 13 | r/s
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 14 | BkW
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 15 | kW
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 16 | r/s
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 17 | BkW
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 18 | kW
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 19 | r/s
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 20 | BkW
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 21 | kW
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 22 | r/s
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 23 | BkW
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 1 | 11.4 12.2 13.0 13.8 14.6 15.5 16.3 17.2 18.0 18.9
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 2 | 1.49 1.76 2.09 2.45 2.84 3.27 3.74 4.24 4.78 5.36
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 3 | 1.68 2.01 2.37 2.78 3.23 3.72 4.24 4.82 5.43 6.09
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 4 | 12.7 13.4 14.1 14.9 15.6 16.4 17.2 18.0 18.8 19.7
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 5 | 1.71 1.99 2.31 2.68 3.07 3.51 3.98 4.49 5.03 5.62
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 6 | 1.92 2.26 2.63 3.04 3.49 3.99 4.52 5.10 5.72 6.38
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 7 | 13.9 14.5 15.2 15.9 16.6 17.3 18.1 18.9 19.6 20.4
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 8 | 1.94 2.21 2.55 2.91 3.31 3.75 4.22 4.74 5.29 5.87
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 9 | 2.18 2.52 2.89 3.31 3.77 4.26 4.80 5.38 6.01 6.68
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 10 | 15.0 15.6 16.2 16.8 17.5 18.2 18.9 19.7 20.4 21.2
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 11 | 2.17 2.45 2.78 3.15 3.56 4.00 4.48 4.99 5.54 6.13
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 12 | 2.44 2.78 3.16 3.58 4.04 4.54 5.09 5.67 6.30 6.97
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 13 | 16.1 16.6 17.2 17.8 18.4 19.1 19.7 20.4 21.2 21.9
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 14 | 2.41 2.69 3.03 3.40 3.81 4.25 4.73 5.25 5.80 6.40
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 15 | 2.71 3.06 3.44 3.86 4.33 4.83 5.38 5.96 6.60 7.27
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 16 | 17.1 17.6 18.1 18.7 19.3 19.9 20.5 21.2 21.9 22.6
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 17 | 2.66 2.94 3.28 3.65 4.06 4.51 4.99 5.51 6.07 6.67
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 18 | 2.99 3.34 3.72 4.15 4.61 5.12 5.67 6.26 6.90 7.57
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 19 | 18.1 18.5 19.0 19.6 20.1 20.7 21.3 21.9 22.6 23.3
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 20 | 2.91 3.19 3.53 3.91 4.32 4.77 5.25 5.77 6.33 6.93
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 21 | 3.28 3.62 4.01 4.44 4.91 5.41 5.97 6.56 7.20 7.88
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 22 | 19.0 19.4 19.9 20.4 20.9 21.5 22.1 22.7 23.3 24.0
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 23 | 3.17 3.45 3.79 4.16 4.58 5.03 5.52 6.04 6.60 7.21
25 | 2 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 1 | 1 | 448
25 | 2 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 1 | 4 | 473
25 | 2 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 1 | r/s
25 | 2 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 2 | BkW
25 | 2 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 3 | kW
25 | 2 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 4 | r/s
25 | 2 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 5 | BkW
25 | 2 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 6 | kW
25 | 2 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 7 | r/s
25 | 2 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 8 | BkW
25 | 2 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 1 | 20.0 20.3 20.7 21.2 21.7 22.2 22.8 23.4 24.0 24.6
25 | 2 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 2 | 3.43 3.71 4.05 4.43 4.84 5.30 5.78 6.31 6.88 7.48
25 | 2 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 3 | 3.86 4.21 4.60 5.03 5.50 6.02 6.57 7.17 7.82 8.50
25 | 2 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 4 | 20.4 20.8 21.2 21.6 22.1 22.6 23.2 23.7 24.3 —
25 | 2 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 5 | 3.57 3.84 4.18 4.56 4.98 5.43 5.92 6.45 7.02 —
25 | 2 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 6 | 4.02 4.36 4.75 5.18 5.66 6.17 6.73 7.33 7.97 —
25 | 2 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 7 | 20.8 21.2 21.6 22.0 22.5 23.0 23.5 24.1 24.7 —
25 | 2 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 8 | 3.71 3.97 4.32 4.70 5.11 5.57 6.06 6.59 7.15 —
26 | 1 | Performance data (cont) | 1 | 1 | 50
26 | 1 | Performance data (cont) | 1 | 4 | 100
26 | 1 | Performance data (cont) | 1 | 7 | 149
26 | 1 | Performance data (cont) | 1 | 10 | 199
26 | 1 | Performance data (cont) | 1 | 13 | 249
26 | 1 | Performance data (cont) | 1 | 16 | 299
26 | 1 | Performance data (cont) | 2 | 1 | r/s
26 | 1 | Performance data (cont) | 2 | 2 | BkW
26 | 1 | Performance data (cont) | 2 | 3 | kW
26 | 1 | Performance data (cont) | 2 | 4 | r/s
26 | 1 | Performance data (cont) | 2 | 5 | BkW
26 | 1 | Performance data (cont) | 2 | 6 | kW
26 | 1 | Performance data (cont) | 2 | 7 | r/s
26 | 1 | Performance data (cont) | 2 | 8 | BkW
26 | 1 | Performance data (cont) | 2 | 9 | kW
26 | 1 | Performance data (cont) | 2 | 10 | r/s
26 | 1 | Performance data (cont) | 2 | 11 | BkW
26 | 1 | Performance data (cont) | 2 | 12 | kW
26 | 1 | Performance data (cont) | 2 | 13 | r/s
26 | 1 | Performance data (cont) | 2 | 14 | BkW
26 | 1 | Performance data (cont) | 2 | 15 | kW
26 | 1 | Performance data (cont) | 2 | 16 | r/s
26 | 1 | Performance data (cont) | 2 | 17 | BkW
26 | 1 | Performance data (cont) | 2 | 18 | kW
26 | 1 | Performance data (cont) | 2 | 19 | r/s
26 | 1 | Performance data (cont) | 2 | 20 | BkW
26 | 1 | Performance data (cont) | 3 | 1 | 14.1 14.9 15.8 16.7 17.6 18.4 19.3 20.2 21.1 21.5
26 | 1 | Performance data (cont) | 3 | 2 | 2.41 2.82 3.28 3.78 4.33 4.92 5.56 6.25 6.99 7.38
26 | 1 | Performance data (cont) | 3 | 3 | 2009 2355 2735 3153 3608 4102 4635 5210 5826 6151
26 | 1 | Performance data (cont) | 3 | 4 | 15.1 15.9 16.7 17.6 18.4 19.2 20.1 20.9 21.8 22.2
26 | 1 | Performance data (cont) | 3 | 5 | 2.67 3.09 3.55 4.06 4.61 5.21 5.86 6.56 7.30 7.69
26 | 1 | Performance data (cont) | 3 | 6 | 2222 2574 2961 3384 3845 4345 4884 5464 6086 6413
26 | 1 | Performance data (cont) | 3 | 7 | 16.2 16.9 17.7 18.4 19.2 20.0 20.8 21.7 22.5 22.9
26 | 1 | Performance data (cont) | 3 | 8 | 2.93 3.36 3.83 4.34 4.90 5.51 6.16 6.87 7.62 8.01
26 | 1 | Performance data (cont) | 3 | 9 | 2441 2799 3191 3620 4087 4592 5137 5722 6349 6679
26 | 1 | Performance data (cont) | 3 | 10 | 17.1 17.8 18.5 19.3 20.0 20.8 21.6 22.4 23.2 23.6
26 | 1 | Performance data (cont) | 3 | 11 | 3.20 3.63 4.11 4.63 5.20 5.81 6.47 7.18 7.94 8.34
26 | 1 | Performance data (cont) | 3 | 12 | 2666 3029 3427 3861 4332 4843 5393 5983 6616 6948
26 | 1 | Performance data (cont) | 3 | 13 | 18.1 18.7 19.4 20.1 20.8 21.5 22.3 23.1 23.8 24.2
26 | 1 | Performance data (cont) | 3 | 14 | 3.48 3.92 4.40 4.93 5.50 6.12 6.78 7.50 8.26 8.66
26 | 1 | Performance data (cont) | 3 | 15 | 2897 3264 3667 4106 4582 5097 5652 6248 6885 7219
26 | 1 | Performance data (cont) | 3 | 16 | 19.0 19.6 20.2 20.9 21.6 22.3 23.0 23.7 24.5 24.9
26 | 1 | Performance data (cont) | 3 | 17 | 3.76 4.20 4.69 5.22 5.80 6.43 7.10 7.82 8.59 8.99
26 | 1 | Performance data (cont) | 3 | 18 | 3133 3504 3911 4355 4836 5356 5915 6515 7157 7494
26 | 1 | Performance data (cont) | 3 | 19 | 19.8 20.4 21.0 21.6 22.3 23.0 23.7 24.4 25.1 25.5
26 | 1 | Performance data (cont) | 3 | 20 | 4.05 4.50 4.99 5.53 6.11 6.74 7.42 8.14 8.92 9.32
26 | 2 | Performance data (cont) | 1 | 1 | 399
26 | 2 | Performance data (cont) | 2 | 1 | r/s
26 | 2 | Performance data (cont) | 2 | 2 | BkW
26 | 2 | Performance data (cont) | 2 | 3 | kW
26 | 2 | Performance data (cont) | 2 | 4 | r/s
26 | 2 | Performance data (cont) | 2 | 5 | BkW
26 | 2 | Performance data (cont) | 3 | 1 | 20.7 21.2 21.8 22.4 23.0 23.7 24.4 25.1 25.8 —
26 | 2 | Performance data (cont) | 3 | 2 | 4.34 4.80 5.30 5.84 6.42 7.06 7.74 8.47 9.25 —
26 | 2 | Performance data (cont) | 3 | 3 | 3621 4000 4414 4866 5355 5883 6451 7060 7710 —
26 | 2 | Performance data (cont) | 3 | 4 | 21.5 22.0 22.5 23.1 23.7 24.4 25.0 25.7 — —
26 | 2 | Performance data (cont) | 3 | 5 | 3.63 4.11 4.63 5.20 5.81 6.47 7.18 7.94 — —
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 1 | 1 | 0.2
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 1 | 4 | 0.4
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 1 | 7 | 0.6
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 1 | 10 | 0.8
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 1 | 13 | 1
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 1 | Rpm
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 2 | Bhp
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 3 | Watts
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 4 | Rpm
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 5 | Bhp
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 6 | Watts
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 7 | Rpm
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 8 | Bhp
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 9 | Watts
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 10 | Rpm
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 11 | Bhp
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 12 | Watts
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 13 | Rpm
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 14 | Bhp
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 15 | Watts
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 16 | Rpm
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 17 | Bhp
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 1 | 684 715 747 779 812 845 878 912 946 981 1016
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 2 | 1.28 1.47 1.67 1.90 2.14 2.40 2.68 2.98 3.29 3.63 3.99
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 3 | 1102 1265 1442 1635 1844 2068 2309 2566 2841 3133 3443
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 4 | 791 817 844 872 901 931 961 992 1023 1055 1087
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 5 | 1.49 1.68 1.89 2.12 2.37 2.64 2.92 3.22 3.55 3.89 4.25
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 6 | 1283 1451 1633 1831 2044 2273 2518 2780 3059 3355 3669
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 7 | 887 910 934 959 985 1011 1039 1067 1096 1125 —
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 8 | 1.70 1.90 2.12 2.35 2.60 2.87 3.16 3.47 3.80 4.15 —
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 9 | 1466 1638 1825 2027 2245 2478 2728 2994 3277 3578 —
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 10 | 977 997 1018 1040 1063 1087 1112 1138 1165 — —
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 11 | 1.92 2.12 2.34 2.58 2.84 3.11 3.41 3.72 4.05 — —
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 12 | 1652 1828 2019 2226 2448 2685 2939 3209 3496 — —
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 13 | 1061 1078 1097 1117 1138 1160 1183 1207 1232 — —
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 14 | 2.13 2.34 2.57 2.81 3.07 3.35 3.65 3.97 4.31 — —
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 15 | 1841 2021 2216 2426 2652 2893 3151 3425 3716 — —
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 16 | 1139 1155 1171 1189 1209 1229 1250 1273 — — —
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 17 | 2.36 2.57 2.80 3.05 3.31 3.60 3.90 4.22 — — —
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 1 | 1 | 1.4
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 1 | 4 | 1.6
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 1 | 7 | 1.8
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 1 | 10 | 1.9
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 1 | Rpm
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 2 | Bhp
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 3 | Watts
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 4 | Rpm
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 5 | Bhp
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 6 | Watts
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 7 | Rpm
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 8 | Bhp
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 9 | Watts
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 10 | Rpm
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 11 | Bhp
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 12 | Watts
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 13 | Rpm
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 14 | Bhp
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 1 | 1214 1228 1243 1259 1277 1295 1315 — — — —
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 2 | 2.59 2.80 3.04 3.29 3.56 3.84 4.15 — — — —
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 3 | 2230 2417 2618 2835 3067 3316 3580 — — — —
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 4 | 1285 1297 1311 1326 1342 1359 — — — — —
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 5 | 2.82 3.04 3.27 3.53 3.80 4.09 — — — — —
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 6 | 2430 2619 2823 3043 3278 3530 — — — — —
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 7 | 1353 1364 1376 1390 1405 1421 — — — — —
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 8 | 3.05 3.27 3.51 3.77 4.05 4.34 — — — — —
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 9 | 2633 2825 3031 3254 3492 3746 — — — — —
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 10 | 1386 1396 1408 1421 1435 — — — — — —
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 11 | 3.17 3.40 3.64 3.90 4.17 — — — — — —
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 12 | 2736 2928 3136 3360 3600 — — — — — —
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 13 | 1418 1428 1439 1452 1466 — — — — — —
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 14 | 3.29 3.52 3.76 4.02 4.30 — — — — — —
28 | 1 | Performance data (cont) | 1 | 1 | 0.2
28 | 1 | Performance data (cont) | 1 | 4 | 0.4
28 | 1 | Performance data (cont) | 1 | 7 | 0.6
28 | 1 | Performance data (cont) | 1 | 10 | 0.8
28 | 1 | Performance data (cont) | 1 | 13 | 1
28 | 1 | Performance data (cont) | 1 | 16 | 1.2
28 | 1 | Performance data (cont) | 2 | 1 | Rpm
28 | 1 | Performance data (cont) | 2 | 2 | Bhp
28 | 1 | Performance data (cont) | 2 | 3 | Watts
28 | 1 | Performance data (cont) | 2 | 4 | Rpm
28 | 1 | Performance data (cont) | 2 | 5 | Bhp
28 | 1 | Performance data (cont) | 2 | 6 | Watts
28 | 1 | Performance data (cont) | 2 | 7 | Rpm
28 | 1 | Performance data (cont) | 2 | 8 | Bhp
28 | 1 | Performance data (cont) | 2 | 9 | Watts
28 | 1 | Performance data (cont) | 2 | 10 | Rpm
28 | 1 | Performance data (cont) | 2 | 11 | Bhp
28 | 1 | Performance data (cont) | 2 | 12 | Watts
28 | 1 | Performance data (cont) | 2 | 13 | Rpm
28 | 1 | Performance data (cont) | 2 | 14 | Bhp
28 | 1 | Performance data (cont) | 2 | 15 | Watts
28 | 1 | Performance data (cont) | 2 | 16 | Rpm
28 | 1 | Performance data (cont) | 2 | 17 | Bhp
28 | 1 | Performance data (cont) | 2 | 18 | Watts
28 | 1 | Performance data (cont) | 2 | 19 | Rpm
28 | 1 | Performance data (cont) | 2 | 20 | Bhp
28 | 1 | Performance data (cont) | 3 | 1 | 682 730 778 828 878 928 979 1030 1082 1134
28 | 1 | Performance data (cont) | 3 | 2 | 1.99 2.38 2.82 3.31 3.84 4.42 5.05 5.73 6.46 7.25
28 | 1 | Performance data (cont) | 3 | 3 | 1675 2005 2373 2780 3227 3715 4245 4817 5433 6093
28 | 1 | Performance data (cont) | 3 | 4 | 760 802 846 892 938 985 1033 1082 1131 1180
28 | 1 | Performance data (cont) | 3 | 5 | 2.29 2.68 3.13 3.62 4.15 4.74 5.38 6.06 6.80 7.59
28 | 1 | Performance data (cont) | 3 | 6 | 1922 2257 2630 3042 3494 3986 4521 5098 5718 6382
28 | 1 | Performance data (cont) | 3 | 7 | 832 871 911 953 996 1040 1085 1131 1178 1226
28 | 1 | Performance data (cont) | 3 | 8 | 2.59 2.99 3.44 3.94 4.48 5.07 5.71 6.40 7.14 7.94
28 | 1 | Performance data (cont) | 3 | 9 | 2177 2516 2893 3310 3766 4263 4801 5382 6007 6675
28 | 1 | Performance data (cont) | 3 | 10 | 901 935 972 1011 1051 1093 1136 1180 1225 1270
28 | 1 | Performance data (cont) | 3 | 11 | 2.90 3.31 3.76 4.26 4.81 5.40 6.05 6.74 7.49 8.29
28 | 1 | Performance data (cont) | 3 | 12 | 2441 2783 3164 3583 4043 4544 5086 5671 6299 6971
28 | 1 | Performance data (cont) | 3 | 13 | 965 997 1031 1067 1105 1144 1185 1227 1270 1313
28 | 1 | Performance data (cont) | 3 | 14 | 3.22 3.63 4.09 4.59 5.14 5.74 6.39 7.09 7.84 8.65
28 | 1 | Performance data (cont) | 3 | 15 | 2712 3057 3440 3863 4326 4830 5375 5964 6595 7271
28 | 1 | Performance data (cont) | 3 | 16 | 1027 1056 1087 1121 1156 1194 1232 1272 1313 1356
28 | 1 | Performance data (cont) | 3 | 17 | 3.56 3.97 4.43 4.93 5.49 6.09 6.74 7.44 8.20 9.01
28 | 1 | Performance data (cont) | 3 | 18 | 2990 3337 3722 4148 4613 5120 5669 6260 6895 7574
28 | 1 | Performance data (cont) | 3 | 19 | 1086 1112 1142 1173 1207 1242 1279 1317 1356 1397
28 | 1 | Performance data (cont) | 3 | 20 | 3.89 4.31 4.77 5.28 5.83 6.44 7.10 7.80 8.56 9.37
28 | 2 | Performance data (cont) | 1 | 1 | 1.6
28 | 2 | Performance data (cont) | 1 | 4 | 1.8
28 | 2 | Performance data (cont) | 1 | 7 | 1.9
28 | 2 | Performance data (cont) | 2 | 1 | Rpm
28 | 2 | Performance data (cont) | 2 | 2 | Bhp
28 | 2 | Performance data (cont) | 2 | 3 | Watts
28 | 2 | Performance data (cont) | 2 | 4 | Rpm
28 | 2 | Performance data (cont) | 2 | 5 | Bhp
28 | 2 | Performance data (cont) | 2 | 6 | Watts
28 | 2 | Performance data (cont) | 2 | 7 | Rpm
28 | 2 | Performance data (cont) | 2 | 8 | Bhp
28 | 2 | Performance data (cont) | 2 | 9 | Watts
28 | 2 | Performance data (cont) | 2 | 10 | Rpm
28 | 2 | Performance data (cont) | 2 | 11 | Bhp
28 | 2 | Performance data (cont) | 3 | 1 | 1142 1167 1194 1224 1255 1289 1324 1360 1398 1438
28 | 2 | Performance data (cont) | 3 | 2 | 4.24 4.66 5.12 5.63 6.19 6.80 7.45 8.16 8.93 9.74
28 | 2 | Performance data (cont) | 3 | 3 | 3567 3915 4304 4733 5203 5714 6268 6865 7505 8190
28 | 2 | Performance data (cont) | 3 | 4 | 1197 1219 1245 1273 1302 1334 1368 1403 1440 1477
28 | 2 | Performance data (cont) | 3 | 5 | 4.59 5.01 5.47 5.98 6.55 7.16 7.82 8.53 9.29 10.11
28 | 2 | Performance data (cont) | 3 | 6 | 3864 4213 4602 5033 5504 6018 6573 7173 7815 8503
28 | 2 | Performance data (cont) | 3 | 7 | 1223 1245 1270 1296 1326 1357 1389 1424 1460 —
28 | 2 | Performance data (cont) | 3 | 8 | 4.77 5.19 5.65 6.17 6.73 7.34 8.00 8.71 9.48 —
28 | 2 | Performance data (cont) | 3 | 9 | 4015 4364 4754 5184 5657 6171 6728 7328 7972 —
28 | 2 | Performance data (cont) | 3 | 10 | 1249 1270 1294 1320 1348 1379 1411 1445 1480 —
28 | 2 | Performance data (cont) | 3 | 11 | 4.96 5.37 5.83 6.35 6.91 7.52 8.18 8.90 9.67 —
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 1 | 1 | 0.2
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 1 | 4 | 0.4
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 1 | 7 | 0.6
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 1 | 10 | 0.8
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 1 | 13 | 1
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 1 | 16 | 1.2
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 1 | Rpm
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 2 | Bhp
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 3 | Watts
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 4 | Rpm
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 5 | Bhp
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 6 | Watts
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 7 | Rpm
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 8 | Bhp
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 9 | Watts
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 10 | Rpm
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 11 | Bhp
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 12 | Watts
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 13 | Rpm
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 14 | Bhp
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 15 | Watts
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 16 | Rpm
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 17 | Bhp
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 18 | Watts
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 19 | Rpm
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 20 | Bhp
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 1 | 845 896 948 1001 1053 1106 1159 1213 1266 1293
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 2 | 3.26 3.82 4.43 5.11 5.85 6.65 7.52 8.45 9.45 9.97
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 3 | 2693 3156 3667 4226 4836 5498 6214 6984 7810 8245
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 4 | 909 956 1005 1054 1104 1155 1206 1257 1309 1334
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 5 | 3.60 4.17 4.80 5.49 6.23 7.04 7.92 8.86 9.87 10.40
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 6 | 2979 3450 3969 4537 5155 5824 6547 7325 8159 8597
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 7 | 969 1014 1060 1106 1154 1202 1251 1300 1350 1375
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 8 | 3.96 4.54 5.17 5.87 6.63 7.44 8.33 9.28 10.29 10.83
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 9 | 3272 3752 4278 4853 5478 6155 6886 7671 8511 8953
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 10 | 1028 1069 1112 1156 1202 1248 1295 1342 1391 1415
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 11 | 4.32 4.91 5.56 6.26 7.02 7.85 8.74 9.70 10.73 11.26
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 12 | 3574 4060 4593 5175 5808 6492 7229 8020 8868 9313
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 13 | 1083 1123 1163 1205 1248 1293 1338 1384 1431 1454
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 14 | 4.70 5.29 5.94 6.66 7.43 8.26 9.16 10.13 11.16 11.70
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 15 | 3883 4375 4915 5504 6142 6833 7577 8375 9229 9677
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 16 | 1137 1174 1213 1253 1294 1336 1380 1424 1470 1493
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 17 | 5.08 5.68 6.34 7.06 7.84 8.68 9.59 10.56 11.60 12.15
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 18 | 4,200 4,698 5,243 5,838 6,483 7,179 7,929 8,733 9,594 10,045
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 19 | 1189 1224 1261 1299 1338 1379 1421 1464 1508 1530
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 20 | 5.47 6.08 6.75 7.47 8.26 9.11 10.02 11.00 12.05 12.60
29 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 1 | 1 | 1.6
29 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 1 | Rpm
29 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 2 | Bhp
29 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 3 | Watts
29 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 4 | Rpm
29 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 5 | Bhp
29 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 1 | 1239 1272 1307 1344 1382 1421 1461 1503 1546 —
29 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 2 | 5.87 6.48 7.16 7.89 8.68 9.54 10.46 11.45 12.50 —
29 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 3 | 4,854 5,362 5,917 6,523 7,179 7,887 8,648 9,464 10,336 —
29 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 4 | 1288 1320 1353 1388 1424 1462 1501 1541 — —
29 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 5 | 4.91 5.56 6.26 7.02 7.85 8.74 9.70 10.73 — —
30 | 1 | Performance data (cont) | 1 | 1 | FAN PERFORMANCE USING ACCESSORY POWER EXHAUST
30 | 1 | Performance data (cont) | 3 | 1 | HORIZONTAL SUPPLY/RETURN FAN PERFORMANCE WITH CRRFCURB013A00 HIGH-STATIC REGAIN ADAPTER NOTE: The CRRFCURB013A00 high-static regain adapter accessory may be used to provide horizontal supply/return. NOTE: The CRRFCURB013A00 horizontal supply and return adapter accessory improves 50TJ fan performance by increasing external static pressure by amount shown above.
31 | 1 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 1 | 1 | 2125
31 | 1 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 1 | 2 | 2360
31 | 1 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 1 | 3 | 2831
31 | 1 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 1 | 4 | 3400
31 | 1 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 2 | 1 | 10
31 | 1 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 2 | 2 | 12
31 | 1 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 2 | 3 | 17
31 | 1 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 2 | 4 | 22
31 | 1 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 3 | 1 | 55
31 | 1 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 3 | 2 | 65
31 | 1 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 3 | 3 | 87
31 | 1 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 3 | 4 | 109
31 | 1 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 5 | 1 | 15 19 25
31 | 1 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 5 | 2 | 17 22 27
31 | 1 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 5 | 3 | 22 27 35
31 | 1 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 5 | 4 | 27 35 46
31 | 2 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 1 | 1 | 4500
31 | 2 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 1 | 2 | 5000
31 | 2 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 1 | 3 | 6000
31 | 2 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 1 | 4 | 7200
31 | 2 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 2 | 1 | 0.04
31 | 2 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 2 | 2 | 0.05
31 | 2 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 2 | 3 | 0.07
31 | 2 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 2 | 4 | 0.09
31 | 2 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 3 | 1 | 0.22
31 | 2 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 3 | 2 | 0.26
31 | 2 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 3 | 3 | 0.35
31 | 2 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 3 | 4 | 0.44
31 | 2 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 5 | 1 | 0.06 0.08 0.10
31 | 2 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 5 | 2 | 0.07 0.09 0.11
31 | 2 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 5 | 3 | 0.09 0.11 0.14
31 | 2 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 5 | 4 | 0.11 0.14 0.18
31 | 3 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 1 | 1 | 2800
31 | 3 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 1 | 2 | 3400
31 | 3 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 1 | 3 | 4247
31 | 3 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 1 | 4 | 4719
31 | 3 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 2 | 1 | 17
31 | 3 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 2 | 2 | 22
31 | 3 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 2 | 3 | 27
31 | 3 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 2 | 4 | 30
31 | 3 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 3 | 1 | 86
31 | 3 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 3 | 2 | 109
31 | 3 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 3 | 3 | 144
31 | 3 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 3 | 4 | 164
31 | 3 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 5 | 1 | 22 28 36
31 | 3 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 5 | 2 | 27 35 46
31 | 3 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 5 | 3 | 37 45 57
31 | 3 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 5 | 4 | 43 53 65
31 | 4 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 1 | 1 | 6000
31 | 4 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 1 | 2 | 7200
31 | 4 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 1 | 3 | 9000
31 | 4 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 1 | 4 | 10000
31 | 4 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 2 | 1 | 0.07
31 | 4 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 2 | 2 | 0.09
31 | 4 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 2 | 3 | 0.11
31 | 4 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 2 | 4 | 0.12
31 | 4 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 3 | 1 | 0.35
31 | 4 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 3 | 2 | 0.44
31 | 4 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 3 | 3 | 0.58
31 | 4 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 3 | 4 | 0.66
31 | 4 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 5 | 1 | 0.09 0.11 0.14
31 | 4 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 5 | 2 | 0.11 0.14 0.18
31 | 4 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 5 | 3 | 0.15 0.18 0.23
31 | 4 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 5 | 4 | 0.17 0.21 0.26
32 | 1 | Performance data (cont) | 1 | 1 | 0
32 | 1 | Performance data (cont) | 1 | 2 | 1/2
32 | 1 | Performance data (cont) | 1 | 3 | 1
32 | 1 | Performance data (cont) | 1 | 4 | 11/2
32 | 1 | Performance data (cont) | 1 | 5 | 2
32 | 1 | Performance data (cont) | 1 | 6 | 21/2
32 | 1 | Performance data (cont) | 1 | 7 | 3
32 | 1 | Performance data (cont) | 1 | 8 | 31/2
32 | 1 | Performance data (cont) | 1 | 9 | 4
32 | 1 | Performance data (cont) | 1 | 10 | 41/2
32 | 1 | Performance data (cont) | 1 | 11 | 5
32 | 1 | Performance data (cont) | 1 | 12 | 51/2
32 | 1 | Performance data (cont) | 2 | 1 | 16.38
32 | 1 | Performance data (cont) | 2 | 2 | 15.99
32 | 1 | Performance data (cont) | 2 | 3 | 15.58
32 | 1 | Performance data (cont) | 2 | 4 | 15.19
32 | 1 | Performance data (cont) | 2 | 5 | 14.78
32 | 1 | Performance data (cont) | 2 | 6 | 14.38
32 | 1 | Performance data (cont) | 2 | 7 | 13.98
32 | 1 | Performance data (cont) | 2 | 8 | 13.58
32 | 1 | Performance data (cont) | 2 | 9 | 13.18
32 | 1 | Performance data (cont) | 2 | 10 | 12.78
32 | 1 | Performance data (cont) | 2 | 11 | 12.38
32 | 1 | Performance data (cont) | 2 | 12 | †
32 | 1 | Performance data (cont) | 3 | 1 | 21.67
32 | 1 | Performance data (cont) | 3 | 2 | 21.2
32 | 1 | Performance data (cont) | 3 | 3 | 20.75
32 | 1 | Performance data (cont) | 3 | 4 | 20.28
32 | 1 | Performance data (cont) | 3 | 5 | 19.82
32 | 1 | Performance data (cont) | 3 | 6 | 19.37
32 | 1 | Performance data (cont) | 3 | 7 | 18.9
32 | 1 | Performance data (cont) | 3 | 8 | 18.43
32 | 1 | Performance data (cont) | 3 | 9 | 17.97
32 | 1 | Performance data (cont) | 3 | 10 | 17.52
32 | 1 | Performance data (cont) | 3 | 11 | 17.05
32 | 1 | Performance data (cont) | 3 | 12 | †
32 | 1 | Performance data (cont) | 4 | 1 | 15.15
32 | 1 | Performance data (cont) | 4 | 2 | 14.92
32 | 1 | Performance data (cont) | 4 | 3 | 14.68
32 | 1 | Performance data (cont) | 4 | 4 | 14.45
32 | 1 | Performance data (cont) | 4 | 5 | 14.22
32 | 1 | Performance data (cont) | 4 | 6 | 13.98
32 | 1 | Performance data (cont) | 4 | 7 | 13.75
32 | 1 | Performance data (cont) | 4 | 8 | 13.52
32 | 1 | Performance data (cont) | 4 | 9 | 13.28
32 | 1 | Performance data (cont) | 4 | 10 | 13.05
32 | 1 | Performance data (cont) | 4 | 11 | 12.82
32 | 1 | Performance data (cont) | 4 | 12 | †
32 | 1 | Performance data (cont) | 5 | 1 | 20.27
32 | 1 | Performance data (cont) | 5 | 2 | 19.97
32 | 1 | Performance data (cont) | 5 | 3 | 19.66
32 | 1 | Performance data (cont) | 5 | 4 | 19.35
32 | 1 | Performance data (cont) | 5 | 5 | 19.03
32 | 1 | Performance data (cont) | 5 | 6 | 18.73
32 | 1 | Performance data (cont) | 5 | 7 | 18.42
32 | 1 | Performance data (cont) | 5 | 8 | 18.12
32 | 1 | Performance data (cont) | 5 | 9 | 17.8
32 | 1 | Performance data (cont) | 5 | 10 | 17.5
32 | 1 | Performance data (cont) | 5 | 11 | 17.19
32 | 1 | Performance data (cont) | 5 | 12 | 16.88
32 | 1 | Performance data (cont) | 6 | 1 | 17.82
32 | 1 | Performance data (cont) | 6 | 2 | 17.52
32 | 1 | Performance data (cont) | 6 | 3 | 17.21
32 | 1 | Performance data (cont) | 6 | 4 | 16.91
32 | 1 | Performance data (cont) | 6 | 5 | 16.61
32 | 1 | Performance data (cont) | 6 | 6 | 16.31
32 | 1 | Performance data (cont) | 6 | 7 | 16.01
32 | 1 | Performance data (cont) | 6 | 8 | 15.71
32 | 1 | Performance data (cont) | 6 | 9 | 15.4
32 | 1 | Performance data (cont) | 6 | 10 | 15.1
32 | 1 | Performance data (cont) | 6 | 11 | 14.8
32 | 1 | Performance data (cont) | 6 | 12 | †
32 | 1 | Performance data (cont) | 7 | 1 | 22.35
32 | 1 | Performance data (cont) | 7 | 2 | 21.97
32 | 1 | Performance data (cont) | 7 | 3 | 21.59
32 | 1 | Performance data (cont) | 7 | 4 | 21.22
32 | 1 | Performance data (cont) | 7 | 5 | 20.84
32 | 1 | Performance data (cont) | 7 | 6 | 20.46
32 | 1 | Performance data (cont) | 7 | 7 | 20.08
32 | 1 | Performance data (cont) | 7 | 8 | 19.7
32 | 1 | Performance data (cont) | 7 | 9 | 19.32
32 | 1 | Performance data (cont) | 7 | 10 | 18.95
32 | 1 | Performance data (cont) | 7 | 11 | 18.57
32 | 1 | Performance data (cont) | 7 | 12 | †
32 | 2 | Performance data (cont) | 1 | 1 | 0
32 | 2 | Performance data (cont) | 1 | 2 | 1/2
32 | 2 | Performance data (cont) | 1 | 3 | 1
32 | 2 | Performance data (cont) | 1 | 4 | 11/2
32 | 2 | Performance data (cont) | 1 | 5 | 2
32 | 2 | Performance data (cont) | 1 | 6 | 21/2
32 | 2 | Performance data (cont) | 1 | 7 | 3
32 | 2 | Performance data (cont) | 1 | 8 | 31/2
32 | 2 | Performance data (cont) | 1 | 9 | 4
32 | 2 | Performance data (cont) | 1 | 10 | 41/2
32 | 2 | Performance data (cont) | 1 | 11 | 5
32 | 2 | Performance data (cont) | 1 | 12 | 51/2
32 | 2 | Performance data (cont) | 2 | 1 | 983
32 | 2 | Performance data (cont) | 2 | 2 | 959
32 | 2 | Performance data (cont) | 2 | 3 | 935
32 | 2 | Performance data (cont) | 2 | 4 | 911
32 | 2 | Performance data (cont) | 2 | 5 | 887
32 | 2 | Performance data (cont) | 2 | 6 | 863
32 | 2 | Performance data (cont) | 2 | 7 | 839
32 | 2 | Performance data (cont) | 2 | 8 | 815
32 | 2 | Performance data (cont) | 2 | 9 | 791
32 | 2 | Performance data (cont) | 2 | 10 | 767
32 | 2 | Performance data (cont) | 2 | 11 | 743
32 | 2 | Performance data (cont) | 2 | 12 | †
32 | 2 | Performance data (cont) | 3 | 1 | 1300
32 | 2 | Performance data (cont) | 3 | 2 | 1272
32 | 2 | Performance data (cont) | 3 | 3 | 1245
32 | 2 | Performance data (cont) | 3 | 4 | 1217
32 | 2 | Performance data (cont) | 3 | 5 | 1189
32 | 2 | Performance data (cont) | 3 | 6 | 1162
32 | 2 | Performance data (cont) | 3 | 7 | 1134
32 | 2 | Performance data (cont) | 3 | 8 | 1106
32 | 2 | Performance data (cont) | 3 | 9 | 1078
32 | 2 | Performance data (cont) | 3 | 10 | 1051
32 | 2 | Performance data (cont) | 3 | 11 | 1023
32 | 2 | Performance data (cont) | 3 | 12 | †
32 | 2 | Performance data (cont) | 4 | 1 | 909
32 | 2 | Performance data (cont) | 4 | 2 | 895
32 | 2 | Performance data (cont) | 4 | 3 | 881
32 | 2 | Performance data (cont) | 4 | 4 | 867
32 | 2 | Performance data (cont) | 4 | 5 | 853
32 | 2 | Performance data (cont) | 4 | 6 | 839
32 | 2 | Performance data (cont) | 4 | 7 | 825
32 | 2 | Performance data (cont) | 4 | 8 | 811
32 | 2 | Performance data (cont) | 4 | 9 | 797
32 | 2 | Performance data (cont) | 4 | 10 | 783
32 | 2 | Performance data (cont) | 4 | 11 | 769
32 | 2 | Performance data (cont) | 4 | 12 | †
32 | 2 | Performance data (cont) | 5 | 1 | 1216
32 | 2 | Performance data (cont) | 5 | 2 | 1198
32 | 2 | Performance data (cont) | 5 | 3 | 1179
32 | 2 | Performance data (cont) | 5 | 4 | 1161
32 | 2 | Performance data (cont) | 5 | 5 | 1142
32 | 2 | Performance data (cont) | 5 | 6 | 1124
32 | 2 | Performance data (cont) | 5 | 7 | 1105
32 | 2 | Performance data (cont) | 5 | 8 | 1087
32 | 2 | Performance data (cont) | 5 | 9 | 1068
32 | 2 | Performance data (cont) | 5 | 10 | 1050
32 | 2 | Performance data (cont) | 5 | 11 | 1031
32 | 2 | Performance data (cont) | 5 | 12 | 1013
32 | 2 | Performance data (cont) | 6 | 1 | 1069
32 | 2 | Performance data (cont) | 6 | 2 | 1051
32 | 2 | Performance data (cont) | 6 | 3 | 1033
32 | 2 | Performance data (cont) | 6 | 4 | 1015
32 | 2 | Performance data (cont) | 6 | 5 | 997
32 | 2 | Performance data (cont) | 6 | 6 | 979
32 | 2 | Performance data (cont) | 6 | 7 | 960
32 | 2 | Performance data (cont) | 6 | 8 | 942
32 | 2 | Performance data (cont) | 6 | 9 | 924
32 | 2 | Performance data (cont) | 6 | 10 | 906
32 | 2 | Performance data (cont) | 6 | 11 | 888
32 | 2 | Performance data (cont) | 6 | 12 | †
32 | 2 | Performance data (cont) | 7 | 1 | 1341
32 | 2 | Performance data (cont) | 7 | 2 | 1318
32 | 2 | Performance data (cont) | 7 | 3 | 1296
32 | 2 | Performance data (cont) | 7 | 4 | 1273
32 | 2 | Performance data (cont) | 7 | 5 | 1250
32 | 2 | Performance data (cont) | 7 | 6 | 1228
32 | 2 | Performance data (cont) | 7 | 7 | 1205
32 | 2 | Performance data (cont) | 7 | 8 | 1182
32 | 2 | Performance data (cont) | 7 | 9 | 1159
32 | 2 | Performance data (cont) | 7 | 10 | 1137
32 | 2 | Performance data (cont) | 7 | 11 | 1114
32 | 2 | Performance data (cont) | 7 | 12 | †
32 | 3 | Performance data (cont) | 1 | 1 | UNIT RATED VOLTAGE
32 | 3 | Performance data (cont) | 1 | 2 | MAXIMUM ACCEPTABLE CONTINUOUS BHP*
32 | 3 | Performance data (cont) | 1 | 3 | MAXIMUM ACCEPTABLE CONTINUOUS BkW*
32 | 3 | Performance data (cont) | 1 | 4 | MAXIMUM ACCEPTABLE OPERATING WATTS
32 | 3 | Performance data (cont) | 2 | 1 | 220
32 | 3 | Performance data (cont) | 2 | 2 | 3.45
32 | 3 | Performance data (cont) | 2 | 3 | 3.17
32 | 3 | Performance data (cont) | 2 | 4 | 3065
32 | 3 | Performance data (cont) | 3 | 1 | 400
32 | 3 | Performance data (cont) | 3 | 2 | 4.25
32 | 3 | Performance data (cont) | 3 | 3 | 3.17
32 | 3 | Performance data (cont) | 3 | 4 | 3775
32 | 3 | Performance data (cont) | 4 | 1 | 220
32 | 3 | Performance data (cont) | 4 | 2 | 10.3
32 | 3 | Performance data (cont) | 4 | 3 | 7.68
32 | 3 | Performance data (cont) | 4 | 4 | 8640
32 | 3 | Performance data (cont) | 5 | 1 | 400
32 | 3 | Performance data (cont) | 5 | 2 | 10.3
32 | 3 | Performance data (cont) | 5 | 3 | 7.68
32 | 3 | Performance data (cont) | 5 | 4 | 8640
32 | 3 | Performance data (cont) | 6 | 1 | 220
32 | 3 | Performance data (cont) | 6 | 2 | 11.5
32 | 3 | Performance data (cont) | 6 | 3 | 8.6
32 | 3 | Performance data (cont) | 6 | 4 | 9600
32 | 3 | Performance data (cont) | 7 | 1 | 400
32 | 3 | Performance data (cont) | 7 | 2 | 13.3
32 | 3 | Performance data (cont) | 7 | 3 | 9.92
32 | 3 | Performance data (cont) | 7 | 4 | 11000
33 | 1 | Electrical data | 1 | 1 | NOMINAL VOLTAGE
33 | 1 | Electrical data | 1 | 2 | VOLTAGE RANGE
33 | 1 | Electrical data | 1 | 4 | COMPRESSOR
33 | 1 | Electrical data | 1 | 8 | OFM
33 | 1 | Electrical data | 1 | 11 | IFM
33 | 1 | Electrical data | 1 | 13 | POWER EXHAUST
33 | 1 | Electrical data | 1 | 15 | ELECTRIC HEAT*
33 | 1 | Electrical data | 2 | 4 | No. 1
33 | 1 | Electrical data | 2 | 6 | No. 2
33 | 1 | Electrical data | 3 | 2 | Min
33 | 1 | Electrical data | 3 | 3 | Max
33 | 1 | Electrical data | 3 | 4 | RLA
33 | 1 | Electrical data | 3 | 5 | LRA
33 | 1 | Electrical data | 3 | 6 | RLA
33 | 1 | Electrical data | 3 | 7 | LRA
33 | 1 | Electrical data | 3 | 8 | Qty
33 | 1 | Electrical data | 3 | 9 | Hp
33 | 1 | Electrical data | 3 | 10 | FLA (ea)
33 | 1 | Electrical data | 3 | 11 | Hp
33 | 1 | Electrical data | 3 | 12 | FLA
33 | 1 | Electrical data | 3 | 13 | FLA
33 | 1 | Electrical data | 3 | 14 | LRA
33 | 1 | Electrical data | 3 | 15 | kW
33 | 1 | Electrical data | 3 | 16 | FLA
33 | 1 | Electrical data | 3 | 17 | MCA
33 | 1 | Electrical data | 4 | 1 | 220
33 | 1 | Electrical data | 4 | 2 | 198
33 | 1 | Electrical data | 4 | 3 | 242
33 | 1 | Electrical data | 4 | 4 | 30.1
33 | 1 | Electrical data | 4 | 5 | 196
33 | 1 | Electrical data | 4 | 6 | 30.1
33 | 1 | Electrical data | 4 | 7 | 196
33 | 1 | Electrical data | 4 | 8 | 2
33 | 1 | Electrical data | 4 | 9 | 1
33 | 1 | Electrical data | 4 | 10 | 6.3
33 | 1 | Electrical data | 4 | 11 | 3
33 | 1 | Electrical data | 4 | 12 | 9.8
33 | 1 | Electrical data | 4 | 13 | — 4.7
33 | 1 | Electrical data | 4 | 14 | — 10.5
33 | 1 | Electrical data | 4 | 15 | — —
33 | 1 | Electrical data | 4 | 16 | — —
33 | 1 | Electrical data | 4 | 17 | 90 95
33 | 1 | Electrical data | 5 | 1 | 400
33 | 1 | Electrical data | 5 | 2 | 360
33 | 1 | Electrical data | 5 | 3 | 440
33 | 1 | Electrical data | 5 | 4 | 15.5
33 | 1 | Electrical data | 5 | 5 | 111
33 | 1 | Electrical data | 5 | 6 | 15.5
33 | 1 | Electrical data | 5 | 7 | 111
33 | 1 | Electrical data | 5 | 8 | 2
33 | 1 | Electrical data | 5 | 9 | 1
33 | 1 | Electrical data | 5 | 10 | 3.4
33 | 1 | Electrical data | 5 | 11 | 3
33 | 1 | Electrical data | 5 | 12 | 4.8
33 | 1 | Electrical data | 5 | 13 | — 4.7
33 | 1 | Electrical data | 5 | 14 | — 10.5
33 | 1 | Electrical data | 5 | 15 | — —
33 | 1 | Electrical data | 5 | 16 | — —
33 | 1 | Electrical data | 5 | 17 | 47 51
33 | 1 | Electrical data | 6 | 13 | 4.7
33 | 1 | Electrical data | 6 | 14 | 10.5
33 | 1 | Electrical data | 6 | 15 | 22.5 22.5
33 | 1 | Electrical data | 6 | 16 | 32.5 32.5
33 | 1 | Electrical data | 6 | 17 | 47 53
33 | 1 | Electrical data | 7 | 13 | — 4.7
33 | 1 | Electrical data | 7 | 14 | — 10.5
33 | 1 | Electrical data | 7 | 15 | 38.2 38.2
33 | 1 | Electrical data | 7 | 16 | 55.1 55.1
33 | 1 | Electrical data | 7 | 17 | 75 81
33 | 1 | Electrical data | 8 | 13 | — 4.7
33 | 1 | Electrical data | 8 | 14 | — 10.5
33 | 1 | Electrical data | 8 | 15 | 55.4** 55.4**
33 | 1 | Electrical data | 8 | 16 | 80.0 80.0
33 | 1 | Electrical data | 8 | 17 | 86 92
33 | 1 | Electrical data | 9 | 1 | 220
33 | 1 | Electrical data | 9 | 2 | 198
33 | 1 | Electrical data | 9 | 3 | 242
33 | 1 | Electrical data | 9 | 4 | 38.5
33 | 1 | Electrical data | 9 | 5 | 293
33 | 1 | Electrical data | 9 | 6 | 37.7
33 | 1 | Electrical data | 9 | 7 | 220
33 | 1 | Electrical data | 9 | 8 | 2
33 | 1 | Electrical data | 9 | 9 | 1
33 | 1 | Electrical data | 9 | 10 | 6.3
33 | 1 | Electrical data | 9 | 11 | 7.5
33 | 1 | Electrical data | 9 | 12 | 23.5
33 | 1 | Electrical data | 9 | 13 | — 4.7
33 | 1 | Electrical data | 9 | 14 | — 10.5
33 | 1 | Electrical data | 9 | 15 | — —
33 | 1 | Electrical data | 9 | 16 | — —
33 | 1 | Electrical data | 9 | 17 | 121 126
33 | 1 | Electrical data | 10 | 1 | 400
33 | 1 | Electrical data | 10 | 2 | 360
33 | 1 | Electrical data | 10 | 3 | 440
33 | 1 | Electrical data | 10 | 4 | 21.8
33 | 1 | Electrical data | 10 | 5 | 167
33 | 1 | Electrical data | 10 | 6 | 17.2
33 | 1 | Electrical data | 10 | 7 | 118
33 | 1 | Electrical data | 10 | 8 | 2
33 | 1 | Electrical data | 10 | 9 | 1
33 | 1 | Electrical data | 10 | 10 | 3.4
33 | 1 | Electrical data | 10 | 11 | 7.5
33 | 1 | Electrical data | 10 | 12 | 12.1
33 | 1 | Electrical data | 10 | 13 | — 4.7
33 | 1 | Electrical data | 10 | 14 | — 10.5
33 | 1 | Electrical data | 10 | 15 | — —
33 | 1 | Electrical data | 10 | 16 | — —
33 | 1 | Electrical data | 10 | 17 | 63 68
33 | 1 | Electrical data | 11 | 13 | — 4.7
33 | 1 | Electrical data | 11 | 14 | — 10.5
33 | 1 | Electrical data | 11 | 15 | 22.5 22.5
33 | 1 | Electrical data | 11 | 16 | 32.5 32.5
33 | 1 | Electrical data | 11 | 17 | 63 68
33 | 1 | Electrical data | 12 | 13 | 4.7
33 | 1 | Electrical data | 12 | 14 | 10.5
33 | 1 | Electrical data | 12 | 15 | 38.2 38.2
33 | 1 | Electrical data | 12 | 16 | 55.1 55.1
33 | 1 | Electrical data | 12 | 17 | 84 90
33 | 1 | Electrical data | 13 | 13 | — 4.7
33 | 1 | Electrical data | 13 | 14 | — 10.5
33 | 1 | Electrical data | 13 | 15 | 55.4** 55.4**
33 | 1 | Electrical data | 13 | 16 | 80.0 80.0
33 | 1 | Electrical data | 13 | 17 | 95 101
33 | 1 | Electrical data | 14 | 1 | 220
33 | 1 | Electrical data | 14 | 2 | 198
33 | 1 | Electrical data | 14 | 3 | 242
33 | 1 | Electrical data | 14 | 4 | 45.4
33 | 1 | Electrical data | 14 | 5 | 345
33 | 1 | Electrical data | 14 | 6 | 38.5
33 | 1 | Electrical data | 14 | 7 | 293
33 | 1 | Electrical data | 14 | 8 | 2
33 | 1 | Electrical data | 14 | 9 | 1
33 | 1 | Electrical data | 14 | 10 | 6.3
33 | 1 | Electrical data | 14 | 11 | 10
33 | 1 | Electrical data | 14 | 12 | 32
33 | 1 | Electrical data | 14 | 13 | — 4.7
33 | 1 | Electrical data | 14 | 14 | — 10.5
33 | 1 | Electrical data | 14 | 15 | — —
33 | 1 | Electrical data | 14 | 16 | — —
33 | 1 | Electrical data | 14 | 17 | 139 144
33 | 1 | Electrical data | 15 | 1 | 400
33 | 1 | Electrical data | 15 | 2 | 360
33 | 1 | Electrical data | 15 | 3 | 440
33 | 1 | Electrical data | 15 | 4 | 23.7
33 | 1 | Electrical data | 15 | 5 | 198
33 | 1 | Electrical data | 15 | 6 | 21.8
33 | 1 | Electrical data | 15 | 7 | 167
33 | 1 | Electrical data | 15 | 8 | 2
33 | 1 | Electrical data | 15 | 9 | 1
33 | 1 | Electrical data | 15 | 10 | 3.4
33 | 1 | Electrical data | 15 | 11 | 10
33 | 1 | Electrical data | 15 | 12 | 14
33 | 1 | Electrical data | 15 | 13 | — 4.7
33 | 1 | Electrical data | 15 | 14 | — 10.5
33 | 1 | Electrical data | 15 | 15 | — —
33 | 1 | Electrical data | 15 | 16 | — —
33 | 1 | Electrical data | 15 | 17 | 72 77
33 | 1 | Electrical data | 16 | 13 | — 4.7
33 | 1 | Electrical data | 16 | 14 | — 10.5
33 | 1 | Electrical data | 16 | 15 | 22.5 22.5
33 | 1 | Electrical data | 16 | 16 | 32.5 32.5
33 | 1 | Electrical data | 16 | 17 | 72 77
33 | 1 | Electrical data | 17 | 13 | — 4.7
33 | 1 | Electrical data | 17 | 14 | — 10.5
33 | 1 | Electrical data | 17 | 15 | 38.2 38.2
33 | 1 | Electrical data | 17 | 16 | 55.1 55.1
33 | 1 | Electrical data | 17 | 17 | 86 92
33 | 1 | Electrical data | 18 | 13 | — 4.7
33 | 1 | Electrical data | 18 | 14 | — 10.5
33 | 1 | Electrical data | 18 | 15 | 55.4** 55.4**
33 | 1 | Electrical data | 18 | 16 | 80.0 80.0
33 | 1 | Electrical data | 18 | 17 | 98 103
33 | 1 | Electrical data | 19 | 1 | 400
33 | 1 | Electrical data | 19 | 2 | 360
33 | 1 | Electrical data | 19 | 3 | 440
33 | 1 | Electrical data | 19 | 4 | 23.7
33 | 1 | Electrical data | 19 | 5 | 198
33 | 1 | Electrical data | 19 | 6 | 21.8
33 | 1 | Electrical data | 19 | 7 | 167
33 | 1 | Electrical data | 19 | 8 | 2
33 | 1 | Electrical data | 19 | 9 | 5
33 | 1 | Electrical data | 19 | 10 | 7.3
33 | 1 | Electrical data | 19 | 11 | 10
33 | 1 | Electrical data | 19 | 12 | 14
33 | 1 | Electrical data | 19 | 13 | — 4.7
33 | 1 | Electrical data | 19 | 14 | — 10.5
33 | 1 | Electrical data | 19 | 15 | — —
33 | 1 | Electrical data | 19 | 16 | — —
33 | 1 | Electrical data | 19 | 17 | 80 85
33 | 1 | Electrical data | 20 | 13 | — 4.7
33 | 1 | Electrical data | 20 | 14 | — 10.5
33 | 1 | Electrical data | 20 | 15 | 22.5 22.5
33 | 1 | Electrical data | 20 | 16 | 32.5 32.5
33 | 1 | Electrical data | 20 | 17 | 80 85
33 | 1 | Electrical data | 21 | 13 | — 4.7
33 | 1 | Electrical data | 21 | 14 | — 10.5
33 | 1 | Electrical data | 21 | 15 | 38.2 38.2
33 | 1 | Electrical data | 21 | 16 | 55.1 55.1
33 | 1 | Electrical data | 21 | 17 | 86 92
33 | 1 | Electrical data | 22 | 13 | — 4.7
33 | 1 | Electrical data | 22 | 14 | — 10.5
33 | 1 | Electrical data | 22 | 15 | 55.4** 55.4**
33 | 1 | Electrical data | 22 | 16 | 80.0 80.0
33 | 1 | Electrical data | 22 | 17 | 98 103

## Performance_Tables
source_page | table_no | page_title | row_no | column_no | cell_value
19 | 1 | Performance data | 1 | 1 | 2124/0.12
19 | 1 | Performance data | 1 | 2 | 2478/0.14
19 | 1 | Performance data | 1 | 3 | 2832/0.15
19 | 1 | Performance data | 1 | 4 | 3186/0.17
19 | 2 | Performance data | 1 | 2 | 17
19 | 2 | Performance data | 1 | 3 | 19
19 | 2 | Performance data | 1 | 4 | 22
19 | 2 | Performance data | 1 | 5 | 17
19 | 2 | Performance data | 1 | 6 | 19
19 | 2 | Performance data | 1 | 7 | 22
19 | 2 | Performance data | 1 | 8 | 17
19 | 2 | Performance data | 1 | 9 | 19
19 | 2 | Performance data | 1 | 10 | 22
19 | 2 | Performance data | 1 | 11 | 17
19 | 2 | Performance data | 1 | 12 | 19
19 | 2 | Performance data | 1 | 13 | 22
19 | 2 | Performance data | 1 | 14 | 17
19 | 2 | Performance data | 1 | 15 | 19
19 | 2 | Performance data | 2 | 1 | TC SHC kW
19 | 2 | Performance data | 2 | 2 | 49.0 41.6 11.3
19 | 2 | Performance data | 2 | 3 | 53.3 35.5 11.7
19 | 2 | Performance data | 2 | 4 | 58.7 28.8 13.3
19 | 2 | Performance data | 2 | 5 | 50.3 45.1 11.5
19 | 2 | Performance data | 2 | 6 | 54.9 37.8 11.9
19 | 2 | Performance data | 2 | 7 | 60.3 30.6 13.4
19 | 2 | Performance data | 2 | 8 | 51.8 47.5 11.6
19 | 2 | Performance data | 2 | 9 | 56.5 40.1 12.0
19 | 2 | Performance data | 2 | 10 | 61.3 32.0 13.5
19 | 2 | Performance data | 2 | 11 | 52.8 50.2 11.7
19 | 2 | Performance data | 2 | 12 | 57.1 43.1 12.0
19 | 2 | Performance data | 2 | 13 | 61.9 34.7 13.6
19 | 2 | Performance data | 2 | 14 | 53.9 52.7 11.7
19 | 2 | Performance data | 2 | 15 | 57.6 45.2 12.1
19 | 2 | Performance data | 3 | 1 | TC SHC kW
19 | 2 | Performance data | 3 | 2 | 47.6 40.8 12.7
19 | 2 | Performance data | 3 | 3 | 51.7 34.7 13.0
19 | 2 | Performance data | 3 | 4 | 56.5 28.2 14.7
19 | 2 | Performance data | 3 | 5 | 49.0 44.0 12.8
19 | 2 | Performance data | 3 | 6 | 53.3 37.1 13.2
19 | 2 | Performance data | 3 | 7 | 58.1 29.7 14.9
19 | 2 | Performance data | 3 | 8 | 50.2 46.7 12.9
19 | 2 | Performance data | 3 | 9 | 54.4 39.3 13.3
19 | 2 | Performance data | 3 | 10 | 59.7 31.2 15.0
19 | 2 | Performance data | 3 | 11 | 51.2 49.4 13.0
19 | 2 | Performance data | 3 | 12 | 55.5 41.4 13.4
19 | 2 | Performance data | 3 | 13 | 60.3 33.1 15.1
19 | 2 | Performance data | 3 | 14 | 52.1 51.7 13.1
19 | 2 | Performance data | 3 | 15 | 56.0 44.2 13.5
19 | 2 | Performance data | 4 | 1 | TC SHC kW
19 | 2 | Performance data | 4 | 2 | 46.0 40.0 14.1
19 | 2 | Performance data | 4 | 3 | 50.1 33.8 14.5
19 | 2 | Performance data | 4 | 4 | 54.9 27.4 16.3
19 | 2 | Performance data | 4 | 5 | 47.4 43.1 14.3
19 | 2 | Performance data | 4 | 6 | 51.5 36.2 14.6
19 | 2 | Performance data | 4 | 7 | 56.5 28.9 16.5
19 | 2 | Performance data | 4 | 8 | 48.5 45.9 14.4
19 | 2 | Performance data | 4 | 9 | 52.6 38.5 14.7
19 | 2 | Performance data | 4 | 10 | 57.6 30.3 16.6
19 | 2 | Performance data | 4 | 11 | 49.4 48.5 14.5
19 | 2 | Performance data | 4 | 12 | 53.3 40.6 14.9
19 | 2 | Performance data | 4 | 13 | 58.7 31.5 16.7
19 | 2 | Performance data | 4 | 14 | 50.4 50.4 14.6
19 | 2 | Performance data | 4 | 15 | 54.4 42.8 15.0
19 | 2 | Performance data | 5 | 1 | TC SHC kW
19 | 2 | Performance data | 5 | 2 | 43.5 38.2 15.7
19 | 2 | Performance data | 5 | 3 | 47.3 32.4 16.2
19 | 2 | Performance data | 5 | 4 | 51.8 26.2 18.1
19 | 2 | Performance data | 5 | 5 | 44.7 41.2 15.9
19 | 2 | Performance data | 5 | 6 | 48.5 34.7 16.3
19 | 2 | Performance data | 5 | 7 | 52.9 27.6 18.3
19 | 2 | Performance data | 5 | 8 | 45.7 44.0 16.0
19 | 2 | Performance data | 5 | 9 | 49.5 36.8 16.4
19 | 2 | Performance data | 5 | 10 | 53.9 28.9 18.4
19 | 2 | Performance data | 5 | 11 | 46.6 46.4 16.1
19 | 2 | Performance data | 5 | 12 | 50.3 38.9 16.5
19 | 2 | Performance data | 5 | 13 | 55.0 30.0 18.5
19 | 2 | Performance data | 5 | 14 | 47.7 47.9 16.2
19 | 2 | Performance data | 5 | 15 | 51.0 41.0 16.6
19 | 2 | Performance data | 6 | 1 | TC SHC kW
19 | 2 | Performance data | 6 | 2 | 40.8 36.5 17.4
19 | 2 | Performance data | 6 | 3 | 44.4 31.0 17.9
19 | 2 | Performance data | 6 | 4 | 48.7 24.9 18.4
19 | 2 | Performance data | 6 | 5 | 41.9 39.5 17.6
19 | 2 | Performance data | 6 | 6 | 45.5 33.2 18.0
19 | 2 | Performance data | 6 | 7 | 49.9 26.3 18.6
19 | 2 | Performance data | 6 | 8 | 42.7 42.2 17.7
19 | 2 | Performance data | 6 | 9 | 46.4 35.3 18.1
19 | 2 | Performance data | 6 | 10 | 50.5 27.6 18.7
19 | 2 | Performance data | 6 | 11 | 43.9 44.1 17.9
19 | 2 | Performance data | 6 | 12 | 47.1 37.2 18.3
19 | 2 | Performance data | 6 | 13 | 51.0 28.7 18.7
19 | 2 | Performance data | 6 | 14 | 44.9 45.2 18.0
19 | 2 | Performance data | 6 | 15 | 47.6 39.2 18.3
19 | 2 | Performance data | 7 | 1 | TC SHC kW
19 | 2 | Performance data | 7 | 2 | 39.0 35.4 18.4
19 | 2 | Performance data | 7 | 3 | 42.4 30.0 18.9
19 | 2 | Performance data | 7 | 4 | 46.6 24.0 19.4
19 | 2 | Performance data | 7 | 5 | 40.0 38.3 18.5
19 | 2 | Performance data | 7 | 6 | 43.5 32.1 19.0
19 | 2 | Performance data | 7 | 7 | 47.7 25.3 19.6
19 | 2 | Performance data | 7 | 8 | 40.9 40.7 18.7
19 | 2 | Performance data | 7 | 9 | 44.3 34.3 19.1
19 | 2 | Performance data | 7 | 10 | 48.4 26.7 19.8
19 | 2 | Performance data | 7 | 11 | 42.0 42.3 18.8
19 | 2 | Performance data | 7 | 12 | 45.0 36.3 19.2
19 | 2 | Performance data | 7 | 13 | 48.8 27.8 19.8
19 | 2 | Performance data | 7 | 14 | 43.0 43.4 18.9
19 | 2 | Performance data | 7 | 15 | 45.5 37.9 19.3
19 | 2 | Performance data | 8 | 1 | TC SHC kW
19 | 2 | Performance data | 8 | 2 | 37.2 34.2 19.3
19 | 2 | Performance data | 8 | 3 | 40.5 29.0 19.7
19 | 2 | Performance data | 8 | 4 | 44.2 23.8 20.3
19 | 2 | Performance data | 8 | 5 | 38.1 36.9 19.4
19 | 2 | Performance data | 8 | 6 | 41.4 31.1 19.9
19 | 2 | Performance data | 8 | 7 | — — —
19 | 2 | Performance data | 8 | 8 | 39.1 39.2 19.6
19 | 2 | Performance data | 8 | 9 | 42.2 33.1 20.1
19 | 2 | Performance data | 8 | 10 | — — —
19 | 2 | Performance data | 8 | 11 | 40.2 40.5 19.7
19 | 2 | Performance data | 8 | 12 | 42.9 35.0 20.1
19 | 2 | Performance data | 8 | 13 | — — —
19 | 2 | Performance data | 8 | 14 | 41.2 41.5 19.9
19 | 2 | Performance data | 8 | 15 | 43.3 36.6 20.1
19 | 3 | Performance data | 1 | 1 | 2832/0.075
19 | 3 | Performance data | 1 | 2 | 3304/0.085
19 | 3 | Performance data | 1 | 3 | 3776/0.100
19 | 3 | Performance data | 1 | 4 | 4248/0.110
19 | 4 | Performance data | 1 | 2 | 17
19 | 4 | Performance data | 1 | 3 | 19
19 | 4 | Performance data | 1 | 4 | 22
19 | 4 | Performance data | 1 | 5 | 17
19 | 4 | Performance data | 1 | 6 | 19
19 | 4 | Performance data | 1 | 7 | 22
19 | 4 | Performance data | 1 | 8 | 17
19 | 4 | Performance data | 1 | 9 | 19
19 | 4 | Performance data | 1 | 10 | 22
19 | 4 | Performance data | 1 | 11 | 17
19 | 4 | Performance data | 1 | 12 | 19
19 | 4 | Performance data | 1 | 13 | 22
19 | 4 | Performance data | 1 | 14 | 17
19 | 4 | Performance data | 1 | 15 | 19
19 | 4 | Performance data | 2 | 1 | TC SHC kW
19 | 4 | Performance data | 2 | 2 | 64.3 55.1 15.1
19 | 4 | Performance data | 2 | 3 | 70.9 46.5 15.6
19 | 4 | Performance data | 2 | 4 | 76.9 36.9 16.5
19 | 4 | Performance data | 2 | 5 | 65.9 59.5 15.2
19 | 4 | Performance data | 2 | 6 | 72.7 49.7 15.8
19 | 4 | Performance data | 2 | 7 | 78.8 38.9 16.7
19 | 4 | Performance data | 2 | 8 | 67.2 63.6 15.4
19 | 4 | Performance data | 2 | 9 | 74.1 53.0 15.9
19 | 4 | Performance data | 2 | 10 | 80.3 40.8 16.9
19 | 4 | Performance data | 2 | 11 | 68.4 67.2 15.5
19 | 4 | Performance data | 2 | 12 | 75.0 56.0 16.0
19 | 4 | Performance data | 2 | 13 | 81.3 42.8 17.0
19 | 4 | Performance data | 2 | 14 | 69.7 69.6 15.7
19 | 4 | Performance data | 2 | 15 | 75.8 59.1 16.1
19 | 4 | Performance data | 3 | 1 | TC SHC kW
19 | 4 | Performance data | 3 | 2 | 62.1 54.0 16.7
19 | 4 | Performance data | 3 | 3 | 68.5 45.4 17.2
19 | 4 | Performance data | 3 | 4 | 74.3 36.0 18.2
19 | 4 | Performance data | 3 | 5 | 63.6 58.4 16.9
19 | 4 | Performance data | 3 | 6 | 70.2 48.8 17.4
19 | 4 | Performance data | 3 | 7 | 76.1 38.0 18.5
19 | 4 | Performance data | 3 | 8 | 64.9 62.4 17.0
19 | 4 | Performance data | 3 | 9 | 71.4 51.9 17.6
19 | 4 | Performance data | 3 | 10 | 77.5 39.9 18.6
19 | 4 | Performance data | 3 | 11 | 66.0 65.6 17.2
19 | 4 | Performance data | 3 | 12 | 72.3 54.8 17.7
19 | 4 | Performance data | 3 | 13 | 78.5 41.7 18.7
19 | 4 | Performance data | 3 | 14 | 67.8 67.6 17.4
19 | 4 | Performance data | 3 | 15 | 73.1 57.9 17.8
19 | 4 | Performance data | 4 | 1 | TC SHC kW
19 | 4 | Performance data | 4 | 2 | 59.8 53.0 18.5
19 | 4 | Performance data | 4 | 3 | 65.9 44.4 19.0
19 | 4 | Performance data | 4 | 4 | 71.6 35.0 20.1
19 | 4 | Performance data | 4 | 5 | 61.2 57.1 18.7
19 | 4 | Performance data | 4 | 6 | 67.4 47.7 19.2
19 | 4 | Performance data | 4 | 7 | 73.2 37.0 20.3
19 | 4 | Performance data | 4 | 8 | 62.4 61.0 18.8
19 | 4 | Performance data | 4 | 9 | 68.6 50.7 19.3
19 | 4 | Performance data | 4 | 10 | 74.4 38.9 20.4
19 | 4 | Performance data | 4 | 11 | 63.8 63.7 19.0
19 | 4 | Performance data | 4 | 12 | 69.4 53.6 19.4
19 | 4 | Performance data | 4 | 13 | 75.3 40.6 20.5
19 | 4 | Performance data | 4 | 14 | 65.3 65.1 19.1
19 | 4 | Performance data | 4 | 15 | 70.0 56.7 19.5
19 | 4 | Performance data | 5 | 1 | TC SHC kW
19 | 4 | Performance data | 5 | 2 | 57.0 51.6 20.3
19 | 4 | Performance data | 5 | 3 | 63.0 43.3 20.8
19 | 4 | Performance data | 5 | 4 | 68.5 33.9 22.0
19 | 4 | Performance data | 5 | 5 | 58.4 55.8 20.5
19 | 4 | Performance data | 5 | 6 | 64.4 46.5 21.0
19 | 4 | Performance data | 5 | 7 | 70.0 35.9 22.2
19 | 4 | Performance data | 5 | 8 | 59.7 59.3 20.6
19 | 4 | Performance data | 5 | 9 | 65.3 49.4 21.1
19 | 4 | Performance data | 5 | 10 | 71.1 37.7 22.3
19 | 4 | Performance data | 5 | 11 | 61.4 61.3 20.8
19 | 4 | Performance data | 5 | 12 | 66.1 52.6 21.2
19 | 4 | Performance data | 5 | 13 | 71.9 39.5 22.4
19 | 4 | Performance data | 5 | 14 | 62.8 62.6 21.0
19 | 4 | Performance data | 5 | 15 | 66.7 55.4 21.3
19 | 4 | Performance data | 6 | 1 | TC SHC kW
19 | 4 | Performance data | 6 | 2 | 54.2 50.2 22.1
19 | 4 | Performance data | 6 | 3 | 59.9 42.0 22.7
19 | 4 | Performance data | 6 | 4 | 65.2 32.8 23.9
19 | 4 | Performance data | 6 | 5 | 55.6 54.3 22.3
19 | 4 | Performance data | 6 | 6 | 61.2 45.3 22.8
19 | 4 | Performance data | 6 | 7 | 66.6 34.7 24.1
19 | 4 | Performance data | 6 | 8 | 57.1 56.9 22.5
19 | 4 | Performance data | 6 | 9 | 62.1 48.3 23.0
19 | 4 | Performance data | 6 | 10 | 67.6 36.5 24.2
19 | 4 | Performance data | 6 | 11 | 58.7 58.6 22.7
19 | 4 | Performance data | 6 | 12 | 62.7 51.1 23.1
19 | 4 | Performance data | 6 | 13 | 68.3 38.3 24.3
19 | 4 | Performance data | 6 | 14 | 60.0 59.8 22.9
19 | 4 | Performance data | 6 | 15 | 63.2 53.7 23.2
19 | 4 | Performance data | 7 | 1 | TC SHC kW
19 | 4 | Performance data | 7 | 2 | 51.2 48.7 24.0
19 | 4 | Performance data | 7 | 3 | 56.6 40.7 24.6
19 | 4 | Performance data | 7 | 4 | — — —
19 | 4 | Performance data | 7 | 5 | 52.7 52.3 24.2
19 | 4 | Performance data | 7 | 6 | 57.6 43.8 24.7
19 | 4 | Performance data | 7 | 7 | — — —
19 | 4 | Performance data | 7 | 8 | 54.3 54.2 24.4
19 | 4 | Performance data | 7 | 9 | 58.4 47.0 24.9
19 | 4 | Performance data | 7 | 10 | — — —
19 | 4 | Performance data | 7 | 11 | 55.9 55.7 24.6
19 | 4 | Performance data | 7 | 12 | 59.0 49.6 25.0
19 | 4 | Performance data | 7 | 13 | — — —
19 | 4 | Performance data | 7 | 14 | 57.0 56.9 24.8
19 | 4 | Performance data | 7 | 15 | 59.4 52.1 25.0
20 | 1 | Performance data (cont) | 1 | 1 | 3304/0.05
20 | 1 | Performance data (cont) | 1 | 2 | 3776/0.06
20 | 1 | Performance data (cont) | 1 | 3 | 4248/0.07
20 | 1 | Performance data (cont) | 1 | 4 | 4720/0.08
20 | 2 | Performance data (cont) | 1 | 2 | 17
20 | 2 | Performance data (cont) | 1 | 3 | 19
20 | 2 | Performance data (cont) | 1 | 4 | 22
20 | 2 | Performance data (cont) | 1 | 5 | 17
20 | 2 | Performance data (cont) | 1 | 6 | 19
20 | 2 | Performance data (cont) | 1 | 7 | 22
20 | 2 | Performance data (cont) | 1 | 8 | 17
20 | 2 | Performance data (cont) | 1 | 9 | 19
20 | 2 | Performance data (cont) | 1 | 10 | 22
20 | 2 | Performance data (cont) | 1 | 11 | 17
20 | 2 | Performance data (cont) | 1 | 12 | 19
20 | 2 | Performance data (cont) | 1 | 13 | 22
20 | 2 | Performance data (cont) | 1 | 14 | 17
20 | 2 | Performance data (cont) | 1 | 15 | 19
20 | 2 | Performance data (cont) | 2 | 1 | TC SHC kW
20 | 2 | Performance data (cont) | 2 | 2 | 79.4 67.7 20.1
20 | 2 | Performance data (cont) | 2 | 3 | 87.6 57.2 20.8
20 | 2 | Performance data (cont) | 2 | 4 | 96.5 46.5 21.6
20 | 2 | Performance data (cont) | 2 | 5 | 81.2 72.6 20.3
20 | 2 | Performance data (cont) | 2 | 6 | 89.6 60.7 21.0
20 | 2 | Performance data (cont) | 2 | 7 | 98.6 48.4 21.8
20 | 2 | Performance data (cont) | 2 | 8 | 82.7 77.5 20.4
20 | 2 | Performance data (cont) | 2 | 9 | 91.0 64.4 21.2
20 | 2 | Performance data (cont) | 2 | 10 | 100.3 51.2 22.0
20 | 2 | Performance data (cont) | 2 | 11 | 83.9 81.7 20.6
20 | 2 | Performance data (cont) | 2 | 12 | 91.9 68.7 21.3
20 | 2 | Performance data (cont) | 2 | 13 | 101.6 53.3 22.2
20 | 2 | Performance data (cont) | 2 | 14 | 85.7 85.6 20.8
20 | 2 | Performance data (cont) | 2 | 15 | 93.4 72.6 21.5
20 | 2 | Performance data (cont) | 3 | 1 | TC SHC kW
20 | 2 | Performance data (cont) | 3 | 2 | 76.6 66.5 22.2
20 | 2 | Performance data (cont) | 3 | 3 | 84.5 55.9 23.0
20 | 2 | Performance data (cont) | 3 | 4 | 93.1 45.0 23.8
20 | 2 | Performance data (cont) | 3 | 5 | 78.3 71.2 22.4
20 | 2 | Performance data (cont) | 3 | 6 | 86.4 59.4 23.2
20 | 2 | Performance data (cont) | 3 | 7 | 95.0 47.4 24.0
20 | 2 | Performance data (cont) | 3 | 8 | 79.8 75.6 22.6
20 | 2 | Performance data (cont) | 3 | 9 | 88.0 62.9 23.4
20 | 2 | Performance data (cont) | 3 | 10 | 96.6 49.4 24.2
20 | 2 | Performance data (cont) | 3 | 11 | 81.0 79.7 22.8
20 | 2 | Performance data (cont) | 3 | 12 | 89.1 66.4 23.5
20 | 2 | Performance data (cont) | 3 | 13 | 98.1 51.6 24.4
20 | 2 | Performance data (cont) | 3 | 14 | 83.1 83.0 23.0
20 | 2 | Performance data (cont) | 3 | 15 | 90.4 70.5 23.7
20 | 2 | Performance data (cont) | 4 | 1 | TC SHC kW
20 | 2 | Performance data (cont) | 4 | 2 | 73.7 65.0 24.6
20 | 2 | Performance data (cont) | 4 | 3 | 81.2 54.6 25.3
20 | 2 | Performance data (cont) | 4 | 4 | 89.4 44.0 26.1
20 | 2 | Performance data (cont) | 4 | 5 | 75.2 69.7 24.7
20 | 2 | Performance data (cont) | 4 | 6 | 83.0 58.1 25.5
20 | 2 | Performance data (cont) | 4 | 7 | 91.1 46.0 26.3
20 | 2 | Performance data (cont) | 4 | 8 | 76.7 74.1 24.9
20 | 2 | Performance data (cont) | 4 | 9 | 84.2 61.8 25.7
20 | 2 | Performance data (cont) | 4 | 10 | 92.7 48.1 26.5
20 | 2 | Performance data (cont) | 4 | 11 | 78.1 77.7 25.1
20 | 2 | Performance data (cont) | 4 | 12 | 85.5 64.8 25.8
20 | 2 | Performance data (cont) | 4 | 13 | 94.0 50.1 26.7
20 | 2 | Performance data (cont) | 4 | 14 | 80.3 80.2 25.4
20 | 2 | Performance data (cont) | 4 | 15 | 86.6 68.9 26.0
20 | 2 | Performance data (cont) | 5 | 1 | TC SHC kW
20 | 2 | Performance data (cont) | 5 | 2 | 70.5 63.3 27.0
20 | 2 | Performance data (cont) | 5 | 3 | 77.8 53.3 27.8
20 | 2 | Performance data (cont) | 5 | 4 | 85.4 42.6 28.6
20 | 2 | Performance data (cont) | 5 | 5 | 71.9 68.0 27.2
20 | 2 | Performance data (cont) | 5 | 6 | 79.2 56.5 28.0
20 | 2 | Performance data (cont) | 5 | 7 | 87.2 44.7 28.8
20 | 2 | Performance data (cont) | 5 | 8 | 73.5 72.0 27.4
20 | 2 | Performance data (cont) | 5 | 9 | 80.4 60.1 28.1
20 | 2 | Performance data (cont) | 5 | 10 | 88.6 46.6 29.0
20 | 2 | Performance data (cont) | 5 | 11 | 75.0 75.0 27.6
20 | 2 | Performance data (cont) | 5 | 12 | 81.4 63.3 28.3
20 | 2 | Performance data (cont) | 5 | 13 | 89.6 48.8 29.2
20 | 2 | Performance data (cont) | 5 | 14 | 77.2 77.1 27.9
20 | 2 | Performance data (cont) | 5 | 15 | 82.5 67.2 28.4
20 | 2 | Performance data (cont) | 6 | 1 | TC SHC kW
20 | 2 | Performance data (cont) | 6 | 2 | 67.1 61.9 29.5
20 | 2 | Performance data (cont) | 6 | 3 | 74.0 51.8 30.3
20 | 2 | Performance data (cont) | 6 | 4 | 81.2 41.0 31.1
20 | 2 | Performance data (cont) | 6 | 5 | 68.4 66.2 29.7
20 | 2 | Performance data (cont) | 6 | 6 | 75.3 55.0 30.5
20 | 2 | Performance data (cont) | 6 | 7 | 82.5 43.1 31.3
20 | 2 | Performance data (cont) | 6 | 8 | 70.0 69.8 30.0
20 | 2 | Performance data (cont) | 6 | 9 | 76.4 58.4 30.7
20 | 2 | Performance data (cont) | 6 | 10 | 83.6 44.9 31.5
20 | 2 | Performance data (cont) | 6 | 11 | 71.9 71.8 30.2
20 | 2 | Performance data (cont) | 6 | 12 | 77.3 61.7 30.8
20 | 2 | Performance data (cont) | 6 | 13 | — — —
20 | 2 | Performance data (cont) | 6 | 14 | 73.8 73.8 30.5
20 | 2 | Performance data (cont) | 6 | 15 | 78.2 65.4 31.0
20 | 2 | Performance data (cont) | 7 | 1 | TC SHC kW
20 | 2 | Performance data (cont) | 7 | 2 | 66.1 61.4 30.3
20 | 2 | Performance data (cont) | 7 | 3 | 72.7 51.3 31.1
20 | 2 | Performance data (cont) | 7 | 4 | — — —
20 | 2 | Performance data (cont) | 7 | 5 | 67.4 65.6 30.5
20 | 2 | Performance data (cont) | 7 | 6 | 73.9 54.5 31.2
20 | 2 | Performance data (cont) | 7 | 7 | — — —
20 | 2 | Performance data (cont) | 7 | 8 | 68.9 68.8 30.7
20 | 2 | Performance data (cont) | 7 | 9 | 74.8 57.8 31.4
20 | 2 | Performance data (cont) | 7 | 10 | — — —
20 | 2 | Performance data (cont) | 7 | 11 | 70.6 70.5 31.0
20 | 2 | Performance data (cont) | 7 | 12 | 75.5 61.1 31.5
20 | 2 | Performance data (cont) | 7 | 13 | — — —
20 | 2 | Performance data (cont) | 7 | 14 | 72.4 72.4 31.2
20 | 2 | Performance data (cont) | 7 | 15 | — — —
20 | 2 | Performance data (cont) | 8 | 1 | TC SHC kW
20 | 2 | Performance data (cont) | 8 | 2 | 65.2 60.9 30.8
20 | 2 | Performance data (cont) | 8 | 3 | — — —
20 | 2 | Performance data (cont) | 8 | 4 | — — —
20 | 2 | Performance data (cont) | 8 | 5 | 66.6 65.2 31.0
20 | 2 | Performance data (cont) | 8 | 6 | — — —
20 | 2 | Performance data (cont) | 8 | 7 | — — —
20 | 2 | Performance data (cont) | 8 | 8 | 68.4 68.4 31.3
20 | 2 | Performance data (cont) | 8 | 9 | — — —
20 | 2 | Performance data (cont) | 8 | 10 | — — —
20 | 2 | Performance data (cont) | 8 | 11 | 70.0 70.0 31.5
20 | 2 | Performance data (cont) | 8 | 12 | — — —
20 | 2 | Performance data (cont) | 8 | 13 | — — —
20 | 2 | Performance data (cont) | 8 | 14 | — — —
20 | 2 | Performance data (cont) | 8 | 15 | — — —
20 | 3 | Performance data (cont) | 1 | 1 | 3304/0.05
20 | 3 | Performance data (cont) | 1 | 2 | 3776/0.06
20 | 3 | Performance data (cont) | 1 | 3 | 4248/0.07
20 | 3 | Performance data (cont) | 1 | 4 | 4720/0.08
20 | 4 | Performance data (cont) | 1 | 2 | 17
20 | 4 | Performance data (cont) | 1 | 3 | 19
20 | 4 | Performance data (cont) | 1 | 4 | 22
20 | 4 | Performance data (cont) | 1 | 5 | 17
20 | 4 | Performance data (cont) | 1 | 6 | 19
20 | 4 | Performance data (cont) | 1 | 7 | 22
20 | 4 | Performance data (cont) | 1 | 8 | 17
20 | 4 | Performance data (cont) | 1 | 9 | 19
20 | 4 | Performance data (cont) | 1 | 10 | 22
20 | 4 | Performance data (cont) | 1 | 11 | 17
20 | 4 | Performance data (cont) | 1 | 12 | 19
20 | 4 | Performance data (cont) | 1 | 13 | 22
20 | 4 | Performance data (cont) | 1 | 14 | 17
20 | 4 | Performance data (cont) | 1 | 15 | 19
20 | 4 | Performance data (cont) | 2 | 1 | TC SHC kW
20 | 4 | Performance data (cont) | 2 | 2 | 82.3 69.1 18.2
20 | 4 | Performance data (cont) | 2 | 3 | 90.8 58.8 18.8
20 | 4 | Performance data (cont) | 2 | 4 | 100.5 47.8 19.4
20 | 4 | Performance data (cont) | 2 | 5 | 84.4 74.1 18.4
20 | 4 | Performance data (cont) | 2 | 6 | 93.2 62.6 19.0
20 | 4 | Performance data (cont) | 2 | 7 | 102.8 50.3 19.6
20 | 4 | Performance data (cont) | 2 | 8 | 85.6 79.7 18.5
20 | 4 | Performance data (cont) | 2 | 9 | 94.6 66.9 19.1
20 | 4 | Performance data (cont) | 2 | 10 | 104.0 54.3 19.7
20 | 4 | Performance data (cont) | 2 | 11 | 87.3 83.2 18.6
20 | 4 | Performance data (cont) | 2 | 12 | 95.8 70.2 19.2
20 | 4 | Performance data (cont) | 2 | 13 | 105.8 56.6 19.9
20 | 4 | Performance data (cont) | 2 | 14 | 89.1 87.9 18.8
20 | 4 | Performance data (cont) | 2 | 15 | 97.3 75.3 19.4
20 | 4 | Performance data (cont) | 3 | 1 | TC SHC kW
20 | 4 | Performance data (cont) | 3 | 2 | 79.7 68.0 20.3
20 | 4 | Performance data (cont) | 3 | 3 | 87.9 57.4 20.8
20 | 4 | Performance data (cont) | 3 | 4 | 97.3 46.6 21.5
20 | 4 | Performance data (cont) | 3 | 5 | 81.7 73.0 20.4
20 | 4 | Performance data (cont) | 3 | 6 | 90.5 61.1 21.0
20 | 4 | Performance data (cont) | 3 | 7 | 99.6 49.1 21.7
20 | 4 | Performance data (cont) | 3 | 8 | 83.2 77.6 20.6
20 | 4 | Performance data (cont) | 3 | 9 | 92.0 65.0 21.2
20 | 4 | Performance data (cont) | 3 | 10 | 101.7 51.4 21.8
20 | 4 | Performance data (cont) | 3 | 11 | 84.7 81.7 20.8
20 | 4 | Performance data (cont) | 3 | 12 | 93.2 68.0 21.4
20 | 4 | Performance data (cont) | 3 | 13 | 102.8 53.7 22.0
20 | 4 | Performance data (cont) | 3 | 14 | 86.7 85.8 20.9
20 | 4 | Performance data (cont) | 3 | 15 | 94.3 73.2 21.4
20 | 4 | Performance data (cont) | 4 | 1 | TC SHC kW
20 | 4 | Performance data (cont) | 4 | 2 | 76.8 66.5 22.6
20 | 4 | Performance data (cont) | 4 | 3 | 85.3 56.2 23.1
20 | 4 | Performance data (cont) | 4 | 4 | 93.8 45.6 23.7
20 | 4 | Performance data (cont) | 4 | 5 | 78.5 71.5 22.6
20 | 4 | Performance data (cont) | 4 | 6 | 87.0 59.7 23.3
20 | 4 | Performance data (cont) | 4 | 7 | 95.8 47.8 23.9
20 | 4 | Performance data (cont) | 4 | 8 | 80.3 75.6 22.8
20 | 4 | Performance data (cont) | 4 | 9 | 88.5 63.1 23.4
20 | 4 | Performance data (cont) | 4 | 10 | 97.6 49.9 24.1
20 | 4 | Performance data (cont) | 4 | 11 | 81.7 79.4 23.0
20 | 4 | Performance data (cont) | 4 | 12 | 90.0 66.6 23.6
20 | 4 | Performance data (cont) | 4 | 13 | 99.0 52.0 24.2
20 | 4 | Performance data (cont) | 4 | 14 | 83.5 82.9 23.1
20 | 4 | Performance data (cont) | 4 | 15 | 91.1 70.6 23.6
20 | 4 | Performance data (cont) | 5 | 1 | TC SHC kW
20 | 4 | Performance data (cont) | 5 | 2 | 73.8 65.1 24.9
20 | 4 | Performance data (cont) | 5 | 3 | 81.7 54.7 25.5
20 | 4 | Performance data (cont) | 5 | 4 | 90.0 44.2 26.1
20 | 4 | Performance data (cont) | 5 | 5 | 75.6 69.6 25.0
20 | 4 | Performance data (cont) | 5 | 6 | 83.5 58.5 25.7
20 | 4 | Performance data (cont) | 5 | 7 | 91.7 46.4 26.3
20 | 4 | Performance data (cont) | 5 | 8 | 77.1 74.1 25.2
20 | 4 | Performance data (cont) | 5 | 9 | 85.0 61.6 25.8
20 | 4 | Performance data (cont) | 5 | 10 | 93.5 48.4 26.5
20 | 4 | Performance data (cont) | 5 | 11 | 78.5 77.4 25.3
20 | 4 | Performance data (cont) | 5 | 12 | 86.1 65.0 25.9
20 | 4 | Performance data (cont) | 5 | 13 | 94.6 50.5 26.5
20 | 4 | Performance data (cont) | 5 | 14 | 80.9 80.6 25.5
20 | 4 | Performance data (cont) | 5 | 15 | 87.0 69.4 26.0
20 | 4 | Performance data (cont) | 6 | 1 | TC SHC kW
20 | 4 | Performance data (cont) | 6 | 2 | 70.3 63.5 27.3
20 | 4 | Performance data (cont) | 6 | 3 | 77.9 53.3 27.9
20 | 4 | Performance data (cont) | 6 | 4 | 85.6 42.7 28.5
20 | 4 | Performance data (cont) | 6 | 5 | 72.1 68.0 27.5
20 | 4 | Performance data (cont) | 6 | 6 | 79.7 57.0 28.1
20 | 4 | Performance data (cont) | 6 | 7 | 87.6 44.8 28.7
20 | 4 | Performance data (cont) | 6 | 8 | 73.8 71.8 27.7
20 | 4 | Performance data (cont) | 6 | 9 | 80.9 60.4 28.3
20 | 4 | Performance data (cont) | 6 | 10 | 88.8 47.0 28.9
20 | 4 | Performance data (cont) | 6 | 11 | 75.6 75.0 27.8
20 | 4 | Performance data (cont) | 6 | 12 | 81.7 63.5 28.3
20 | 4 | Performance data (cont) | 6 | 13 | 90.2 49.5 28.9
20 | 4 | Performance data (cont) | 6 | 14 | 77.6 77.4 28.0
20 | 4 | Performance data (cont) | 6 | 15 | 82.9 67.8 28.5
20 | 4 | Performance data (cont) | 7 | 1 | TC SHC kW
20 | 4 | Performance data (cont) | 7 | 2 | 67.0 61.8 29.9
20 | 4 | Performance data (cont) | 7 | 3 | 73.8 51.9 30.4
20 | 4 | Performance data (cont) | 7 | 4 | 81.5 41.2 31.1
20 | 4 | Performance data (cont) | 7 | 5 | 68.6 66.1 30.0
20 | 4 | Performance data (cont) | 7 | 6 | 75.6 55.4 30.6
20 | 4 | Performance data (cont) | 7 | 7 | 82.9 43.2 31.2
20 | 4 | Performance data (cont) | 7 | 8 | 70.3 69.1 30.2
20 | 4 | Performance data (cont) | 7 | 9 | 76.5 58.5 30.7
20 | 4 | Performance data (cont) | 7 | 10 | 84.1 45.3 31.3
20 | 4 | Performance data (cont) | 7 | 11 | 71.8 71.8 30.4
20 | 4 | Performance data (cont) | 7 | 12 | 77.4 61.6 30.7
20 | 4 | Performance data (cont) | 7 | 13 | 85.3 47.1 31.5
20 | 4 | Performance data (cont) | 7 | 14 | 73.8 73.8 30.6
20 | 4 | Performance data (cont) | 7 | 15 | 77.9 65.6 30.9
21 | 1 | COOLING CAPACITIES — ENGLISH | 1 | 1 | 4500/0.12
21 | 1 | COOLING CAPACITIES — ENGLISH | 1 | 2 | 5250/0.14
21 | 1 | COOLING CAPACITIES — ENGLISH | 1 | 3 | 6000/0.15
21 | 1 | COOLING CAPACITIES — ENGLISH | 1 | 4 | 6750/0.17
21 | 2 | COOLING CAPACITIES — ENGLISH | 1 | 2 | 62
21 | 2 | COOLING CAPACITIES — ENGLISH | 1 | 3 | 67
21 | 2 | COOLING CAPACITIES — ENGLISH | 1 | 4 | 72
21 | 2 | COOLING CAPACITIES — ENGLISH | 1 | 5 | 62
21 | 2 | COOLING CAPACITIES — ENGLISH | 1 | 6 | 67
21 | 2 | COOLING CAPACITIES — ENGLISH | 1 | 7 | 72
21 | 2 | COOLING CAPACITIES — ENGLISH | 1 | 8 | 62
21 | 2 | COOLING CAPACITIES — ENGLISH | 1 | 9 | 67
21 | 2 | COOLING CAPACITIES — ENGLISH | 1 | 10 | 72
21 | 2 | COOLING CAPACITIES — ENGLISH | 1 | 11 | 62
21 | 2 | COOLING CAPACITIES — ENGLISH | 1 | 12 | 67
21 | 2 | COOLING CAPACITIES — ENGLISH | 1 | 13 | 72
21 | 2 | COOLING CAPACITIES — ENGLISH | 1 | 14 | 62
21 | 2 | COOLING CAPACITIES — ENGLISH | 1 | 15 | 67
21 | 2 | COOLING CAPACITIES — ENGLISH | 2 | 1 | TC SHC kW
21 | 2 | COOLING CAPACITIES — ENGLISH | 2 | 2 | 167 142 11.3
21 | 2 | COOLING CAPACITIES — ENGLISH | 2 | 3 | 182 121 11.7
21 | 2 | COOLING CAPACITIES — ENGLISH | 2 | 4 | 200 98 13.3
21 | 2 | COOLING CAPACITIES — ENGLISH | 2 | 5 | 172 154 11.5
21 | 2 | COOLING CAPACITIES — ENGLISH | 2 | 6 | 188 129 11.9
21 | 2 | COOLING CAPACITIES — ENGLISH | 2 | 7 | 206 104 13.4
21 | 2 | COOLING CAPACITIES — ENGLISH | 2 | 8 | 177 162 11.6
21 | 2 | COOLING CAPACITIES — ENGLISH | 2 | 9 | 193 137 12.0
21 | 2 | COOLING CAPACITIES — ENGLISH | 2 | 10 | 209 109 13.5
21 | 2 | COOLING CAPACITIES — ENGLISH | 2 | 11 | 180 171 11.7
21 | 2 | COOLING CAPACITIES — ENGLISH | 2 | 12 | 195 147 12.0
21 | 2 | COOLING CAPACITIES — ENGLISH | 2 | 13 | 211 118 13.6
21 | 2 | COOLING CAPACITIES — ENGLISH | 2 | 14 | 184 180 11.7
21 | 2 | COOLING CAPACITIES — ENGLISH | 2 | 15 | 197 154 12.1
21 | 2 | COOLING CAPACITIES — ENGLISH | 3 | 1 | TC SHC kW
21 | 2 | COOLING CAPACITIES — ENGLISH | 3 | 2 | 162 139 12.7
21 | 2 | COOLING CAPACITIES — ENGLISH | 3 | 3 | 177 118 13.0
21 | 2 | COOLING CAPACITIES — ENGLISH | 3 | 4 | 193 96 14.7
21 | 2 | COOLING CAPACITIES — ENGLISH | 3 | 5 | 167 150 12.8
21 | 2 | COOLING CAPACITIES — ENGLISH | 3 | 6 | 182 126 13.2
21 | 2 | COOLING CAPACITIES — ENGLISH | 3 | 7 | 198 101 14.9
21 | 2 | COOLING CAPACITIES — ENGLISH | 3 | 8 | 171 159 12.9
21 | 2 | COOLING CAPACITIES — ENGLISH | 3 | 9 | 186 134 13.3
21 | 2 | COOLING CAPACITIES — ENGLISH | 3 | 10 | 204 107 15.0
21 | 2 | COOLING CAPACITIES — ENGLISH | 3 | 11 | 175 168 13.0
21 | 2 | COOLING CAPACITIES — ENGLISH | 3 | 12 | 189 141 13.4
21 | 2 | COOLING CAPACITIES — ENGLISH | 3 | 13 | 206 113 15.1
21 | 2 | COOLING CAPACITIES — ENGLISH | 3 | 14 | 178 176 13.1
21 | 2 | COOLING CAPACITIES — ENGLISH | 3 | 15 | 191 151 13.5
21 | 2 | COOLING CAPACITIES — ENGLISH | 4 | 1 | TC SHC kW
21 | 2 | COOLING CAPACITIES — ENGLISH | 4 | 2 | 157 137 14.1
21 | 2 | COOLING CAPACITIES — ENGLISH | 4 | 3 | 171 115 14.5
21 | 2 | COOLING CAPACITIES — ENGLISH | 4 | 4 | 188 94 16.3
21 | 2 | COOLING CAPACITIES — ENGLISH | 4 | 5 | 162 147 14.3
21 | 2 | COOLING CAPACITIES — ENGLISH | 4 | 6 | 176 124 14.6
21 | 2 | COOLING CAPACITIES — ENGLISH | 4 | 7 | 193 99 16.5
21 | 2 | COOLING CAPACITIES — ENGLISH | 4 | 8 | 165 157 14.4
21 | 2 | COOLING CAPACITIES — ENGLISH | 4 | 9 | 180 131 14.7
21 | 2 | COOLING CAPACITIES — ENGLISH | 4 | 10 | 197 103 16.6
21 | 2 | COOLING CAPACITIES — ENGLISH | 4 | 11 | 169 166 14.5
21 | 2 | COOLING CAPACITIES — ENGLISH | 4 | 12 | 182 139 14.9
21 | 2 | COOLING CAPACITIES — ENGLISH | 4 | 13 | 200 108 16.7
21 | 2 | COOLING CAPACITIES — ENGLISH | 4 | 14 | 172 172 14.6
21 | 2 | COOLING CAPACITIES — ENGLISH | 4 | 15 | 186 146 15.0
21 | 2 | COOLING CAPACITIES — ENGLISH | 5 | 1 | TC SHC kW
21 | 2 | COOLING CAPACITIES — ENGLISH | 5 | 2 | 148 130 15.7
21 | 2 | COOLING CAPACITIES — ENGLISH | 5 | 3 | 162 111 16.2
21 | 2 | COOLING CAPACITIES — ENGLISH | 5 | 4 | 177 89 18.1
21 | 2 | COOLING CAPACITIES — ENGLISH | 5 | 5 | 153 140 15.9
21 | 2 | COOLING CAPACITIES — ENGLISH | 5 | 6 | 166 119 16.3
21 | 2 | COOLING CAPACITIES — ENGLISH | 5 | 7 | 180 94 18.3
21 | 2 | COOLING CAPACITIES — ENGLISH | 5 | 8 | 156 150 16.0
21 | 2 | COOLING CAPACITIES — ENGLISH | 5 | 9 | 169 126 16.4
21 | 2 | COOLING CAPACITIES — ENGLISH | 5 | 10 | 184 99 18.4
21 | 2 | COOLING CAPACITIES — ENGLISH | 5 | 11 | 159 158 16.1
21 | 2 | COOLING CAPACITIES — ENGLISH | 5 | 12 | 172 133 16.5
21 | 2 | COOLING CAPACITIES — ENGLISH | 5 | 13 | 188 103 18.5
21 | 2 | COOLING CAPACITIES — ENGLISH | 5 | 14 | 163 163 16.2
21 | 2 | COOLING CAPACITIES — ENGLISH | 5 | 15 | 174 140 16.6
21 | 2 | COOLING CAPACITIES — ENGLISH | 6 | 1 | TC SHC kW
21 | 2 | COOLING CAPACITIES — ENGLISH | 6 | 2 | 139 125 17.4
21 | 2 | COOLING CAPACITIES — ENGLISH | 6 | 3 | 152 106 17.9
21 | 2 | COOLING CAPACITIES — ENGLISH | 6 | 4 | 166 85 18.4
21 | 2 | COOLING CAPACITIES — ENGLISH | 6 | 5 | 143 135 17.6
21 | 2 | COOLING CAPACITIES — ENGLISH | 6 | 6 | 155 113 18.0
21 | 2 | COOLING CAPACITIES — ENGLISH | 6 | 7 | 170 90 18.6
21 | 2 | COOLING CAPACITIES — ENGLISH | 6 | 8 | 146 144 17.7
21 | 2 | COOLING CAPACITIES — ENGLISH | 6 | 9 | 158 121 18.1
21 | 2 | COOLING CAPACITIES — ENGLISH | 6 | 10 | 173 94 18.7
21 | 2 | COOLING CAPACITIES — ENGLISH | 6 | 11 | 150 150 17.9
21 | 2 | COOLING CAPACITIES — ENGLISH | 6 | 12 | 161 127 18.3
21 | 2 | COOLING CAPACITIES — ENGLISH | 6 | 13 | 174 98 18.7
21 | 2 | COOLING CAPACITIES — ENGLISH | 6 | 14 | 153 154 18.0
21 | 2 | COOLING CAPACITIES — ENGLISH | 6 | 15 | 163 134 18.3
21 | 2 | COOLING CAPACITIES — ENGLISH | 7 | 1 | TC SHC kW
21 | 2 | COOLING CAPACITIES — ENGLISH | 7 | 2 | 133 121 18.4
21 | 2 | COOLING CAPACITIES — ENGLISH | 7 | 3 | 145 102 18.9
21 | 2 | COOLING CAPACITIES — ENGLISH | 7 | 4 | 159 82 19.4
21 | 2 | COOLING CAPACITIES — ENGLISH | 7 | 5 | 136 131 18.5
21 | 2 | COOLING CAPACITIES — ENGLISH | 7 | 6 | 148 110 19.0
21 | 2 | COOLING CAPACITIES — ENGLISH | 7 | 7 | 163 86 19.6
21 | 2 | COOLING CAPACITIES — ENGLISH | 7 | 8 | 140 139 18.7
21 | 2 | COOLING CAPACITIES — ENGLISH | 7 | 9 | 151 117 19.1
21 | 2 | COOLING CAPACITIES — ENGLISH | 7 | 10 | 165 91 19.8
21 | 2 | COOLING CAPACITIES — ENGLISH | 7 | 11 | 143 144 18.8
21 | 2 | COOLING CAPACITIES — ENGLISH | 7 | 12 | 154 124 19.2
21 | 2 | COOLING CAPACITIES — ENGLISH | 7 | 13 | 166 95 19.8
21 | 2 | COOLING CAPACITIES — ENGLISH | 7 | 14 | 147 148 18.9
21 | 2 | COOLING CAPACITIES — ENGLISH | 7 | 15 | 155 129 19.3
21 | 2 | COOLING CAPACITIES — ENGLISH | 8 | 1 | TC SHC kW
21 | 2 | COOLING CAPACITIES — ENGLISH | 8 | 2 | 127 117 19.3
21 | 2 | COOLING CAPACITIES — ENGLISH | 8 | 3 | 138 99 19.7
21 | 2 | COOLING CAPACITIES — ENGLISH | 8 | 4 | 151 81 20.3
21 | 2 | COOLING CAPACITIES — ENGLISH | 8 | 5 | 130 126 19.4
21 | 2 | COOLING CAPACITIES — ENGLISH | 8 | 6 | 141 106 19.9
21 | 2 | COOLING CAPACITIES — ENGLISH | 8 | 7 | — — —
21 | 2 | COOLING CAPACITIES — ENGLISH | 8 | 8 | 134 134 19.6
21 | 2 | COOLING CAPACITIES — ENGLISH | 8 | 9 | 144 113 20.1
21 | 2 | COOLING CAPACITIES — ENGLISH | 8 | 10 | — — —
21 | 2 | COOLING CAPACITIES — ENGLISH | 8 | 11 | 137 138 19.7
21 | 2 | COOLING CAPACITIES — ENGLISH | 8 | 12 | 146 119 20.1
21 | 2 | COOLING CAPACITIES — ENGLISH | 8 | 13 | — — —
21 | 2 | COOLING CAPACITIES — ENGLISH | 8 | 14 | 140 142 19.9
21 | 2 | COOLING CAPACITIES — ENGLISH | 8 | 15 | 148 125 20.1
21 | 3 | COOLING CAPACITIES — ENGLISH | 1 | 1 | 6000/0.075
21 | 3 | COOLING CAPACITIES — ENGLISH | 1 | 2 | 7000/0.085
21 | 3 | COOLING CAPACITIES — ENGLISH | 1 | 3 | 8000/0.10
21 | 3 | COOLING CAPACITIES — ENGLISH | 1 | 4 | 9000/0.11
21 | 4 | COOLING CAPACITIES — ENGLISH | 1 | 2 | 62
21 | 4 | COOLING CAPACITIES — ENGLISH | 1 | 3 | 67
21 | 4 | COOLING CAPACITIES — ENGLISH | 1 | 4 | 72
21 | 4 | COOLING CAPACITIES — ENGLISH | 1 | 5 | 62
21 | 4 | COOLING CAPACITIES — ENGLISH | 1 | 6 | 67
21 | 4 | COOLING CAPACITIES — ENGLISH | 1 | 7 | 72
21 | 4 | COOLING CAPACITIES — ENGLISH | 1 | 8 | 62
21 | 4 | COOLING CAPACITIES — ENGLISH | 1 | 9 | 67
21 | 4 | COOLING CAPACITIES — ENGLISH | 1 | 10 | 72
21 | 4 | COOLING CAPACITIES — ENGLISH | 1 | 11 | 62
21 | 4 | COOLING CAPACITIES — ENGLISH | 1 | 12 | 67
21 | 4 | COOLING CAPACITIES — ENGLISH | 1 | 13 | 72
21 | 4 | COOLING CAPACITIES — ENGLISH | 1 | 14 | 62
21 | 4 | COOLING CAPACITIES — ENGLISH | 1 | 15 | 67
21 | 4 | COOLING CAPACITIES — ENGLISH | 2 | 1 | TC SHC kW
21 | 4 | COOLING CAPACITIES — ENGLISH | 2 | 2 | 219.5 188.0 15.1
21 | 4 | COOLING CAPACITIES — ENGLISH | 2 | 3 | 242.0 158.6 15.6
21 | 4 | COOLING CAPACITIES — ENGLISH | 2 | 4 | 262.6 125.9 16.5
21 | 4 | COOLING CAPACITIES — ENGLISH | 2 | 5 | 224.9 203.2 15.2
21 | 4 | COOLING CAPACITIES — ENGLISH | 2 | 6 | 248.0 169.6 15.8
21 | 4 | COOLING CAPACITIES — ENGLISH | 2 | 7 | 268.8 132.7 16.7
21 | 4 | COOLING CAPACITIES — ENGLISH | 2 | 8 | 229.2 217.0 15.4
21 | 4 | COOLING CAPACITIES — ENGLISH | 2 | 9 | 252.8 180.7 15.9
21 | 4 | COOLING CAPACITIES — ENGLISH | 2 | 10 | 274.0 139.3 16.9
21 | 4 | COOLING CAPACITIES — ENGLISH | 2 | 11 | 233.3 229.5 15.5
21 | 4 | COOLING CAPACITIES — ENGLISH | 2 | 12 | 256.1 191.1 16.0
21 | 4 | COOLING CAPACITIES — ENGLISH | 2 | 13 | 277.5 146.1 17.0
21 | 4 | COOLING CAPACITIES — ENGLISH | 2 | 14 | 238.0 237.6 15.7
21 | 4 | COOLING CAPACITIES — ENGLISH | 2 | 15 | 258.8 201.7 16.1
21 | 4 | COOLING CAPACITIES — ENGLISH | 3 | 1 | TC SHC kW
21 | 4 | COOLING CAPACITIES — ENGLISH | 3 | 2 | 211.9 184.5 16.7
21 | 4 | COOLING CAPACITIES — ENGLISH | 3 | 3 | 233.6 154.9 17.2
21 | 4 | COOLING CAPACITIES — ENGLISH | 3 | 4 | 253.5 122.7 18.2
21 | 4 | COOLING CAPACITIES — ENGLISH | 3 | 5 | 217.1 199.3 16.9
21 | 4 | COOLING CAPACITIES — ENGLISH | 3 | 6 | 239.6 166.7 17.4
21 | 4 | COOLING CAPACITIES — ENGLISH | 3 | 7 | 259.8 129.6 18.5
21 | 4 | COOLING CAPACITIES — ENGLISH | 3 | 8 | 221.4 212.9 17.0
21 | 4 | COOLING CAPACITIES — ENGLISH | 3 | 9 | 243.8 177.0 17.6
21 | 4 | COOLING CAPACITIES — ENGLISH | 3 | 10 | 264.6 136.1 18.6
21 | 4 | COOLING CAPACITIES — ENGLISH | 3 | 11 | 225.2 224.0 17.2
21 | 4 | COOLING CAPACITIES — ENGLISH | 3 | 12 | 246.8 187.2 17.7
21 | 4 | COOLING CAPACITIES — ENGLISH | 3 | 13 | 267.9 142.3 18.7
21 | 4 | COOLING CAPACITIES — ENGLISH | 3 | 14 | 231.3 230.7 17.4
21 | 4 | COOLING CAPACITIES — ENGLISH | 3 | 15 | 249.5 197.6 17.8
21 | 4 | COOLING CAPACITIES — ENGLISH | 4 | 1 | TC SHC kW
21 | 4 | COOLING CAPACITIES — ENGLISH | 4 | 2 | 204.1 180.8 18.5
21 | 4 | COOLING CAPACITIES — ENGLISH | 4 | 3 | 224.9 151.7 19.0
21 | 4 | COOLING CAPACITIES — ENGLISH | 4 | 4 | 244.2 119.4 20.1
21 | 4 | COOLING CAPACITIES — ENGLISH | 4 | 5 | 208.8 194.9 18.7
21 | 4 | COOLING CAPACITIES — ENGLISH | 4 | 6 | 229.9 162.7 19.2
21 | 4 | COOLING CAPACITIES — ENGLISH | 4 | 7 | 249.8 126.3 20.3
21 | 4 | COOLING CAPACITIES — ENGLISH | 4 | 8 | 213.0 208.3 18.8
21 | 4 | COOLING CAPACITIES — ENGLISH | 4 | 9 | 234.0 173.2 19.3
21 | 4 | COOLING CAPACITIES — ENGLISH | 4 | 10 | 253.9 132.7 20.4
21 | 4 | COOLING CAPACITIES — ENGLISH | 4 | 11 | 217.6 217.2 19.0
21 | 4 | COOLING CAPACITIES — ENGLISH | 4 | 12 | 236.8 183.0 19.4
21 | 4 | COOLING CAPACITIES — ENGLISH | 4 | 13 | 256.9 138.7 20.5
21 | 4 | COOLING CAPACITIES — ENGLISH | 4 | 14 | 222.9 222.4 19.1
21 | 4 | COOLING CAPACITIES — ENGLISH | 4 | 15 | 239.1 193.4 19.5
21 | 4 | COOLING CAPACITIES — ENGLISH | 5 | 1 | TC SHC kW
21 | 4 | COOLING CAPACITIES — ENGLISH | 5 | 2 | 194.5 176.2 20.3
21 | 4 | COOLING CAPACITIES — ENGLISH | 5 | 3 | 215.0 147.8 20.8
21 | 4 | COOLING CAPACITIES — ENGLISH | 5 | 4 | 233.7 115.7 22.0
21 | 4 | COOLING CAPACITIES — ENGLISH | 5 | 5 | 199.5 190.4 20.5
21 | 4 | COOLING CAPACITIES — ENGLISH | 5 | 6 | 219.8 158.7 21.0
21 | 4 | COOLING CAPACITIES — ENGLISH | 5 | 7 | 238.9 122.5 22.2
21 | 4 | COOLING CAPACITIES — ENGLISH | 5 | 8 | 203.8 202.5 20.6
21 | 4 | COOLING CAPACITIES — ENGLISH | 5 | 9 | 223.0 168.7 21.1
21 | 4 | COOLING CAPACITIES — ENGLISH | 5 | 10 | 242.7 128.8 22.3
21 | 4 | COOLING CAPACITIES — ENGLISH | 5 | 11 | 209.6 209.3 20.8
21 | 4 | COOLING CAPACITIES — ENGLISH | 5 | 12 | 225.6 179.6 21.2
21 | 4 | COOLING CAPACITIES — ENGLISH | 5 | 13 | 245.5 134.9 22.4
21 | 4 | COOLING CAPACITIES — ENGLISH | 5 | 14 | 214.3 213.8 21.0
21 | 4 | COOLING CAPACITIES — ENGLISH | 5 | 15 | 227.6 189.0 21.3
21 | 4 | COOLING CAPACITIES — ENGLISH | 6 | 1 | TC SHC kW
21 | 4 | COOLING CAPACITIES — ENGLISH | 6 | 2 | 185.1 171.5 22.1
21 | 4 | COOLING CAPACITIES — ENGLISH | 6 | 3 | 204.6 143.3 22.7
21 | 4 | COOLING CAPACITIES — ENGLISH | 6 | 4 | 222.6 111.9 23.9
21 | 4 | COOLING CAPACITIES — ENGLISH | 6 | 5 | 189.8 185.2 22.3
21 | 4 | COOLING CAPACITIES — ENGLISH | 6 | 6 | 208.9 154.7 22.8
21 | 4 | COOLING CAPACITIES — ENGLISH | 6 | 7 | 227.3 118.5 24.1
21 | 4 | COOLING CAPACITIES — ENGLISH | 6 | 8 | 194.8 194.3 22.5
21 | 4 | COOLING CAPACITIES — ENGLISH | 6 | 9 | 211.8 164.9 23.0
21 | 4 | COOLING CAPACITIES — ENGLISH | 6 | 10 | 230.6 124.5 24.2
21 | 4 | COOLING CAPACITIES — ENGLISH | 6 | 11 | 200.4 199.9 22.7
21 | 4 | COOLING CAPACITIES — ENGLISH | 6 | 12 | 214.0 174.3 23.1
21 | 4 | COOLING CAPACITIES — ENGLISH | 6 | 13 | 233.2 130.7 24.3
21 | 4 | COOLING CAPACITIES — ENGLISH | 6 | 14 | 204.6 204.2 22.9
21 | 4 | COOLING CAPACITIES — ENGLISH | 6 | 15 | 215.8 183.3 23.2
21 | 4 | COOLING CAPACITIES — ENGLISH | 7 | 1 | TC SHC kW
21 | 4 | COOLING CAPACITIES — ENGLISH | 7 | 2 | 174.9 166.2 24.0
21 | 4 | COOLING CAPACITIES — ENGLISH | 7 | 3 | 193.1 138.7 24.6
21 | 4 | COOLING CAPACITIES — ENGLISH | 7 | 4 | — — —
21 | 4 | COOLING CAPACITIES — ENGLISH | 7 | 5 | 179.9 178.5 24.2
21 | 4 | COOLING CAPACITIES — ENGLISH | 7 | 6 | 196.7 149.5 24.7
21 | 4 | COOLING CAPACITIES — ENGLISH | 7 | 7 | — — —
21 | 4 | COOLING CAPACITIES — ENGLISH | 7 | 8 | 185.3 184.9 24.4
21 | 4 | COOLING CAPACITIES — ENGLISH | 7 | 9 | 199.5 160.3 24.9
21 | 4 | COOLING CAPACITIES — ENGLISH | 7 | 10 | — — —
21 | 4 | COOLING CAPACITIES — ENGLISH | 7 | 11 | 190.6 190.2 24.6
21 | 4 | COOLING CAPACITIES — ENGLISH | 7 | 12 | 201.4 169.4 25.0
21 | 4 | COOLING CAPACITIES — ENGLISH | 7 | 13 | — — —
21 | 4 | COOLING CAPACITIES — ENGLISH | 7 | 14 | 194.7 194.0 24.8
21 | 4 | COOLING CAPACITIES — ENGLISH | 7 | 15 | 202.8 177.7 25.0
22 | 1 | Performance data (cont) | 1 | 1 | 7000/0.05
22 | 1 | Performance data (cont) | 1 | 2 | 8000/0.06
22 | 1 | Performance data (cont) | 1 | 3 | 9000/0.07
22 | 1 | Performance data (cont) | 1 | 4 | 10,000/0.08
22 | 2 | Performance data (cont) | 1 | 2 | 62
22 | 2 | Performance data (cont) | 1 | 3 | 67
22 | 2 | Performance data (cont) | 1 | 4 | 72
22 | 2 | Performance data (cont) | 1 | 5 | 62
22 | 2 | Performance data (cont) | 1 | 6 | 67
22 | 2 | Performance data (cont) | 1 | 7 | 72
22 | 2 | Performance data (cont) | 1 | 8 | 62
22 | 2 | Performance data (cont) | 1 | 9 | 67
22 | 2 | Performance data (cont) | 1 | 10 | 72
22 | 2 | Performance data (cont) | 1 | 11 | 62
22 | 2 | Performance data (cont) | 1 | 12 | 67
22 | 2 | Performance data (cont) | 1 | 13 | 72
22 | 2 | Performance data (cont) | 1 | 14 | 62
22 | 2 | Performance data (cont) | 1 | 15 | 67
22 | 2 | Performance data (cont) | 2 | 1 | TC SHC kW
22 | 2 | Performance data (cont) | 2 | 2 | 270.9 231.2 20.1
22 | 2 | Performance data (cont) | 2 | 3 | 298.9 195.1 20.8
22 | 2 | Performance data (cont) | 2 | 4 | 329.5 158.8 21.6
22 | 2 | Performance data (cont) | 2 | 5 | 277.1 247.7 20.3
22 | 2 | Performance data (cont) | 2 | 6 | 305.7 207.1 21.0
22 | 2 | Performance data (cont) | 2 | 7 | 336.5 165.1 21.8
22 | 2 | Performance data (cont) | 2 | 8 | 282.2 264.4 20.4
22 | 2 | Performance data (cont) | 2 | 9 | 310.5 219.8 21.2
22 | 2 | Performance data (cont) | 2 | 10 | 342.2 174.6 22.0
22 | 2 | Performance data (cont) | 2 | 11 | 286.2 278.8 20.6
22 | 2 | Performance data (cont) | 2 | 12 | 313.6 234.5 21.3
22 | 2 | Performance data (cont) | 2 | 13 | 346.8 181.9 22.2
22 | 2 | Performance data (cont) | 2 | 14 | 292.5 292.1 20.8
22 | 2 | Performance data (cont) | 2 | 15 | 318.6 247.9 21.5
22 | 2 | Performance data (cont) | 3 | 1 | TC SHC kW
22 | 2 | Performance data (cont) | 3 | 2 | 261.5 226.8 22.2
22 | 2 | Performance data (cont) | 3 | 3 | 288.5 190.8 23.0
22 | 2 | Performance data (cont) | 3 | 4 | 317.7 153.6 23.8
22 | 2 | Performance data (cont) | 3 | 5 | 267.1 243.1 22.4
22 | 2 | Performance data (cont) | 3 | 6 | 295.0 202.9 23.2
22 | 2 | Performance data (cont) | 3 | 7 | 324.2 161.9 24.0
22 | 2 | Performance data (cont) | 3 | 8 | 272.5 257.9 22.6
22 | 2 | Performance data (cont) | 3 | 9 | 300.2 214.6 23.4
22 | 2 | Performance data (cont) | 3 | 10 | 329.8 168.8 24.2
22 | 2 | Performance data (cont) | 3 | 11 | 276.5 272.2 22.8
22 | 2 | Performance data (cont) | 3 | 12 | 304.2 226.7 23.5
22 | 2 | Performance data (cont) | 3 | 13 | 334.8 176.0 24.4
22 | 2 | Performance data (cont) | 3 | 14 | 283.5 283.3 23.0
22 | 2 | Performance data (cont) | 3 | 15 | 308.4 240.5 23.7
22 | 2 | Performance data (cont) | 4 | 1 | TC SHC kW
22 | 2 | Performance data (cont) | 4 | 2 | 251.5 221.8 24.6
22 | 2 | Performance data (cont) | 4 | 3 | 277.2 186.4 25.3
22 | 2 | Performance data (cont) | 4 | 4 | 305.1 150.1 26.1
22 | 2 | Performance data (cont) | 4 | 5 | 256.6 237.9 24.7
22 | 2 | Performance data (cont) | 4 | 6 | 283.3 198.3 25.5
22 | 2 | Performance data (cont) | 4 | 7 | 311.0 157.1 26.3
22 | 2 | Performance data (cont) | 4 | 8 | 261.9 252.7 24.9
22 | 2 | Performance data (cont) | 4 | 9 | 287.3 211.0 25.7
22 | 2 | Performance data (cont) | 4 | 10 | 316.5 164.2 26.5
22 | 2 | Performance data (cont) | 4 | 11 | 266.4 265.2 25.1
22 | 2 | Performance data (cont) | 4 | 12 | 291.9 221.3 25.8
22 | 2 | Performance data (cont) | 4 | 13 | 320.8 171.0 26.7
22 | 2 | Performance data (cont) | 4 | 14 | 274.0 273.7 25.4
22 | 2 | Performance data (cont) | 4 | 15 | 295.4 235.0 26.0
22 | 2 | Performance data (cont) | 5 | 1 | TC SHC kW
22 | 2 | Performance data (cont) | 5 | 2 | 240.6 215.9 27.0
22 | 2 | Performance data (cont) | 5 | 3 | 265.7 181.8 27.8
22 | 2 | Performance data (cont) | 5 | 4 | 291.4 145.2 28.6
22 | 2 | Performance data (cont) | 5 | 5 | 245.5 231.9 27.2
22 | 2 | Performance data (cont) | 5 | 6 | 270.5 192.9 28.0
22 | 2 | Performance data (cont) | 5 | 7 | 297.8 152.5 28.8
22 | 2 | Performance data (cont) | 5 | 8 | 250.7 245.8 27.4
22 | 2 | Performance data (cont) | 5 | 9 | 274.6 205.0 28.1
22 | 2 | Performance data (cont) | 5 | 10 | 302.2 159.2 29.0
22 | 2 | Performance data (cont) | 5 | 11 | 256.0 255.9 27.6
22 | 2 | Performance data (cont) | 5 | 12 | 277.9 216.1 28.3
22 | 2 | Performance data (cont) | 5 | 13 | 305.7 166.5 29.2
22 | 2 | Performance data (cont) | 5 | 14 | 263.4 263.2 27.9
22 | 2 | Performance data (cont) | 5 | 15 | 281.4 229.5 28.4
22 | 2 | Performance data (cont) | 6 | 1 | TC SHC kW
22 | 2 | Performance data (cont) | 6 | 2 | 229.0 211.2 29.5
22 | 2 | Performance data (cont) | 6 | 3 | 252.4 176.8 30.3
22 | 2 | Performance data (cont) | 6 | 4 | 277.3 140.0 31.1
22 | 2 | Performance data (cont) | 6 | 5 | 233.5 225.9 29.7
22 | 2 | Performance data (cont) | 6 | 6 | 256.9 187.6 30.5
22 | 2 | Performance data (cont) | 6 | 7 | 281.5 147.1 31.3
22 | 2 | Performance data (cont) | 6 | 8 | 239.0 238.3 30.0
22 | 2 | Performance data (cont) | 6 | 9 | 260.6 199.4 30.7
22 | 2 | Performance data (cont) | 6 | 10 | 285.4 153.4 31.5
22 | 2 | Performance data (cont) | 6 | 11 | 245.2 245.0 30.2
22 | 2 | Performance data (cont) | 6 | 12 | 263.7 210.6 30.8
22 | 2 | Performance data (cont) | 6 | 13 | — — —
22 | 2 | Performance data (cont) | 6 | 14 | 252.0 251.9 30.5
22 | 2 | Performance data (cont) | 6 | 15 | 267.0 223.2 31.0
22 | 2 | Performance data (cont) | 7 | 1 | TC SHC kW
22 | 2 | Performance data (cont) | 7 | 2 | 225.6 209.6 30.3
22 | 2 | Performance data (cont) | 7 | 3 | 248.0 175.1 31.1
22 | 2 | Performance data (cont) | 7 | 4 | — — —
22 | 2 | Performance data (cont) | 7 | 5 | 230.0 223.9 30.5
22 | 2 | Performance data (cont) | 7 | 6 | 252.3 186.0 31.2
22 | 2 | Performance data (cont) | 7 | 7 | — — —
22 | 2 | Performance data (cont) | 7 | 8 | 235.1 234.7 30.7
22 | 2 | Performance data (cont) | 7 | 9 | 255.3 197.4 31.4
22 | 2 | Performance data (cont) | 7 | 10 | — — —
22 | 2 | Performance data (cont) | 7 | 11 | 240.9 240.5 31.0
22 | 2 | Performance data (cont) | 7 | 12 | 257.5 208.6 31.5
22 | 2 | Performance data (cont) | 7 | 13 | — — —
22 | 2 | Performance data (cont) | 7 | 14 | 247.2 247.1 31.2
22 | 2 | Performance data (cont) | 7 | 15 | — — —
22 | 2 | Performance data (cont) | 8 | 1 | TC SHC kW
22 | 2 | Performance data (cont) | 8 | 2 | 222.6 208.0 30.8
22 | 2 | Performance data (cont) | 8 | 3 | — — —
22 | 2 | Performance data (cont) | 8 | 4 | — — —
22 | 2 | Performance data (cont) | 8 | 5 | 227.4 222.5 31.0
22 | 2 | Performance data (cont) | 8 | 6 | — — —
22 | 2 | Performance data (cont) | 8 | 7 | — — —
22 | 2 | Performance data (cont) | 8 | 8 | 233.6 233.3 31.3
22 | 2 | Performance data (cont) | 8 | 9 | — — —
22 | 2 | Performance data (cont) | 8 | 10 | — — —
22 | 2 | Performance data (cont) | 8 | 11 | 239.0 239.0 31.5
22 | 2 | Performance data (cont) | 8 | 12 | — — —
22 | 2 | Performance data (cont) | 8 | 13 | — — —
22 | 2 | Performance data (cont) | 8 | 14 | — — —
22 | 2 | Performance data (cont) | 8 | 15 | — — —
22 | 3 | Performance data (cont) | 1 | 1 | 7000/0.05
22 | 3 | Performance data (cont) | 1 | 2 | 8000/0.06
22 | 3 | Performance data (cont) | 1 | 3 | 9000/0.07
22 | 3 | Performance data (cont) | 1 | 4 | 10,000/0.08
22 | 4 | Performance data (cont) | 1 | 2 | 62
22 | 4 | Performance data (cont) | 1 | 3 | 67
22 | 4 | Performance data (cont) | 1 | 4 | 72
22 | 4 | Performance data (cont) | 1 | 5 | 62
22 | 4 | Performance data (cont) | 1 | 6 | 67
22 | 4 | Performance data (cont) | 1 | 7 | 72
22 | 4 | Performance data (cont) | 1 | 8 | 62
22 | 4 | Performance data (cont) | 1 | 9 | 67
22 | 4 | Performance data (cont) | 1 | 10 | 72
22 | 4 | Performance data (cont) | 1 | 11 | 62
22 | 4 | Performance data (cont) | 1 | 12 | 67
22 | 4 | Performance data (cont) | 1 | 13 | 72
22 | 4 | Performance data (cont) | 1 | 14 | 62
22 | 4 | Performance data (cont) | 1 | 15 | 67
22 | 4 | Performance data (cont) | 2 | 1 | TC SHC kW
22 | 4 | Performance data (cont) | 2 | 2 | 281 236 18.2
22 | 4 | Performance data (cont) | 2 | 3 | 310 201 18.8
22 | 4 | Performance data (cont) | 2 | 4 | 343 163 19.4
22 | 4 | Performance data (cont) | 2 | 5 | 288 253 18.4
22 | 4 | Performance data (cont) | 2 | 6 | 318 214 19.0
22 | 4 | Performance data (cont) | 2 | 7 | 351 172 19.6
22 | 4 | Performance data (cont) | 2 | 8 | 292 272 18.5
22 | 4 | Performance data (cont) | 2 | 9 | 323 228 19.1
22 | 4 | Performance data (cont) | 2 | 10 | 355 185 19.7
22 | 4 | Performance data (cont) | 2 | 11 | 298 284 18.6
22 | 4 | Performance data (cont) | 2 | 12 | 327 240 19.2
22 | 4 | Performance data (cont) | 2 | 13 | 361 193 19.9
22 | 4 | Performance data (cont) | 2 | 14 | 304 300 18.8
22 | 4 | Performance data (cont) | 2 | 15 | 332 257 19.4
22 | 4 | Performance data (cont) | 3 | 1 | TC SHC kW
22 | 4 | Performance data (cont) | 3 | 2 | 272 232 20.3
22 | 4 | Performance data (cont) | 3 | 3 | 300 196 20.8
22 | 4 | Performance data (cont) | 3 | 4 | 332 159 21.5
22 | 4 | Performance data (cont) | 3 | 5 | 279 249 20.4
22 | 4 | Performance data (cont) | 3 | 6 | 309 209 21.0
22 | 4 | Performance data (cont) | 3 | 7 | 340 168 21.7
22 | 4 | Performance data (cont) | 3 | 8 | 284 265 20.6
22 | 4 | Performance data (cont) | 3 | 9 | 314 222 21.2
22 | 4 | Performance data (cont) | 3 | 10 | 347 176 21.8
22 | 4 | Performance data (cont) | 3 | 11 | 289 279 20.8
22 | 4 | Performance data (cont) | 3 | 12 | 318 232 21.4
22 | 4 | Performance data (cont) | 3 | 13 | 351 183 22.0
22 | 4 | Performance data (cont) | 3 | 14 | 296 293 20.9
22 | 4 | Performance data (cont) | 3 | 15 | 322 250 21.4
22 | 4 | Performance data (cont) | 4 | 1 | TC SHC kW
22 | 4 | Performance data (cont) | 4 | 2 | 262 227 22.6
22 | 4 | Performance data (cont) | 4 | 3 | 291 192 23.1
22 | 4 | Performance data (cont) | 4 | 4 | 320 156 23.7
22 | 4 | Performance data (cont) | 4 | 5 | 268 244 22.6
22 | 4 | Performance data (cont) | 4 | 6 | 297 204 23.3
22 | 4 | Performance data (cont) | 4 | 7 | 327 163 23.9
22 | 4 | Performance data (cont) | 4 | 8 | 274 258 22.8
22 | 4 | Performance data (cont) | 4 | 9 | 302 216 23.4
22 | 4 | Performance data (cont) | 4 | 10 | 333 170 24.1
22 | 4 | Performance data (cont) | 4 | 11 | 279 271 23.0
22 | 4 | Performance data (cont) | 4 | 12 | 307 227 23.6
22 | 4 | Performance data (cont) | 4 | 13 | 338 178 24.2
22 | 4 | Performance data (cont) | 4 | 14 | 285 283 23.1
22 | 4 | Performance data (cont) | 4 | 15 | 311 241 23.6
22 | 4 | Performance data (cont) | 5 | 1 | TC SHC kW
22 | 4 | Performance data (cont) | 5 | 2 | 252 222 24.9
22 | 4 | Performance data (cont) | 5 | 3 | 279 187 25.5
22 | 4 | Performance data (cont) | 5 | 4 | 307 151 26.1
22 | 4 | Performance data (cont) | 5 | 5 | 258 238 25.0
22 | 4 | Performance data (cont) | 5 | 6 | 285 200 25.7
22 | 4 | Performance data (cont) | 5 | 7 | 313 158 26.3
22 | 4 | Performance data (cont) | 5 | 8 | 263 253 25.2
22 | 4 | Performance data (cont) | 5 | 9 | 290 210 25.8
22 | 4 | Performance data (cont) | 5 | 10 | 319 165 26.5
22 | 4 | Performance data (cont) | 5 | 11 | 268 264 25.3
22 | 4 | Performance data (cont) | 5 | 12 | 294 222 25.9
22 | 4 | Performance data (cont) | 5 | 13 | 323 172 26.5
22 | 4 | Performance data (cont) | 5 | 14 | 276 275 25.5
22 | 4 | Performance data (cont) | 5 | 15 | 297 237 26.0
22 | 4 | Performance data (cont) | 6 | 1 | TC SHC kW
22 | 4 | Performance data (cont) | 6 | 2 | 240 217 27.3
22 | 4 | Performance data (cont) | 6 | 3 | 266 182 27.9
22 | 4 | Performance data (cont) | 6 | 4 | 292 146 28.5
22 | 4 | Performance data (cont) | 6 | 5 | 246 232 27.5
22 | 4 | Performance data (cont) | 6 | 6 | 272 194 28.1
22 | 4 | Performance data (cont) | 6 | 7 | 299 153 28.7
22 | 4 | Performance data (cont) | 6 | 8 | 252 245 27.7
22 | 4 | Performance data (cont) | 6 | 9 | 276 206 28.3
22 | 4 | Performance data (cont) | 6 | 10 | 303 160 28.9
22 | 4 | Performance data (cont) | 6 | 11 | 258 256 27.8
22 | 4 | Performance data (cont) | 6 | 12 | 279 217 28.3
22 | 4 | Performance data (cont) | 6 | 13 | 308 169 28.9
22 | 4 | Performance data (cont) | 6 | 14 | 265 264 28.0
22 | 4 | Performance data (cont) | 6 | 15 | 283 231 28.5
22 | 4 | Performance data (cont) | 7 | 1 | TC SHC kW
22 | 4 | Performance data (cont) | 7 | 2 | 229 211 29.9
22 | 4 | Performance data (cont) | 7 | 3 | 252 177 30.4
22 | 4 | Performance data (cont) | 7 | 4 | 278 141 31.1
22 | 4 | Performance data (cont) | 7 | 5 | 234 226 30.0
22 | 4 | Performance data (cont) | 7 | 6 | 258 189 30.6
22 | 4 | Performance data (cont) | 7 | 7 | 283 148 31.2
22 | 4 | Performance data (cont) | 7 | 8 | 240 236 30.2
22 | 4 | Performance data (cont) | 7 | 9 | 261 200 30.7
22 | 4 | Performance data (cont) | 7 | 10 | 287 155 31.3
22 | 4 | Performance data (cont) | 7 | 11 | 245 245 30.4
22 | 4 | Performance data (cont) | 7 | 12 | 264 210 30.7
22 | 4 | Performance data (cont) | 7 | 13 | 291 161 31.5
22 | 4 | Performance data (cont) | 7 | 14 | 252 252 30.6
22 | 4 | Performance data (cont) | 7 | 15 | 266 224 30.9
23 | 1 | GLYCOL HEATING PERFORMANCE | 1 | 1 | 4400
23 | 1 | GLYCOL HEATING PERFORMANCE | 1 | 2 | 5400
23 | 2 | GLYCOL HEATING PERFORMANCE | 1 | 2 | 25
23 | 2 | GLYCOL HEATING PERFORMANCE | 1 | 5 | 50
23 | 2 | GLYCOL HEATING PERFORMANCE | 1 | 8 | 25
23 | 2 | GLYCOL HEATING PERFORMANCE | 1 | 11 | 50
23 | 2 | GLYCOL HEATING PERFORMANCE | 1 | 14 | 25
23 | 2 | GLYCOL HEATING PERFORMANCE | 2 | 1 | Ewt
23 | 2 | GLYCOL HEATING PERFORMANCE | 2 | 2 | Cap
23 | 2 | GLYCOL HEATING PERFORMANCE | 2 | 3 | Gpm
23 | 2 | GLYCOL HEATING PERFORMANCE | 2 | 4 | Ldb
23 | 2 | GLYCOL HEATING PERFORMANCE | 2 | 5 | Cap
23 | 2 | GLYCOL HEATING PERFORMANCE | 2 | 6 | Gpm
23 | 2 | GLYCOL HEATING PERFORMANCE | 2 | 7 | Ldb
23 | 2 | GLYCOL HEATING PERFORMANCE | 2 | 8 | Cap
23 | 2 | GLYCOL HEATING PERFORMANCE | 2 | 9 | Gpm
23 | 2 | GLYCOL HEATING PERFORMANCE | 2 | 10 | Ldb
23 | 2 | GLYCOL HEATING PERFORMANCE | 2 | 11 | Cap
23 | 2 | GLYCOL HEATING PERFORMANCE | 2 | 12 | Gpm
23 | 2 | GLYCOL HEATING PERFORMANCE | 2 | 13 | Ldb
23 | 2 | GLYCOL HEATING PERFORMANCE | 2 | 14 | Cap
23 | 2 | GLYCOL HEATING PERFORMANCE | 2 | 15 | Gpm
23 | 2 | GLYCOL HEATING PERFORMANCE | 2 | 16 | Ldb
23 | 2 | GLYCOL HEATING PERFORMANCE | 2 | 17 | Cap
23 | 2 | GLYCOL HEATING PERFORMANCE | 2 | 18 | Gpm
23 | 2 | GLYCOL HEATING PERFORMANCE | 3 | 1 | 200
23 | 2 | GLYCOL HEATING PERFORMANCE | 3 | 2 | 310
23 | 2 | GLYCOL HEATING PERFORMANCE | 3 | 3 | 33
23 | 2 | GLYCOL HEATING PERFORMANCE | 3 | 4 | 120
23 | 2 | GLYCOL HEATING PERFORMANCE | 3 | 5 | 293
23 | 2 | GLYCOL HEATING PERFORMANCE | 3 | 6 | 33
23 | 2 | GLYCOL HEATING PERFORMANCE | 3 | 7 | 116
23 | 2 | GLYCOL HEATING PERFORMANCE | 3 | 8 | 347
23 | 2 | GLYCOL HEATING PERFORMANCE | 3 | 9 | 37
23 | 2 | GLYCOL HEATING PERFORMANCE | 3 | 10 | 115
23 | 2 | GLYCOL HEATING PERFORMANCE | 3 | 11 | 327
23 | 2 | GLYCOL HEATING PERFORMANCE | 3 | 12 | 37
23 | 2 | GLYCOL HEATING PERFORMANCE | 3 | 13 | 111
23 | 2 | GLYCOL HEATING PERFORMANCE | 3 | 14 | 405
23 | 2 | GLYCOL HEATING PERFORMANCE | 3 | 15 | 43
23 | 2 | GLYCOL HEATING PERFORMANCE | 3 | 16 | 107
23 | 2 | GLYCOL HEATING PERFORMANCE | 3 | 17 | 381
23 | 2 | GLYCOL HEATING PERFORMANCE | 3 | 18 | 43
23 | 2 | GLYCOL HEATING PERFORMANCE | 4 | 1 | 180
23 | 2 | GLYCOL HEATING PERFORMANCE | 4 | 2 | 255
23 | 2 | GLYCOL HEATING PERFORMANCE | 4 | 3 | 27
23 | 2 | GLYCOL HEATING PERFORMANCE | 4 | 4 | 108
23 | 2 | GLYCOL HEATING PERFORMANCE | 4 | 5 | 237
23 | 2 | GLYCOL HEATING PERFORMANCE | 4 | 6 | 27
23 | 2 | GLYCOL HEATING PERFORMANCE | 4 | 7 | 105
23 | 2 | GLYCOL HEATING PERFORMANCE | 4 | 8 | 285
23 | 2 | GLYCOL HEATING PERFORMANCE | 4 | 9 | 30
23 | 2 | GLYCOL HEATING PERFORMANCE | 4 | 10 | 104
23 | 2 | GLYCOL HEATING PERFORMANCE | 4 | 11 | 264
23 | 2 | GLYCOL HEATING PERFORMANCE | 4 | 12 | 30
23 | 2 | GLYCOL HEATING PERFORMANCE | 4 | 13 | 101
23 | 2 | GLYCOL HEATING PERFORMANCE | 4 | 14 | 332
23 | 2 | GLYCOL HEATING PERFORMANCE | 4 | 15 | 35
23 | 2 | GLYCOL HEATING PERFORMANCE | 4 | 16 | 98
23 | 2 | GLYCOL HEATING PERFORMANCE | 4 | 17 | 306
23 | 2 | GLYCOL HEATING PERFORMANCE | 4 | 18 | 35
23 | 2 | GLYCOL HEATING PERFORMANCE | 5 | 1 | 160
23 | 2 | GLYCOL HEATING PERFORMANCE | 5 | 2 | 200
23 | 2 | GLYCOL HEATING PERFORMANCE | 5 | 3 | 21
23 | 2 | GLYCOL HEATING PERFORMANCE | 5 | 4 | 97
23 | 2 | GLYCOL HEATING PERFORMANCE | 5 | 5 | 181
23 | 2 | GLYCOL HEATING PERFORMANCE | 5 | 6 | 21
23 | 2 | GLYCOL HEATING PERFORMANCE | 5 | 7 | 93
23 | 2 | GLYCOL HEATING PERFORMANCE | 5 | 8 | 223
23 | 2 | GLYCOL HEATING PERFORMANCE | 5 | 9 | 24
23 | 2 | GLYCOL HEATING PERFORMANCE | 5 | 10 | 94
23 | 2 | GLYCOL HEATING PERFORMANCE | 5 | 11 | 202
23 | 2 | GLYCOL HEATING PERFORMANCE | 5 | 12 | 23
23 | 2 | GLYCOL HEATING PERFORMANCE | 5 | 13 | 90
23 | 2 | GLYCOL HEATING PERFORMANCE | 5 | 14 | 259
23 | 2 | GLYCOL HEATING PERFORMANCE | 5 | 15 | 27
23 | 2 | GLYCOL HEATING PERFORMANCE | 5 | 16 | 89
23 | 2 | GLYCOL HEATING PERFORMANCE | 5 | 17 | 233
23 | 2 | GLYCOL HEATING PERFORMANCE | 5 | 18 | 27
23 | 2 | GLYCOL HEATING PERFORMANCE | 6 | 1 | 200
23 | 2 | GLYCOL HEATING PERFORMANCE | 6 | 2 | 274
23 | 2 | GLYCOL HEATING PERFORMANCE | 6 | 3 | 29
23 | 2 | GLYCOL HEATING PERFORMANCE | 6 | 4 | 127
23 | 2 | GLYCOL HEATING PERFORMANCE | 6 | 5 | 257
23 | 2 | GLYCOL HEATING PERFORMANCE | 6 | 6 | 29
23 | 2 | GLYCOL HEATING PERFORMANCE | 6 | 7 | 124
23 | 2 | GLYCOL HEATING PERFORMANCE | 6 | 8 | 306
23 | 2 | GLYCOL HEATING PERFORMANCE | 6 | 9 | 32
23 | 2 | GLYCOL HEATING PERFORMANCE | 6 | 10 | 123
23 | 2 | GLYCOL HEATING PERFORMANCE | 6 | 11 | 287
23 | 2 | GLYCOL HEATING PERFORMANCE | 6 | 12 | 33
23 | 2 | GLYCOL HEATING PERFORMANCE | 6 | 13 | 119
23 | 2 | GLYCOL HEATING PERFORMANCE | 6 | 14 | 357
23 | 2 | GLYCOL HEATING PERFORMANCE | 6 | 15 | 38
23 | 2 | GLYCOL HEATING PERFORMANCE | 6 | 16 | 116
23 | 2 | GLYCOL HEATING PERFORMANCE | 6 | 17 | 333
23 | 2 | GLYCOL HEATING PERFORMANCE | 6 | 18 | 38
23 | 2 | GLYCOL HEATING PERFORMANCE | 7 | 1 | 180
23 | 2 | GLYCOL HEATING PERFORMANCE | 7 | 2 | 218
23 | 2 | GLYCOL HEATING PERFORMANCE | 7 | 3 | 23
23 | 2 | GLYCOL HEATING PERFORMANCE | 7 | 4 | 116
23 | 2 | GLYCOL HEATING PERFORMANCE | 7 | 5 | 201
23 | 2 | GLYCOL HEATING PERFORMANCE | 7 | 6 | 23
23 | 2 | GLYCOL HEATING PERFORMANCE | 7 | 7 | 112
23 | 2 | GLYCOL HEATING PERFORMANCE | 7 | 8 | 244
23 | 2 | GLYCOL HEATING PERFORMANCE | 7 | 9 | 26
23 | 2 | GLYCOL HEATING PERFORMANCE | 7 | 10 | 112
23 | 2 | GLYCOL HEATING PERFORMANCE | 7 | 11 | 224
23 | 2 | GLYCOL HEATING PERFORMANCE | 7 | 12 | 26
23 | 2 | GLYCOL HEATING PERFORMANCE | 7 | 13 | 109
23 | 2 | GLYCOL HEATING PERFORMANCE | 7 | 14 | 284
23 | 2 | GLYCOL HEATING PERFORMANCE | 7 | 15 | 30
23 | 2 | GLYCOL HEATING PERFORMANCE | 7 | 16 | 107
23 | 2 | GLYCOL HEATING PERFORMANCE | 7 | 17 | 259
23 | 2 | GLYCOL HEATING PERFORMANCE | 7 | 18 | 30
23 | 2 | GLYCOL HEATING PERFORMANCE | 8 | 1 | 160
23 | 2 | GLYCOL HEATING PERFORMANCE | 8 | 2 | 164
23 | 2 | GLYCOL HEATING PERFORMANCE | 8 | 3 | 17
23 | 2 | GLYCOL HEATING PERFORMANCE | 8 | 4 | 104
23 | 2 | GLYCOL HEATING PERFORMANCE | 8 | 5 | 146
23 | 2 | GLYCOL HEATING PERFORMANCE | 8 | 6 | 17
23 | 2 | GLYCOL HEATING PERFORMANCE | 8 | 7 | 100
23 | 2 | GLYCOL HEATING PERFORMANCE | 8 | 8 | 183
23 | 2 | GLYCOL HEATING PERFORMANCE | 8 | 9 | 19
23 | 2 | GLYCOL HEATING PERFORMANCE | 8 | 10 | 101
23 | 2 | GLYCOL HEATING PERFORMANCE | 8 | 11 | 162
23 | 2 | GLYCOL HEATING PERFORMANCE | 8 | 12 | 19
23 | 2 | GLYCOL HEATING PERFORMANCE | 8 | 13 | 98
23 | 2 | GLYCOL HEATING PERFORMANCE | 8 | 14 | 212
23 | 2 | GLYCOL HEATING PERFORMANCE | 8 | 15 | 22
23 | 2 | GLYCOL HEATING PERFORMANCE | 8 | 16 | 97
23 | 2 | GLYCOL HEATING PERFORMANCE | 8 | 17 | 187
23 | 2 | GLYCOL HEATING PERFORMANCE | 8 | 18 | 22
23 | 2 | GLYCOL HEATING PERFORMANCE | 9 | 1 | 200
23 | 2 | GLYCOL HEATING PERFORMANCE | 9 | 2 | 249
23 | 2 | GLYCOL HEATING PERFORMANCE | 9 | 3 | 26
23 | 2 | GLYCOL HEATING PERFORMANCE | 9 | 4 | 132
23 | 2 | GLYCOL HEATING PERFORMANCE | 9 | 5 | 233
23 | 2 | GLYCOL HEATING PERFORMANCE | 9 | 6 | 27
23 | 2 | GLYCOL HEATING PERFORMANCE | 9 | 7 | 129
23 | 2 | GLYCOL HEATING PERFORMANCE | 9 | 8 | 279
23 | 2 | GLYCOL HEATING PERFORMANCE | 9 | 9 | 30
23 | 2 | GLYCOL HEATING PERFORMANCE | 9 | 10 | 128
23 | 2 | GLYCOL HEATING PERFORMANCE | 9 | 11 | 260
23 | 2 | GLYCOL HEATING PERFORMANCE | 9 | 12 | 30
23 | 2 | GLYCOL HEATING PERFORMANCE | 9 | 13 | 125
23 | 2 | GLYCOL HEATING PERFORMANCE | 9 | 14 | 325
23 | 2 | GLYCOL HEATING PERFORMANCE | 9 | 15 | 34
23 | 2 | GLYCOL HEATING PERFORMANCE | 9 | 16 | 122
23 | 2 | GLYCOL HEATING PERFORMANCE | 9 | 17 | 302
23 | 2 | GLYCOL HEATING PERFORMANCE | 9 | 18 | 34
23 | 2 | GLYCOL HEATING PERFORMANCE | 10 | 1 | 180
23 | 2 | GLYCOL HEATING PERFORMANCE | 10 | 2 | 194
23 | 2 | GLYCOL HEATING PERFORMANCE | 10 | 3 | 21
23 | 2 | GLYCOL HEATING PERFORMANCE | 10 | 4 | 121
23 | 2 | GLYCOL HEATING PERFORMANCE | 10 | 5 | 177
23 | 2 | GLYCOL HEATING PERFORMANCE | 10 | 6 | 20
23 | 2 | GLYCOL HEATING PERFORMANCE | 10 | 7 | 117
23 | 2 | GLYCOL HEATING PERFORMANCE | 10 | 8 | 217
23 | 2 | GLYCOL HEATING PERFORMANCE | 10 | 9 | 23
23 | 2 | GLYCOL HEATING PERFORMANCE | 10 | 10 | 117
23 | 2 | GLYCOL HEATING PERFORMANCE | 10 | 11 | 197
23 | 2 | GLYCOL HEATING PERFORMANCE | 10 | 12 | 23
23 | 2 | GLYCOL HEATING PERFORMANCE | 10 | 13 | 114
23 | 2 | GLYCOL HEATING PERFORMANCE | 10 | 14 | 252
23 | 2 | GLYCOL HEATING PERFORMANCE | 10 | 15 | 26
23 | 2 | GLYCOL HEATING PERFORMANCE | 10 | 16 | 113
23 | 2 | GLYCOL HEATING PERFORMANCE | 10 | 17 | 228
23 | 2 | GLYCOL HEATING PERFORMANCE | 10 | 18 | 27
23 | 2 | GLYCOL HEATING PERFORMANCE | 11 | 1 | 160
23 | 2 | GLYCOL HEATING PERFORMANCE | 11 | 2 | 140
23 | 2 | GLYCOL HEATING PERFORMANCE | 11 | 3 | 15
23 | 2 | GLYCOL HEATING PERFORMANCE | 11 | 4 | 109
23 | 2 | GLYCOL HEATING PERFORMANCE | 11 | 5 | 123
23 | 2 | GLYCOL HEATING PERFORMANCE | 11 | 6 | 14
23 | 2 | GLYCOL HEATING PERFORMANCE | 11 | 7 | 106
23 | 2 | GLYCOL HEATING PERFORMANCE | 11 | 8 | 156
23 | 2 | GLYCOL HEATING PERFORMANCE | 11 | 9 | 16
23 | 2 | GLYCOL HEATING PERFORMANCE | 11 | 10 | 107
23 | 2 | GLYCOL HEATING PERFORMANCE | 11 | 11 | 136
23 | 2 | GLYCOL HEATING PERFORMANCE | 11 | 12 | 16
23 | 2 | GLYCOL HEATING PERFORMANCE | 11 | 13 | 103
23 | 2 | GLYCOL HEATING PERFORMANCE | 11 | 14 | 180
23 | 2 | GLYCOL HEATING PERFORMANCE | 11 | 15 | 18
23 | 2 | GLYCOL HEATING PERFORMANCE | 11 | 16 | 103
23 | 2 | GLYCOL HEATING PERFORMANCE | 11 | 17 | 156
23 | 2 | GLYCOL HEATING PERFORMANCE | 11 | 18 | 19
23 | 3 | GLYCOL HEATING PERFORMANCE | 1 | 2 | 25
23 | 3 | GLYCOL HEATING PERFORMANCE | 2 | 1 | Ewt
23 | 3 | GLYCOL HEATING PERFORMANCE | 2 | 2 | Cap
23 | 3 | GLYCOL HEATING PERFORMANCE | 2 | 3 | Gpm
23 | 3 | GLYCOL HEATING PERFORMANCE | 2 | 4 | Ldb
23 | 3 | GLYCOL HEATING PERFORMANCE | 2 | 5 | Cap
23 | 3 | GLYCOL HEATING PERFORMANCE | 2 | 6 | Gpm
23 | 3 | GLYCOL HEATING PERFORMANCE | 3 | 1 | 200
23 | 3 | GLYCOL HEATING PERFORMANCE | 3 | 2 | 453
23 | 3 | GLYCOL HEATING PERFORMANCE | 3 | 3 | 48
23 | 3 | GLYCOL HEATING PERFORMANCE | 3 | 4 | 102
23 | 3 | GLYCOL HEATING PERFORMANCE | 3 | 5 | 425
23 | 3 | GLYCOL HEATING PERFORMANCE | 3 | 6 | 48
23 | 3 | GLYCOL HEATING PERFORMANCE | 4 | 1 | 180
23 | 3 | GLYCOL HEATING PERFORMANCE | 4 | 2 | 371
23 | 3 | GLYCOL HEATING PERFORMANCE | 4 | 3 | 39
23 | 3 | GLYCOL HEATING PERFORMANCE | 4 | 4 | 93
23 | 3 | GLYCOL HEATING PERFORMANCE | 4 | 5 | 342
23 | 3 | GLYCOL HEATING PERFORMANCE | 4 | 6 | 39
23 | 3 | GLYCOL HEATING PERFORMANCE | 5 | 1 | 160
23 | 3 | GLYCOL HEATING PERFORMANCE | 5 | 2 | 290
23 | 3 | GLYCOL HEATING PERFORMANCE | 5 | 3 | 31
23 | 3 | GLYCOL HEATING PERFORMANCE | 5 | 4 | 85
23 | 3 | GLYCOL HEATING PERFORMANCE | 5 | 5 | 260
23 | 3 | GLYCOL HEATING PERFORMANCE | 5 | 6 | 30
23 | 3 | GLYCOL HEATING PERFORMANCE | 6 | 1 | 200
23 | 3 | GLYCOL HEATING PERFORMANCE | 6 | 2 | 400
23 | 3 | GLYCOL HEATING PERFORMANCE | 6 | 3 | 42
23 | 3 | GLYCOL HEATING PERFORMANCE | 6 | 4 | 111
23 | 3 | GLYCOL HEATING PERFORMANCE | 6 | 5 | 372
23 | 3 | GLYCOL HEATING PERFORMANCE | 6 | 6 | 42
23 | 3 | GLYCOL HEATING PERFORMANCE | 7 | 1 | 180
23 | 3 | GLYCOL HEATING PERFORMANCE | 7 | 2 | 317
23 | 3 | GLYCOL HEATING PERFORMANCE | 7 | 3 | 34
23 | 3 | GLYCOL HEATING PERFORMANCE | 7 | 4 | 103
23 | 3 | GLYCOL HEATING PERFORMANCE | 7 | 5 | 287
23 | 3 | GLYCOL HEATING PERFORMANCE | 7 | 6 | 33
23 | 3 | GLYCOL HEATING PERFORMANCE | 8 | 1 | 160
23 | 3 | GLYCOL HEATING PERFORMANCE | 8 | 2 | 237
23 | 3 | GLYCOL HEATING PERFORMANCE | 8 | 3 | 25
23 | 3 | GLYCOL HEATING PERFORMANCE | 8 | 4 | 94
23 | 3 | GLYCOL HEATING PERFORMANCE | 8 | 5 | 208
23 | 3 | GLYCOL HEATING PERFORMANCE | 8 | 6 | 24
23 | 3 | GLYCOL HEATING PERFORMANCE | 9 | 1 | 200
23 | 3 | GLYCOL HEATING PERFORMANCE | 9 | 2 | 364
23 | 3 | GLYCOL HEATING PERFORMANCE | 9 | 3 | 39
23 | 3 | GLYCOL HEATING PERFORMANCE | 9 | 4 | 118
23 | 3 | GLYCOL HEATING PERFORMANCE | 9 | 5 | 337
23 | 3 | GLYCOL HEATING PERFORMANCE | 9 | 6 | 38
23 | 3 | GLYCOL HEATING PERFORMANCE | 10 | 1 | 180
23 | 3 | GLYCOL HEATING PERFORMANCE | 10 | 2 | 281
23 | 3 | GLYCOL HEATING PERFORMANCE | 10 | 3 | 30
23 | 3 | GLYCOL HEATING PERFORMANCE | 10 | 4 | 109
23 | 3 | GLYCOL HEATING PERFORMANCE | 10 | 5 | 254
23 | 3 | GLYCOL HEATING PERFORMANCE | 10 | 6 | 29
23 | 3 | GLYCOL HEATING PERFORMANCE | 11 | 1 | 160
23 | 3 | GLYCOL HEATING PERFORMANCE | 11 | 2 | 201
23 | 3 | GLYCOL HEATING PERFORMANCE | 11 | 3 | 21
23 | 3 | GLYCOL HEATING PERFORMANCE | 11 | 4 | 101
23 | 3 | GLYCOL HEATING PERFORMANCE | 11 | 5 | 173
23 | 3 | GLYCOL HEATING PERFORMANCE | 11 | 6 | 20
23 | 4 | GLYCOL HEATING PERFORMANCE | 1 | 1 | 4000
23 | 4 | GLYCOL HEATING PERFORMANCE | 1 | 3 | 5000
23 | 4 | GLYCOL HEATING PERFORMANCE | 1 | 5 | 6000
23 | 4 | GLYCOL HEATING PERFORMANCE | 1 | 7 | 8000
23 | 4 | GLYCOL HEATING PERFORMANCE | 2 | 1 | Gpm
23 | 4 | GLYCOL HEATING PERFORMANCE | 2 | 2 | ∆∆∆∆ P*
23 | 4 | GLYCOL HEATING PERFORMANCE | 2 | 3 | Gpm
23 | 4 | GLYCOL HEATING PERFORMANCE | 2 | 4 | ∆∆∆∆ P*
23 | 4 | GLYCOL HEATING PERFORMANCE | 2 | 5 | Gpm
23 | 4 | GLYCOL HEATING PERFORMANCE | 2 | 6 | ∆∆∆∆ P*
23 | 4 | GLYCOL HEATING PERFORMANCE | 2 | 7 | Gpm
23 | 4 | GLYCOL HEATING PERFORMANCE | 2 | 8 | ∆∆∆∆ P*
23 | 4 | GLYCOL HEATING PERFORMANCE | 2 | 9 | Gpm
23 | 4 | GLYCOL HEATING PERFORMANCE | 3 | 1 | 27
23 | 4 | GLYCOL HEATING PERFORMANCE | 3 | 2 | 1.2
23 | 4 | GLYCOL HEATING PERFORMANCE | 3 | 3 | 31
23 | 4 | GLYCOL HEATING PERFORMANCE | 3 | 4 | 1.5
23 | 4 | GLYCOL HEATING PERFORMANCE | 3 | 5 | 35
23 | 4 | GLYCOL HEATING PERFORMANCE | 3 | 6 | 1.8
23 | 4 | GLYCOL HEATING PERFORMANCE | 3 | 7 | 41
23 | 4 | GLYCOL HEATING PERFORMANCE | 3 | 8 | 2.4
23 | 4 | GLYCOL HEATING PERFORMANCE | 3 | 9 | 47
23 | 4 | GLYCOL HEATING PERFORMANCE | 4 | 1 | 22
23 | 4 | GLYCOL HEATING PERFORMANCE | 4 | 2 | 0.9
23 | 4 | GLYCOL HEATING PERFORMANCE | 4 | 3 | 25
23 | 4 | GLYCOL HEATING PERFORMANCE | 4 | 4 | 1.1
23 | 4 | GLYCOL HEATING PERFORMANCE | 4 | 5 | 27
23 | 4 | GLYCOL HEATING PERFORMANCE | 4 | 6 | 1.3
23 | 4 | GLYCOL HEATING PERFORMANCE | 4 | 7 | 32
23 | 4 | GLYCOL HEATING PERFORMANCE | 4 | 8 | 1.6
23 | 4 | GLYCOL HEATING PERFORMANCE | 4 | 9 | 36
23 | 4 | GLYCOL HEATING PERFORMANCE | 5 | 1 | 16
23 | 4 | GLYCOL HEATING PERFORMANCE | 5 | 2 | 0.6
23 | 4 | GLYCOL HEATING PERFORMANCE | 5 | 3 | 19
23 | 4 | GLYCOL HEATING PERFORMANCE | 5 | 4 | 0.7
23 | 4 | GLYCOL HEATING PERFORMANCE | 5 | 5 | 20
23 | 4 | GLYCOL HEATING PERFORMANCE | 5 | 6 | 0.8
23 | 4 | GLYCOL HEATING PERFORMANCE | 5 | 7 | 24
23 | 4 | GLYCOL HEATING PERFORMANCE | 5 | 8 | 1
23 | 4 | GLYCOL HEATING PERFORMANCE | 5 | 9 | 27
24 | 1 | Performance data (cont) | 1 | 1 | 50
24 | 1 | Performance data (cont) | 1 | 4 | 100
24 | 1 | Performance data (cont) | 1 | 7 | 149
24 | 1 | Performance data (cont) | 1 | 10 | 199
24 | 1 | Performance data (cont) | 1 | 13 | 249
24 | 1 | Performance data (cont) | 2 | 1 | r/s
24 | 1 | Performance data (cont) | 2 | 2 | BkW
24 | 1 | Performance data (cont) | 2 | 3 | kW
24 | 1 | Performance data (cont) | 2 | 4 | r/s
24 | 1 | Performance data (cont) | 2 | 5 | BkW
24 | 1 | Performance data (cont) | 2 | 6 | kW
24 | 1 | Performance data (cont) | 2 | 7 | r/s
24 | 1 | Performance data (cont) | 2 | 8 | BkW
24 | 1 | Performance data (cont) | 2 | 9 | kW
24 | 1 | Performance data (cont) | 2 | 10 | r/s
24 | 1 | Performance data (cont) | 2 | 11 | BkW
24 | 1 | Performance data (cont) | 2 | 12 | kW
24 | 1 | Performance data (cont) | 2 | 13 | r/s
24 | 1 | Performance data (cont) | 2 | 14 | BkW
24 | 1 | Performance data (cont) | 2 | 15 | kW
24 | 1 | Performance data (cont) | 2 | 16 | r/s
24 | 1 | Performance data (cont) | 2 | 17 | BkW
24 | 1 | Performance data (cont) | 3 | 1 | 11.4 11.9 12.4 13.0 13.5 14.1 14.6 15.2 15.8 16.3 16.9
24 | 1 | Performance data (cont) | 3 | 2 | 0.95 1.09 1.24 1.40 1.58 1.77 1.98 2.20 2.44 2.69 2.95
24 | 1 | Performance data (cont) | 3 | 3 | 1.10 1.26 1.44 1.64 1.84 2.07 2.31 2.57 2.84 3.13 3.44
24 | 1 | Performance data (cont) | 3 | 4 | 13.2 13.6 14.1 14.5 15.0 15.5 16.0 16.5 17.0 17.6 18.1
24 | 1 | Performance data (cont) | 3 | 5 | 1.10 1.24 1.40 1.57 1.75 1.95 2.16 2.39 2.62 2.88 3.15
24 | 1 | Performance data (cont) | 3 | 6 | 1.28 1.45 1.63 1.83 2.04 2.27 2.52 2.78 3.06 3.36 3.67
24 | 1 | Performance data (cont) | 3 | 7 | 14.8 15.2 15.6 16.0 16.4 16.9 17.3 17.8 18.3 18.8 —
24 | 1 | Performance data (cont) | 3 | 8 | 1.26 1.41 1.57 1.74 1.93 2.13 2.34 2.57 2.81 3.07 —
24 | 1 | Performance data (cont) | 3 | 9 | 1.47 1.64 1.83 2.03 2.25 2.48 2.73 2.99 3.28 3.58 —
24 | 1 | Performance data (cont) | 3 | 10 | 16.3 16.6 17.0 17.3 17.7 18.1 18.5 19.0 19.4 — —
24 | 1 | Performance data (cont) | 3 | 11 | 1.42 1.57 1.73 1.91 2.10 2.30 2.52 2.75 3.00 — —
24 | 1 | Performance data (cont) | 3 | 12 | 1.65 1.83 2.02 2.23 2.45 2.69 2.94 3.21 3.50 — —
24 | 1 | Performance data (cont) | 3 | 13 | 17.7 18.0 18.3 18.6 19.0 19.3 19.7 20.1 20.5 — —
24 | 1 | Performance data (cont) | 3 | 14 | 1.58 1.73 1.90 2.08 2.28 2.48 2.70 2.94 3.19 — —
24 | 1 | Performance data (cont) | 3 | 15 | 1.84 2.02 2.22 2.43 2.65 2.89 3.15 3.43 3.72 — —
24 | 1 | Performance data (cont) | 3 | 16 | 19.0 19.2 19.5 19.8 20.1 20.5 20.8 21.2 — — —
24 | 1 | Performance data (cont) | 3 | 17 | 1.75 1.90 2.07 2.26 2.45 2.66 2.89 3.13 — — —
24 | 2 | Performance data (cont) | 1 | 1 | 349
24 | 2 | Performance data (cont) | 1 | 4 | 399
24 | 2 | Performance data (cont) | 1 | 7 | 448
24 | 2 | Performance data (cont) | 1 | 10 | 473
24 | 2 | Performance data (cont) | 2 | 1 | r/s
24 | 2 | Performance data (cont) | 2 | 2 | BkW
24 | 2 | Performance data (cont) | 2 | 3 | kW
24 | 2 | Performance data (cont) | 2 | 4 | r/s
24 | 2 | Performance data (cont) | 2 | 5 | BkW
24 | 2 | Performance data (cont) | 2 | 6 | kW
24 | 2 | Performance data (cont) | 2 | 7 | r/s
24 | 2 | Performance data (cont) | 2 | 8 | BkW
24 | 2 | Performance data (cont) | 2 | 9 | kW
24 | 2 | Performance data (cont) | 2 | 10 | r/s
24 | 2 | Performance data (cont) | 2 | 11 | BkW
24 | 2 | Performance data (cont) | 2 | 12 | kW
24 | 2 | Performance data (cont) | 2 | 13 | r/s
24 | 2 | Performance data (cont) | 2 | 14 | BkW
24 | 2 | Performance data (cont) | 3 | 1 | 20.2 20.5 20.7 21.0 21.3 21.6 21.9 — — — —
24 | 2 | Performance data (cont) | 3 | 2 | 1.91 2.07 2.25 2.43 2.63 2.84 3.07 — — — —
24 | 2 | Performance data (cont) | 3 | 3 | 2.23 2.42 2.62 2.83 3.07 3.32 3.58 — — — —
24 | 2 | Performance data (cont) | 3 | 4 | 21.4 21.6 21.8 22.1 22.4 22.7 — — — — —
24 | 2 | Performance data (cont) | 3 | 5 | 2.08 2.25 2.42 2.61 2.81 3.03 — — — — —
24 | 2 | Performance data (cont) | 3 | 6 | 2.43 2.62 2.82 3.04 3.28 3.53 — — — — —
24 | 2 | Performance data (cont) | 3 | 7 | 22.6 22.7 22.9 23.2 23.4 23.7 — — — — —
24 | 2 | Performance data (cont) | 3 | 8 | 2.26 2.42 2.60 2.79 3.00 3.21 — — — — —
24 | 2 | Performance data (cont) | 3 | 9 | 2.63 2.82 3.03 3.25 3.49 3.75 — — — — —
24 | 2 | Performance data (cont) | 3 | 10 | 23.1 23.3 23.5 23.7 23.9 — — — — — —
24 | 2 | Performance data (cont) | 3 | 11 | 2.35 2.51 2.69 2.88 3.09 — — — — — —
24 | 2 | Performance data (cont) | 3 | 12 | 2.74 2.93 3.14 3.36 3.60 — — — — — —
24 | 2 | Performance data (cont) | 3 | 13 | 23.6 23.8 24.0 24.2 24.4 — — — — — —
24 | 2 | Performance data (cont) | 3 | 14 | 2.44 2.60 2.78 2.97 3.18 — — — — — —
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 1 | 1 | 50
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 1 | 4 | 100
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 1 | 7 | 149
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 1 | 10 | 199
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 1 | 13 | 249
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 1 | 16 | 299
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 1 | 19 | 349
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 1 | r/s
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 2 | BkW
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 3 | kW
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 4 | r/s
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 5 | BkW
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 6 | kW
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 7 | r/s
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 8 | BkW
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 9 | kW
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 10 | r/s
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 11 | BkW
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 12 | kW
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 13 | r/s
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 14 | BkW
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 15 | kW
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 16 | r/s
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 17 | BkW
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 18 | kW
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 19 | r/s
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 20 | BkW
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 21 | kW
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 22 | r/s
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 23 | BkW
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 1 | 11.4 12.2 13.0 13.8 14.6 15.5 16.3 17.2 18.0 18.9
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 2 | 1.49 1.76 2.09 2.45 2.84 3.27 3.74 4.24 4.78 5.36
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 3 | 1.68 2.01 2.37 2.78 3.23 3.72 4.24 4.82 5.43 6.09
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 4 | 12.7 13.4 14.1 14.9 15.6 16.4 17.2 18.0 18.8 19.7
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 5 | 1.71 1.99 2.31 2.68 3.07 3.51 3.98 4.49 5.03 5.62
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 6 | 1.92 2.26 2.63 3.04 3.49 3.99 4.52 5.10 5.72 6.38
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 7 | 13.9 14.5 15.2 15.9 16.6 17.3 18.1 18.9 19.6 20.4
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 8 | 1.94 2.21 2.55 2.91 3.31 3.75 4.22 4.74 5.29 5.87
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 9 | 2.18 2.52 2.89 3.31 3.77 4.26 4.80 5.38 6.01 6.68
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 10 | 15.0 15.6 16.2 16.8 17.5 18.2 18.9 19.7 20.4 21.2
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 11 | 2.17 2.45 2.78 3.15 3.56 4.00 4.48 4.99 5.54 6.13
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 12 | 2.44 2.78 3.16 3.58 4.04 4.54 5.09 5.67 6.30 6.97
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 13 | 16.1 16.6 17.2 17.8 18.4 19.1 19.7 20.4 21.2 21.9
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 14 | 2.41 2.69 3.03 3.40 3.81 4.25 4.73 5.25 5.80 6.40
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 15 | 2.71 3.06 3.44 3.86 4.33 4.83 5.38 5.96 6.60 7.27
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 16 | 17.1 17.6 18.1 18.7 19.3 19.9 20.5 21.2 21.9 22.6
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 17 | 2.66 2.94 3.28 3.65 4.06 4.51 4.99 5.51 6.07 6.67
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 18 | 2.99 3.34 3.72 4.15 4.61 5.12 5.67 6.26 6.90 7.57
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 19 | 18.1 18.5 19.0 19.6 20.1 20.7 21.3 21.9 22.6 23.3
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 20 | 2.91 3.19 3.53 3.91 4.32 4.77 5.25 5.77 6.33 6.93
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 21 | 3.28 3.62 4.01 4.44 4.91 5.41 5.97 6.56 7.20 7.88
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 22 | 19.0 19.4 19.9 20.4 20.9 21.5 22.1 22.7 23.3 24.0
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 23 | 3.17 3.45 3.79 4.16 4.58 5.03 5.52 6.04 6.60 7.21
25 | 2 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 1 | 1 | 448
25 | 2 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 1 | 4 | 473
25 | 2 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 1 | r/s
25 | 2 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 2 | BkW
25 | 2 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 3 | kW
25 | 2 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 4 | r/s
25 | 2 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 5 | BkW
25 | 2 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 6 | kW
25 | 2 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 7 | r/s
25 | 2 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | 8 | BkW
25 | 2 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 1 | 20.0 20.3 20.7 21.2 21.7 22.2 22.8 23.4 24.0 24.6
25 | 2 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 2 | 3.43 3.71 4.05 4.43 4.84 5.30 5.78 6.31 6.88 7.48
25 | 2 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 3 | 3.86 4.21 4.60 5.03 5.50 6.02 6.57 7.17 7.82 8.50
25 | 2 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 4 | 20.4 20.8 21.2 21.6 22.1 22.6 23.2 23.7 24.3 —
25 | 2 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 5 | 3.57 3.84 4.18 4.56 4.98 5.43 5.92 6.45 7.02 —
25 | 2 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 6 | 4.02 4.36 4.75 5.18 5.66 6.17 6.73 7.33 7.97 —
25 | 2 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 7 | 20.8 21.2 21.6 22.0 22.5 23.0 23.5 24.1 24.7 —
25 | 2 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 8 | 3.71 3.97 4.32 4.70 5.11 5.57 6.06 6.59 7.15 —
26 | 1 | Performance data (cont) | 1 | 1 | 50
26 | 1 | Performance data (cont) | 1 | 4 | 100
26 | 1 | Performance data (cont) | 1 | 7 | 149
26 | 1 | Performance data (cont) | 1 | 10 | 199
26 | 1 | Performance data (cont) | 1 | 13 | 249
26 | 1 | Performance data (cont) | 1 | 16 | 299
26 | 1 | Performance data (cont) | 2 | 1 | r/s
26 | 1 | Performance data (cont) | 2 | 2 | BkW
26 | 1 | Performance data (cont) | 2 | 3 | kW
26 | 1 | Performance data (cont) | 2 | 4 | r/s
26 | 1 | Performance data (cont) | 2 | 5 | BkW
26 | 1 | Performance data (cont) | 2 | 6 | kW
26 | 1 | Performance data (cont) | 2 | 7 | r/s
26 | 1 | Performance data (cont) | 2 | 8 | BkW
26 | 1 | Performance data (cont) | 2 | 9 | kW
26 | 1 | Performance data (cont) | 2 | 10 | r/s
26 | 1 | Performance data (cont) | 2 | 11 | BkW
26 | 1 | Performance data (cont) | 2 | 12 | kW
26 | 1 | Performance data (cont) | 2 | 13 | r/s
26 | 1 | Performance data (cont) | 2 | 14 | BkW
26 | 1 | Performance data (cont) | 2 | 15 | kW
26 | 1 | Performance data (cont) | 2 | 16 | r/s
26 | 1 | Performance data (cont) | 2 | 17 | BkW
26 | 1 | Performance data (cont) | 2 | 18 | kW
26 | 1 | Performance data (cont) | 2 | 19 | r/s
26 | 1 | Performance data (cont) | 2 | 20 | BkW
26 | 1 | Performance data (cont) | 3 | 1 | 14.1 14.9 15.8 16.7 17.6 18.4 19.3 20.2 21.1 21.5
26 | 1 | Performance data (cont) | 3 | 2 | 2.41 2.82 3.28 3.78 4.33 4.92 5.56 6.25 6.99 7.38
26 | 1 | Performance data (cont) | 3 | 3 | 2009 2355 2735 3153 3608 4102 4635 5210 5826 6151
26 | 1 | Performance data (cont) | 3 | 4 | 15.1 15.9 16.7 17.6 18.4 19.2 20.1 20.9 21.8 22.2
26 | 1 | Performance data (cont) | 3 | 5 | 2.67 3.09 3.55 4.06 4.61 5.21 5.86 6.56 7.30 7.69
26 | 1 | Performance data (cont) | 3 | 6 | 2222 2574 2961 3384 3845 4345 4884 5464 6086 6413
26 | 1 | Performance data (cont) | 3 | 7 | 16.2 16.9 17.7 18.4 19.2 20.0 20.8 21.7 22.5 22.9
26 | 1 | Performance data (cont) | 3 | 8 | 2.93 3.36 3.83 4.34 4.90 5.51 6.16 6.87 7.62 8.01
26 | 1 | Performance data (cont) | 3 | 9 | 2441 2799 3191 3620 4087 4592 5137 5722 6349 6679
26 | 1 | Performance data (cont) | 3 | 10 | 17.1 17.8 18.5 19.3 20.0 20.8 21.6 22.4 23.2 23.6
26 | 1 | Performance data (cont) | 3 | 11 | 3.20 3.63 4.11 4.63 5.20 5.81 6.47 7.18 7.94 8.34
26 | 1 | Performance data (cont) | 3 | 12 | 2666 3029 3427 3861 4332 4843 5393 5983 6616 6948
26 | 1 | Performance data (cont) | 3 | 13 | 18.1 18.7 19.4 20.1 20.8 21.5 22.3 23.1 23.8 24.2
26 | 1 | Performance data (cont) | 3 | 14 | 3.48 3.92 4.40 4.93 5.50 6.12 6.78 7.50 8.26 8.66
26 | 1 | Performance data (cont) | 3 | 15 | 2897 3264 3667 4106 4582 5097 5652 6248 6885 7219
26 | 1 | Performance data (cont) | 3 | 16 | 19.0 19.6 20.2 20.9 21.6 22.3 23.0 23.7 24.5 24.9
26 | 1 | Performance data (cont) | 3 | 17 | 3.76 4.20 4.69 5.22 5.80 6.43 7.10 7.82 8.59 8.99
26 | 1 | Performance data (cont) | 3 | 18 | 3133 3504 3911 4355 4836 5356 5915 6515 7157 7494
26 | 1 | Performance data (cont) | 3 | 19 | 19.8 20.4 21.0 21.6 22.3 23.0 23.7 24.4 25.1 25.5
26 | 1 | Performance data (cont) | 3 | 20 | 4.05 4.50 4.99 5.53 6.11 6.74 7.42 8.14 8.92 9.32
26 | 2 | Performance data (cont) | 1 | 1 | 399
26 | 2 | Performance data (cont) | 2 | 1 | r/s
26 | 2 | Performance data (cont) | 2 | 2 | BkW
26 | 2 | Performance data (cont) | 2 | 3 | kW
26 | 2 | Performance data (cont) | 2 | 4 | r/s
26 | 2 | Performance data (cont) | 2 | 5 | BkW
26 | 2 | Performance data (cont) | 3 | 1 | 20.7 21.2 21.8 22.4 23.0 23.7 24.4 25.1 25.8 —
26 | 2 | Performance data (cont) | 3 | 2 | 4.34 4.80 5.30 5.84 6.42 7.06 7.74 8.47 9.25 —
26 | 2 | Performance data (cont) | 3 | 3 | 3621 4000 4414 4866 5355 5883 6451 7060 7710 —
26 | 2 | Performance data (cont) | 3 | 4 | 21.5 22.0 22.5 23.1 23.7 24.4 25.0 25.7 — —
26 | 2 | Performance data (cont) | 3 | 5 | 3.63 4.11 4.63 5.20 5.81 6.47 7.18 7.94 — —
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 1 | 1 | 0.2
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 1 | 4 | 0.4
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 1 | 7 | 0.6
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 1 | 10 | 0.8
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 1 | 13 | 1
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 1 | Rpm
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 2 | Bhp
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 3 | Watts
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 4 | Rpm
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 5 | Bhp
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 6 | Watts
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 7 | Rpm
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 8 | Bhp
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 9 | Watts
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 10 | Rpm
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 11 | Bhp
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 12 | Watts
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 13 | Rpm
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 14 | Bhp
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 15 | Watts
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 16 | Rpm
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 17 | Bhp
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 1 | 684 715 747 779 812 845 878 912 946 981 1016
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 2 | 1.28 1.47 1.67 1.90 2.14 2.40 2.68 2.98 3.29 3.63 3.99
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 3 | 1102 1265 1442 1635 1844 2068 2309 2566 2841 3133 3443
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 4 | 791 817 844 872 901 931 961 992 1023 1055 1087
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 5 | 1.49 1.68 1.89 2.12 2.37 2.64 2.92 3.22 3.55 3.89 4.25
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 6 | 1283 1451 1633 1831 2044 2273 2518 2780 3059 3355 3669
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 7 | 887 910 934 959 985 1011 1039 1067 1096 1125 —
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 8 | 1.70 1.90 2.12 2.35 2.60 2.87 3.16 3.47 3.80 4.15 —
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 9 | 1466 1638 1825 2027 2245 2478 2728 2994 3277 3578 —
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 10 | 977 997 1018 1040 1063 1087 1112 1138 1165 — —
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 11 | 1.92 2.12 2.34 2.58 2.84 3.11 3.41 3.72 4.05 — —
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 12 | 1652 1828 2019 2226 2448 2685 2939 3209 3496 — —
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 13 | 1061 1078 1097 1117 1138 1160 1183 1207 1232 — —
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 14 | 2.13 2.34 2.57 2.81 3.07 3.35 3.65 3.97 4.31 — —
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 15 | 1841 2021 2216 2426 2652 2893 3151 3425 3716 — —
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 16 | 1139 1155 1171 1189 1209 1229 1250 1273 — — —
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 17 | 2.36 2.57 2.80 3.05 3.31 3.60 3.90 4.22 — — —
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 1 | 1 | 1.4
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 1 | 4 | 1.6
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 1 | 7 | 1.8
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 1 | 10 | 1.9
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 1 | Rpm
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 2 | Bhp
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 3 | Watts
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 4 | Rpm
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 5 | Bhp
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 6 | Watts
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 7 | Rpm
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 8 | Bhp
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 9 | Watts
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 10 | Rpm
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 11 | Bhp
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 12 | Watts
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 13 | Rpm
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | 14 | Bhp
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 1 | 1214 1228 1243 1259 1277 1295 1315 — — — —
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 2 | 2.59 2.80 3.04 3.29 3.56 3.84 4.15 — — — —
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 3 | 2230 2417 2618 2835 3067 3316 3580 — — — —
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 4 | 1285 1297 1311 1326 1342 1359 — — — — —
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 5 | 2.82 3.04 3.27 3.53 3.80 4.09 — — — — —
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 6 | 2430 2619 2823 3043 3278 3530 — — — — —
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 7 | 1353 1364 1376 1390 1405 1421 — — — — —
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 8 | 3.05 3.27 3.51 3.77 4.05 4.34 — — — — —
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 9 | 2633 2825 3031 3254 3492 3746 — — — — —
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 10 | 1386 1396 1408 1421 1435 — — — — — —
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 11 | 3.17 3.40 3.64 3.90 4.17 — — — — — —
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 12 | 2736 2928 3136 3360 3600 — — — — — —
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 13 | 1418 1428 1439 1452 1466 — — — — — —
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 14 | 3.29 3.52 3.76 4.02 4.30 — — — — — —
28 | 1 | Performance data (cont) | 1 | 1 | 0.2
28 | 1 | Performance data (cont) | 1 | 4 | 0.4
28 | 1 | Performance data (cont) | 1 | 7 | 0.6
28 | 1 | Performance data (cont) | 1 | 10 | 0.8
28 | 1 | Performance data (cont) | 1 | 13 | 1
28 | 1 | Performance data (cont) | 1 | 16 | 1.2
28 | 1 | Performance data (cont) | 2 | 1 | Rpm
28 | 1 | Performance data (cont) | 2 | 2 | Bhp
28 | 1 | Performance data (cont) | 2 | 3 | Watts
28 | 1 | Performance data (cont) | 2 | 4 | Rpm
28 | 1 | Performance data (cont) | 2 | 5 | Bhp
28 | 1 | Performance data (cont) | 2 | 6 | Watts
28 | 1 | Performance data (cont) | 2 | 7 | Rpm
28 | 1 | Performance data (cont) | 2 | 8 | Bhp
28 | 1 | Performance data (cont) | 2 | 9 | Watts
28 | 1 | Performance data (cont) | 2 | 10 | Rpm
28 | 1 | Performance data (cont) | 2 | 11 | Bhp
28 | 1 | Performance data (cont) | 2 | 12 | Watts
28 | 1 | Performance data (cont) | 2 | 13 | Rpm
28 | 1 | Performance data (cont) | 2 | 14 | Bhp
28 | 1 | Performance data (cont) | 2 | 15 | Watts
28 | 1 | Performance data (cont) | 2 | 16 | Rpm
28 | 1 | Performance data (cont) | 2 | 17 | Bhp
28 | 1 | Performance data (cont) | 2 | 18 | Watts
28 | 1 | Performance data (cont) | 2 | 19 | Rpm
28 | 1 | Performance data (cont) | 2 | 20 | Bhp
28 | 1 | Performance data (cont) | 3 | 1 | 682 730 778 828 878 928 979 1030 1082 1134
28 | 1 | Performance data (cont) | 3 | 2 | 1.99 2.38 2.82 3.31 3.84 4.42 5.05 5.73 6.46 7.25
28 | 1 | Performance data (cont) | 3 | 3 | 1675 2005 2373 2780 3227 3715 4245 4817 5433 6093
28 | 1 | Performance data (cont) | 3 | 4 | 760 802 846 892 938 985 1033 1082 1131 1180
28 | 1 | Performance data (cont) | 3 | 5 | 2.29 2.68 3.13 3.62 4.15 4.74 5.38 6.06 6.80 7.59
28 | 1 | Performance data (cont) | 3 | 6 | 1922 2257 2630 3042 3494 3986 4521 5098 5718 6382
28 | 1 | Performance data (cont) | 3 | 7 | 832 871 911 953 996 1040 1085 1131 1178 1226
28 | 1 | Performance data (cont) | 3 | 8 | 2.59 2.99 3.44 3.94 4.48 5.07 5.71 6.40 7.14 7.94
28 | 1 | Performance data (cont) | 3 | 9 | 2177 2516 2893 3310 3766 4263 4801 5382 6007 6675
28 | 1 | Performance data (cont) | 3 | 10 | 901 935 972 1011 1051 1093 1136 1180 1225 1270
28 | 1 | Performance data (cont) | 3 | 11 | 2.90 3.31 3.76 4.26 4.81 5.40 6.05 6.74 7.49 8.29
28 | 1 | Performance data (cont) | 3 | 12 | 2441 2783 3164 3583 4043 4544 5086 5671 6299 6971
28 | 1 | Performance data (cont) | 3 | 13 | 965 997 1031 1067 1105 1144 1185 1227 1270 1313
28 | 1 | Performance data (cont) | 3 | 14 | 3.22 3.63 4.09 4.59 5.14 5.74 6.39 7.09 7.84 8.65
28 | 1 | Performance data (cont) | 3 | 15 | 2712 3057 3440 3863 4326 4830 5375 5964 6595 7271
28 | 1 | Performance data (cont) | 3 | 16 | 1027 1056 1087 1121 1156 1194 1232 1272 1313 1356
28 | 1 | Performance data (cont) | 3 | 17 | 3.56 3.97 4.43 4.93 5.49 6.09 6.74 7.44 8.20 9.01
28 | 1 | Performance data (cont) | 3 | 18 | 2990 3337 3722 4148 4613 5120 5669 6260 6895 7574
28 | 1 | Performance data (cont) | 3 | 19 | 1086 1112 1142 1173 1207 1242 1279 1317 1356 1397
28 | 1 | Performance data (cont) | 3 | 20 | 3.89 4.31 4.77 5.28 5.83 6.44 7.10 7.80 8.56 9.37
28 | 2 | Performance data (cont) | 1 | 1 | 1.6
28 | 2 | Performance data (cont) | 1 | 4 | 1.8
28 | 2 | Performance data (cont) | 1 | 7 | 1.9
28 | 2 | Performance data (cont) | 2 | 1 | Rpm
28 | 2 | Performance data (cont) | 2 | 2 | Bhp
28 | 2 | Performance data (cont) | 2 | 3 | Watts
28 | 2 | Performance data (cont) | 2 | 4 | Rpm
28 | 2 | Performance data (cont) | 2 | 5 | Bhp
28 | 2 | Performance data (cont) | 2 | 6 | Watts
28 | 2 | Performance data (cont) | 2 | 7 | Rpm
28 | 2 | Performance data (cont) | 2 | 8 | Bhp
28 | 2 | Performance data (cont) | 2 | 9 | Watts
28 | 2 | Performance data (cont) | 2 | 10 | Rpm
28 | 2 | Performance data (cont) | 2 | 11 | Bhp
28 | 2 | Performance data (cont) | 3 | 1 | 1142 1167 1194 1224 1255 1289 1324 1360 1398 1438
28 | 2 | Performance data (cont) | 3 | 2 | 4.24 4.66 5.12 5.63 6.19 6.80 7.45 8.16 8.93 9.74
28 | 2 | Performance data (cont) | 3 | 3 | 3567 3915 4304 4733 5203 5714 6268 6865 7505 8190
28 | 2 | Performance data (cont) | 3 | 4 | 1197 1219 1245 1273 1302 1334 1368 1403 1440 1477
28 | 2 | Performance data (cont) | 3 | 5 | 4.59 5.01 5.47 5.98 6.55 7.16 7.82 8.53 9.29 10.11
28 | 2 | Performance data (cont) | 3 | 6 | 3864 4213 4602 5033 5504 6018 6573 7173 7815 8503
28 | 2 | Performance data (cont) | 3 | 7 | 1223 1245 1270 1296 1326 1357 1389 1424 1460 —
28 | 2 | Performance data (cont) | 3 | 8 | 4.77 5.19 5.65 6.17 6.73 7.34 8.00 8.71 9.48 —
28 | 2 | Performance data (cont) | 3 | 9 | 4015 4364 4754 5184 5657 6171 6728 7328 7972 —
28 | 2 | Performance data (cont) | 3 | 10 | 1249 1270 1294 1320 1348 1379 1411 1445 1480 —
28 | 2 | Performance data (cont) | 3 | 11 | 4.96 5.37 5.83 6.35 6.91 7.52 8.18 8.90 9.67 —
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 1 | 1 | 0.2
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 1 | 4 | 0.4
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 1 | 7 | 0.6
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 1 | 10 | 0.8
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 1 | 13 | 1
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 1 | 16 | 1.2
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 1 | Rpm
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 2 | Bhp
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 3 | Watts
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 4 | Rpm
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 5 | Bhp
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 6 | Watts
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 7 | Rpm
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 8 | Bhp
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 9 | Watts
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 10 | Rpm
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 11 | Bhp
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 12 | Watts
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 13 | Rpm
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 14 | Bhp
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 15 | Watts
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 16 | Rpm
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 17 | Bhp
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 18 | Watts
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 19 | Rpm
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 20 | Bhp
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 1 | 845 896 948 1001 1053 1106 1159 1213 1266 1293
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 2 | 3.26 3.82 4.43 5.11 5.85 6.65 7.52 8.45 9.45 9.97
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 3 | 2693 3156 3667 4226 4836 5498 6214 6984 7810 8245
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 4 | 909 956 1005 1054 1104 1155 1206 1257 1309 1334
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 5 | 3.60 4.17 4.80 5.49 6.23 7.04 7.92 8.86 9.87 10.40
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 6 | 2979 3450 3969 4537 5155 5824 6547 7325 8159 8597
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 7 | 969 1014 1060 1106 1154 1202 1251 1300 1350 1375
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 8 | 3.96 4.54 5.17 5.87 6.63 7.44 8.33 9.28 10.29 10.83
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 9 | 3272 3752 4278 4853 5478 6155 6886 7671 8511 8953
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 10 | 1028 1069 1112 1156 1202 1248 1295 1342 1391 1415
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 11 | 4.32 4.91 5.56 6.26 7.02 7.85 8.74 9.70 10.73 11.26
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 12 | 3574 4060 4593 5175 5808 6492 7229 8020 8868 9313
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 13 | 1083 1123 1163 1205 1248 1293 1338 1384 1431 1454
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 14 | 4.70 5.29 5.94 6.66 7.43 8.26 9.16 10.13 11.16 11.70
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 15 | 3883 4375 4915 5504 6142 6833 7577 8375 9229 9677
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 16 | 1137 1174 1213 1253 1294 1336 1380 1424 1470 1493
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 17 | 5.08 5.68 6.34 7.06 7.84 8.68 9.59 10.56 11.60 12.15
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 18 | 4,200 4,698 5,243 5,838 6,483 7,179 7,929 8,733 9,594 10,045
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 19 | 1189 1224 1261 1299 1338 1379 1421 1464 1508 1530
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 20 | 5.47 6.08 6.75 7.47 8.26 9.11 10.02 11.00 12.05 12.60
29 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 1 | 1 | 1.6
29 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 1 | Rpm
29 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 2 | Bhp
29 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 3 | Watts
29 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 4 | Rpm
29 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | 5 | Bhp
29 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 1 | 1239 1272 1307 1344 1382 1421 1461 1503 1546 —
29 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 2 | 5.87 6.48 7.16 7.89 8.68 9.54 10.46 11.45 12.50 —
29 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 3 | 4,854 5,362 5,917 6,523 7,179 7,887 8,648 9,464 10,336 —
29 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 4 | 1288 1320 1353 1388 1424 1462 1501 1541 — —
29 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 5 | 4.91 5.56 6.26 7.02 7.85 8.74 9.70 10.73 — —
30 | 1 | Performance data (cont) | 1 | 1 | FAN PERFORMANCE USING ACCESSORY POWER EXHAUST
30 | 1 | Performance data (cont) | 3 | 1 | HORIZONTAL SUPPLY/RETURN FAN PERFORMANCE WITH CRRFCURB013A00 HIGH-STATIC REGAIN ADAPTER NOTE: The CRRFCURB013A00 high-static regain adapter accessory may be used to provide horizontal supply/return. NOTE: The CRRFCURB013A00 horizontal supply and return adapter accessory improves 50TJ fan performance by increasing external static pressure by amount shown above.
31 | 1 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 1 | 1 | 2125
31 | 1 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 1 | 2 | 2360
31 | 1 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 1 | 3 | 2831
31 | 1 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 1 | 4 | 3400
31 | 1 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 2 | 1 | 10
31 | 1 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 2 | 2 | 12
31 | 1 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 2 | 3 | 17
31 | 1 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 2 | 4 | 22
31 | 1 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 3 | 1 | 55
31 | 1 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 3 | 2 | 65
31 | 1 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 3 | 3 | 87
31 | 1 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 3 | 4 | 109
31 | 1 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 5 | 1 | 15 19 25
31 | 1 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 5 | 2 | 17 22 27
31 | 1 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 5 | 3 | 22 27 35
31 | 1 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 5 | 4 | 27 35 46
31 | 2 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 1 | 1 | 4500
31 | 2 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 1 | 2 | 5000
31 | 2 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 1 | 3 | 6000
31 | 2 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 1 | 4 | 7200
31 | 2 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 2 | 1 | 0.04
31 | 2 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 2 | 2 | 0.05
31 | 2 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 2 | 3 | 0.07
31 | 2 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 2 | 4 | 0.09
31 | 2 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 3 | 1 | 0.22
31 | 2 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 3 | 2 | 0.26
31 | 2 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 3 | 3 | 0.35
31 | 2 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 3 | 4 | 0.44
31 | 2 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 5 | 1 | 0.06 0.08 0.10
31 | 2 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 5 | 2 | 0.07 0.09 0.11
31 | 2 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 5 | 3 | 0.09 0.11 0.14
31 | 2 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 5 | 4 | 0.11 0.14 0.18
31 | 3 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 1 | 1 | 2800
31 | 3 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 1 | 2 | 3400
31 | 3 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 1 | 3 | 4247
31 | 3 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 1 | 4 | 4719
31 | 3 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 2 | 1 | 17
31 | 3 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 2 | 2 | 22
31 | 3 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 2 | 3 | 27
31 | 3 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 2 | 4 | 30
31 | 3 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 3 | 1 | 86
31 | 3 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 3 | 2 | 109
31 | 3 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 3 | 3 | 144
31 | 3 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 3 | 4 | 164
31 | 3 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 5 | 1 | 22 28 36
31 | 3 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 5 | 2 | 27 35 46
31 | 3 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 5 | 3 | 37 45 57
31 | 3 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 5 | 4 | 43 53 65
31 | 4 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 1 | 1 | 6000
31 | 4 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 1 | 2 | 7200
31 | 4 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 1 | 3 | 9000
31 | 4 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 1 | 4 | 10000
31 | 4 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 2 | 1 | 0.07
31 | 4 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 2 | 2 | 0.09
31 | 4 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 2 | 3 | 0.11
31 | 4 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 2 | 4 | 0.12
31 | 4 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 3 | 1 | 0.35
31 | 4 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 3 | 2 | 0.44
31 | 4 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 3 | 3 | 0.58
31 | 4 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 3 | 4 | 0.66
31 | 4 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 5 | 1 | 0.09 0.11 0.14
31 | 4 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 5 | 2 | 0.11 0.14 0.18
31 | 4 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 5 | 3 | 0.15 0.18 0.23
31 | 4 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 5 | 4 | 0.17 0.21 0.26
32 | 1 | Performance data (cont) | 1 | 1 | 0
32 | 1 | Performance data (cont) | 1 | 2 | 1/2
32 | 1 | Performance data (cont) | 1 | 3 | 1
32 | 1 | Performance data (cont) | 1 | 4 | 11/2
32 | 1 | Performance data (cont) | 1 | 5 | 2
32 | 1 | Performance data (cont) | 1 | 6 | 21/2
32 | 1 | Performance data (cont) | 1 | 7 | 3
32 | 1 | Performance data (cont) | 1 | 8 | 31/2
32 | 1 | Performance data (cont) | 1 | 9 | 4
32 | 1 | Performance data (cont) | 1 | 10 | 41/2
32 | 1 | Performance data (cont) | 1 | 11 | 5
32 | 1 | Performance data (cont) | 1 | 12 | 51/2
32 | 1 | Performance data (cont) | 2 | 1 | 16.38
32 | 1 | Performance data (cont) | 2 | 2 | 15.99
32 | 1 | Performance data (cont) | 2 | 3 | 15.58
32 | 1 | Performance data (cont) | 2 | 4 | 15.19
32 | 1 | Performance data (cont) | 2 | 5 | 14.78
32 | 1 | Performance data (cont) | 2 | 6 | 14.38
32 | 1 | Performance data (cont) | 2 | 7 | 13.98
32 | 1 | Performance data (cont) | 2 | 8 | 13.58
32 | 1 | Performance data (cont) | 2 | 9 | 13.18
32 | 1 | Performance data (cont) | 2 | 10 | 12.78
32 | 1 | Performance data (cont) | 2 | 11 | 12.38
32 | 1 | Performance data (cont) | 2 | 12 | †
32 | 1 | Performance data (cont) | 3 | 1 | 21.67
32 | 1 | Performance data (cont) | 3 | 2 | 21.2
32 | 1 | Performance data (cont) | 3 | 3 | 20.75
32 | 1 | Performance data (cont) | 3 | 4 | 20.28
32 | 1 | Performance data (cont) | 3 | 5 | 19.82
32 | 1 | Performance data (cont) | 3 | 6 | 19.37
32 | 1 | Performance data (cont) | 3 | 7 | 18.9
32 | 1 | Performance data (cont) | 3 | 8 | 18.43
32 | 1 | Performance data (cont) | 3 | 9 | 17.97
32 | 1 | Performance data (cont) | 3 | 10 | 17.52
32 | 1 | Performance data (cont) | 3 | 11 | 17.05
32 | 1 | Performance data (cont) | 3 | 12 | †
32 | 1 | Performance data (cont) | 4 | 1 | 15.15
32 | 1 | Performance data (cont) | 4 | 2 | 14.92
32 | 1 | Performance data (cont) | 4 | 3 | 14.68
32 | 1 | Performance data (cont) | 4 | 4 | 14.45
32 | 1 | Performance data (cont) | 4 | 5 | 14.22
32 | 1 | Performance data (cont) | 4 | 6 | 13.98
32 | 1 | Performance data (cont) | 4 | 7 | 13.75
32 | 1 | Performance data (cont) | 4 | 8 | 13.52
32 | 1 | Performance data (cont) | 4 | 9 | 13.28
32 | 1 | Performance data (cont) | 4 | 10 | 13.05
32 | 1 | Performance data (cont) | 4 | 11 | 12.82
32 | 1 | Performance data (cont) | 4 | 12 | †
32 | 1 | Performance data (cont) | 5 | 1 | 20.27
32 | 1 | Performance data (cont) | 5 | 2 | 19.97
32 | 1 | Performance data (cont) | 5 | 3 | 19.66
32 | 1 | Performance data (cont) | 5 | 4 | 19.35
32 | 1 | Performance data (cont) | 5 | 5 | 19.03
32 | 1 | Performance data (cont) | 5 | 6 | 18.73
32 | 1 | Performance data (cont) | 5 | 7 | 18.42
32 | 1 | Performance data (cont) | 5 | 8 | 18.12
32 | 1 | Performance data (cont) | 5 | 9 | 17.8
32 | 1 | Performance data (cont) | 5 | 10 | 17.5
32 | 1 | Performance data (cont) | 5 | 11 | 17.19
32 | 1 | Performance data (cont) | 5 | 12 | 16.88
32 | 1 | Performance data (cont) | 6 | 1 | 17.82
32 | 1 | Performance data (cont) | 6 | 2 | 17.52
32 | 1 | Performance data (cont) | 6 | 3 | 17.21
32 | 1 | Performance data (cont) | 6 | 4 | 16.91
32 | 1 | Performance data (cont) | 6 | 5 | 16.61
32 | 1 | Performance data (cont) | 6 | 6 | 16.31
32 | 1 | Performance data (cont) | 6 | 7 | 16.01
32 | 1 | Performance data (cont) | 6 | 8 | 15.71
32 | 1 | Performance data (cont) | 6 | 9 | 15.4
32 | 1 | Performance data (cont) | 6 | 10 | 15.1
32 | 1 | Performance data (cont) | 6 | 11 | 14.8
32 | 1 | Performance data (cont) | 6 | 12 | †
32 | 1 | Performance data (cont) | 7 | 1 | 22.35
32 | 1 | Performance data (cont) | 7 | 2 | 21.97
32 | 1 | Performance data (cont) | 7 | 3 | 21.59
32 | 1 | Performance data (cont) | 7 | 4 | 21.22
32 | 1 | Performance data (cont) | 7 | 5 | 20.84
32 | 1 | Performance data (cont) | 7 | 6 | 20.46
32 | 1 | Performance data (cont) | 7 | 7 | 20.08
32 | 1 | Performance data (cont) | 7 | 8 | 19.7
32 | 1 | Performance data (cont) | 7 | 9 | 19.32
32 | 1 | Performance data (cont) | 7 | 10 | 18.95
32 | 1 | Performance data (cont) | 7 | 11 | 18.57
32 | 1 | Performance data (cont) | 7 | 12 | †
32 | 2 | Performance data (cont) | 1 | 1 | 0
32 | 2 | Performance data (cont) | 1 | 2 | 1/2
32 | 2 | Performance data (cont) | 1 | 3 | 1
32 | 2 | Performance data (cont) | 1 | 4 | 11/2
32 | 2 | Performance data (cont) | 1 | 5 | 2
32 | 2 | Performance data (cont) | 1 | 6 | 21/2
32 | 2 | Performance data (cont) | 1 | 7 | 3
32 | 2 | Performance data (cont) | 1 | 8 | 31/2
32 | 2 | Performance data (cont) | 1 | 9 | 4
32 | 2 | Performance data (cont) | 1 | 10 | 41/2
32 | 2 | Performance data (cont) | 1 | 11 | 5
32 | 2 | Performance data (cont) | 1 | 12 | 51/2
32 | 2 | Performance data (cont) | 2 | 1 | 983
32 | 2 | Performance data (cont) | 2 | 2 | 959
32 | 2 | Performance data (cont) | 2 | 3 | 935
32 | 2 | Performance data (cont) | 2 | 4 | 911
32 | 2 | Performance data (cont) | 2 | 5 | 887
32 | 2 | Performance data (cont) | 2 | 6 | 863
32 | 2 | Performance data (cont) | 2 | 7 | 839
32 | 2 | Performance data (cont) | 2 | 8 | 815
32 | 2 | Performance data (cont) | 2 | 9 | 791
32 | 2 | Performance data (cont) | 2 | 10 | 767
32 | 2 | Performance data (cont) | 2 | 11 | 743
32 | 2 | Performance data (cont) | 2 | 12 | †
32 | 2 | Performance data (cont) | 3 | 1 | 1300
32 | 2 | Performance data (cont) | 3 | 2 | 1272
32 | 2 | Performance data (cont) | 3 | 3 | 1245
32 | 2 | Performance data (cont) | 3 | 4 | 1217
32 | 2 | Performance data (cont) | 3 | 5 | 1189
32 | 2 | Performance data (cont) | 3 | 6 | 1162
32 | 2 | Performance data (cont) | 3 | 7 | 1134
32 | 2 | Performance data (cont) | 3 | 8 | 1106
32 | 2 | Performance data (cont) | 3 | 9 | 1078
32 | 2 | Performance data (cont) | 3 | 10 | 1051
32 | 2 | Performance data (cont) | 3 | 11 | 1023
32 | 2 | Performance data (cont) | 3 | 12 | †
32 | 2 | Performance data (cont) | 4 | 1 | 909
32 | 2 | Performance data (cont) | 4 | 2 | 895
32 | 2 | Performance data (cont) | 4 | 3 | 881
32 | 2 | Performance data (cont) | 4 | 4 | 867
32 | 2 | Performance data (cont) | 4 | 5 | 853
32 | 2 | Performance data (cont) | 4 | 6 | 839
32 | 2 | Performance data (cont) | 4 | 7 | 825
32 | 2 | Performance data (cont) | 4 | 8 | 811
32 | 2 | Performance data (cont) | 4 | 9 | 797
32 | 2 | Performance data (cont) | 4 | 10 | 783
32 | 2 | Performance data (cont) | 4 | 11 | 769
32 | 2 | Performance data (cont) | 4 | 12 | †
32 | 2 | Performance data (cont) | 5 | 1 | 1216
32 | 2 | Performance data (cont) | 5 | 2 | 1198
32 | 2 | Performance data (cont) | 5 | 3 | 1179
32 | 2 | Performance data (cont) | 5 | 4 | 1161
32 | 2 | Performance data (cont) | 5 | 5 | 1142
32 | 2 | Performance data (cont) | 5 | 6 | 1124
32 | 2 | Performance data (cont) | 5 | 7 | 1105
32 | 2 | Performance data (cont) | 5 | 8 | 1087
32 | 2 | Performance data (cont) | 5 | 9 | 1068
32 | 2 | Performance data (cont) | 5 | 10 | 1050
32 | 2 | Performance data (cont) | 5 | 11 | 1031
32 | 2 | Performance data (cont) | 5 | 12 | 1013
32 | 2 | Performance data (cont) | 6 | 1 | 1069
32 | 2 | Performance data (cont) | 6 | 2 | 1051
32 | 2 | Performance data (cont) | 6 | 3 | 1033
32 | 2 | Performance data (cont) | 6 | 4 | 1015
32 | 2 | Performance data (cont) | 6 | 5 | 997
32 | 2 | Performance data (cont) | 6 | 6 | 979
32 | 2 | Performance data (cont) | 6 | 7 | 960
32 | 2 | Performance data (cont) | 6 | 8 | 942
32 | 2 | Performance data (cont) | 6 | 9 | 924
32 | 2 | Performance data (cont) | 6 | 10 | 906
32 | 2 | Performance data (cont) | 6 | 11 | 888
32 | 2 | Performance data (cont) | 6 | 12 | †
32 | 2 | Performance data (cont) | 7 | 1 | 1341
32 | 2 | Performance data (cont) | 7 | 2 | 1318
32 | 2 | Performance data (cont) | 7 | 3 | 1296
32 | 2 | Performance data (cont) | 7 | 4 | 1273
32 | 2 | Performance data (cont) | 7 | 5 | 1250
32 | 2 | Performance data (cont) | 7 | 6 | 1228
32 | 2 | Performance data (cont) | 7 | 7 | 1205
32 | 2 | Performance data (cont) | 7 | 8 | 1182
32 | 2 | Performance data (cont) | 7 | 9 | 1159
32 | 2 | Performance data (cont) | 7 | 10 | 1137
32 | 2 | Performance data (cont) | 7 | 11 | 1114
32 | 2 | Performance data (cont) | 7 | 12 | †
32 | 3 | Performance data (cont) | 1 | 1 | UNIT RATED VOLTAGE
32 | 3 | Performance data (cont) | 1 | 2 | MAXIMUM ACCEPTABLE CONTINUOUS BHP*
32 | 3 | Performance data (cont) | 1 | 3 | MAXIMUM ACCEPTABLE CONTINUOUS BkW*
32 | 3 | Performance data (cont) | 1 | 4 | MAXIMUM ACCEPTABLE OPERATING WATTS
32 | 3 | Performance data (cont) | 2 | 1 | 220
32 | 3 | Performance data (cont) | 2 | 2 | 3.45
32 | 3 | Performance data (cont) | 2 | 3 | 3.17
32 | 3 | Performance data (cont) | 2 | 4 | 3065
32 | 3 | Performance data (cont) | 3 | 1 | 400
32 | 3 | Performance data (cont) | 3 | 2 | 4.25
32 | 3 | Performance data (cont) | 3 | 3 | 3.17
32 | 3 | Performance data (cont) | 3 | 4 | 3775
32 | 3 | Performance data (cont) | 4 | 1 | 220
32 | 3 | Performance data (cont) | 4 | 2 | 10.3
32 | 3 | Performance data (cont) | 4 | 3 | 7.68
32 | 3 | Performance data (cont) | 4 | 4 | 8640
32 | 3 | Performance data (cont) | 5 | 1 | 400
32 | 3 | Performance data (cont) | 5 | 2 | 10.3
32 | 3 | Performance data (cont) | 5 | 3 | 7.68
32 | 3 | Performance data (cont) | 5 | 4 | 8640
32 | 3 | Performance data (cont) | 6 | 1 | 220
32 | 3 | Performance data (cont) | 6 | 2 | 11.5
32 | 3 | Performance data (cont) | 6 | 3 | 8.6
32 | 3 | Performance data (cont) | 6 | 4 | 9600
32 | 3 | Performance data (cont) | 7 | 1 | 400
32 | 3 | Performance data (cont) | 7 | 2 | 13.3
32 | 3 | Performance data (cont) | 7 | 3 | 9.92
32 | 3 | Performance data (cont) | 7 | 4 | 11000

## Cooling_Capacity
source_page | table_no | page_title | table_row | col_1 | col_2 | col_3 | col_4 | col_5 | col_6 | col_7 | col_8 | col_9 | col_10 | col_11 | col_12 | col_13 | col_14 | col_15 | col_16 | col_17 | col_18 | col_19 | col_20 | col_21 | col_22 | col_23
19 | 1 | Performance data | 1 | col_1: 2124/0.12; col_2: 2478/0.14; col_3: 2832/0.15; col_4: 3186/0.17
19 | 2 | Performance data | 1 |  | 17 | 19 | 22 | 17 | 19 | 22 | 17 | 19 | 22 | 17 | 19 | 22 | 17 | 19
19 | 2 | Performance data | 2 | TC SHC kW | 49.0 41.6 11.3 | 53.3 35.5 11.7 | 58.7 28.8 13.3 | 50.3 45.1 11.5 | 54.9 37.8 11.9 | 60.3 30.6 13.4 | 51.8 47.5 11.6 | 56.5 40.1 12.0 | 61.3 32.0 13.5 | 52.8 50.2 11.7 | 57.1 43.1 12.0 | 61.9 34.7 13.6 | 53.9 52.7 11.7 | 57.6 45.2 12.1
19 | 2 | Performance data | 3 | TC SHC kW | 47.6 40.8 12.7 | 51.7 34.7 13.0 | 56.5 28.2 14.7 | 49.0 44.0 12.8 | 53.3 37.1 13.2 | 58.1 29.7 14.9 | 50.2 46.7 12.9 | 54.4 39.3 13.3 | 59.7 31.2 15.0 | 51.2 49.4 13.0 | 55.5 41.4 13.4 | 60.3 33.1 15.1 | 52.1 51.7 13.1 | 56.0 44.2 13.5
19 | 2 | Performance data | 4 | TC SHC kW | 46.0 40.0 14.1 | 50.1 33.8 14.5 | 54.9 27.4 16.3 | 47.4 43.1 14.3 | 51.5 36.2 14.6 | 56.5 28.9 16.5 | 48.5 45.9 14.4 | 52.6 38.5 14.7 | 57.6 30.3 16.6 | 49.4 48.5 14.5 | 53.3 40.6 14.9 | 58.7 31.5 16.7 | 50.4 50.4 14.6 | 54.4 42.8 15.0
19 | 2 | Performance data | 5 | TC SHC kW | 43.5 38.2 15.7 | 47.3 32.4 16.2 | 51.8 26.2 18.1 | 44.7 41.2 15.9 | 48.5 34.7 16.3 | 52.9 27.6 18.3 | 45.7 44.0 16.0 | 49.5 36.8 16.4 | 53.9 28.9 18.4 | 46.6 46.4 16.1 | 50.3 38.9 16.5 | 55.0 30.0 18.5 | 47.7 47.9 16.2 | 51.0 41.0 16.6
19 | 2 | Performance data | 6 | TC SHC kW | 40.8 36.5 17.4 | 44.4 31.0 17.9 | 48.7 24.9 18.4 | 41.9 39.5 17.6 | 45.5 33.2 18.0 | 49.9 26.3 18.6 | 42.7 42.2 17.7 | 46.4 35.3 18.1 | 50.5 27.6 18.7 | 43.9 44.1 17.9 | 47.1 37.2 18.3 | 51.0 28.7 18.7 | 44.9 45.2 18.0 | 47.6 39.2 18.3
19 | 2 | Performance data | 7 | TC SHC kW | 39.0 35.4 18.4 | 42.4 30.0 18.9 | 46.6 24.0 19.4 | 40.0 38.3 18.5 | 43.5 32.1 19.0 | 47.7 25.3 19.6 | 40.9 40.7 18.7 | 44.3 34.3 19.1 | 48.4 26.7 19.8 | 42.0 42.3 18.8 | 45.0 36.3 19.2 | 48.8 27.8 19.8 | 43.0 43.4 18.9 | 45.5 37.9 19.3
19 | 2 | Performance data | 8 | TC SHC kW | 37.2 34.2 19.3 | 40.5 29.0 19.7 | 44.2 23.8 20.3 | 38.1 36.9 19.4 | 41.4 31.1 19.9 | — — — | 39.1 39.2 19.6 | 42.2 33.1 20.1 | — — — | 40.2 40.5 19.7 | 42.9 35.0 20.1 | — — — | 41.2 41.5 19.9 | 43.3 36.6 20.1
19 | 3 | Performance data | 1 | col_1: 2832/0.075; col_2: 3304/0.085; col_3: 3776/0.100; col_4: 4248/0.110
19 | 4 | Performance data | 1 |  | 17 | 19 | 22 | 17 | 19 | 22 | 17 | 19 | 22 | 17 | 19 | 22 | 17 | 19
19 | 4 | Performance data | 2 | TC SHC kW | 64.3 55.1 15.1 | 70.9 46.5 15.6 | 76.9 36.9 16.5 | 65.9 59.5 15.2 | 72.7 49.7 15.8 | 78.8 38.9 16.7 | 67.2 63.6 15.4 | 74.1 53.0 15.9 | 80.3 40.8 16.9 | 68.4 67.2 15.5 | 75.0 56.0 16.0 | 81.3 42.8 17.0 | 69.7 69.6 15.7 | 75.8 59.1 16.1
19 | 4 | Performance data | 3 | TC SHC kW | 62.1 54.0 16.7 | 68.5 45.4 17.2 | 74.3 36.0 18.2 | 63.6 58.4 16.9 | 70.2 48.8 17.4 | 76.1 38.0 18.5 | 64.9 62.4 17.0 | 71.4 51.9 17.6 | 77.5 39.9 18.6 | 66.0 65.6 17.2 | 72.3 54.8 17.7 | 78.5 41.7 18.7 | 67.8 67.6 17.4 | 73.1 57.9 17.8
19 | 4 | Performance data | 4 | TC SHC kW | 59.8 53.0 18.5 | 65.9 44.4 19.0 | 71.6 35.0 20.1 | 61.2 57.1 18.7 | 67.4 47.7 19.2 | 73.2 37.0 20.3 | 62.4 61.0 18.8 | 68.6 50.7 19.3 | 74.4 38.9 20.4 | 63.8 63.7 19.0 | 69.4 53.6 19.4 | 75.3 40.6 20.5 | 65.3 65.1 19.1 | 70.0 56.7 19.5
19 | 4 | Performance data | 5 | TC SHC kW | 57.0 51.6 20.3 | 63.0 43.3 20.8 | 68.5 33.9 22.0 | 58.4 55.8 20.5 | 64.4 46.5 21.0 | 70.0 35.9 22.2 | 59.7 59.3 20.6 | 65.3 49.4 21.1 | 71.1 37.7 22.3 | 61.4 61.3 20.8 | 66.1 52.6 21.2 | 71.9 39.5 22.4 | 62.8 62.6 21.0 | 66.7 55.4 21.3
19 | 4 | Performance data | 6 | TC SHC kW | 54.2 50.2 22.1 | 59.9 42.0 22.7 | 65.2 32.8 23.9 | 55.6 54.3 22.3 | 61.2 45.3 22.8 | 66.6 34.7 24.1 | 57.1 56.9 22.5 | 62.1 48.3 23.0 | 67.6 36.5 24.2 | 58.7 58.6 22.7 | 62.7 51.1 23.1 | 68.3 38.3 24.3 | 60.0 59.8 22.9 | 63.2 53.7 23.2
19 | 4 | Performance data | 7 | TC SHC kW | 51.2 48.7 24.0 | 56.6 40.7 24.6 | — — — | 52.7 52.3 24.2 | 57.6 43.8 24.7 | — — — | 54.3 54.2 24.4 | 58.4 47.0 24.9 | — — — | 55.9 55.7 24.6 | 59.0 49.6 25.0 | — — — | 57.0 56.9 24.8 | 59.4 52.1 25.0
20 | 1 | Performance data (cont) | 1 | col_1: 3304/0.05; col_2: 3776/0.06; col_3: 4248/0.07; col_4: 4720/0.08
20 | 2 | Performance data (cont) | 1 |  | 17 | 19 | 22 | 17 | 19 | 22 | 17 | 19 | 22 | 17 | 19 | 22 | 17 | 19
20 | 2 | Performance data (cont) | 2 | TC SHC kW | 79.4 67.7 20.1 | 87.6 57.2 20.8 | 96.5 46.5 21.6 | 81.2 72.6 20.3 | 89.6 60.7 21.0 | 98.6 48.4 21.8 | 82.7 77.5 20.4 | 91.0 64.4 21.2 | 100.3 51.2 22.0 | 83.9 81.7 20.6 | 91.9 68.7 21.3 | 101.6 53.3 22.2 | 85.7 85.6 20.8 | 93.4 72.6 21.5
20 | 2 | Performance data (cont) | 3 | TC SHC kW | 76.6 66.5 22.2 | 84.5 55.9 23.0 | 93.1 45.0 23.8 | 78.3 71.2 22.4 | 86.4 59.4 23.2 | 95.0 47.4 24.0 | 79.8 75.6 22.6 | 88.0 62.9 23.4 | 96.6 49.4 24.2 | 81.0 79.7 22.8 | 89.1 66.4 23.5 | 98.1 51.6 24.4 | 83.1 83.0 23.0 | 90.4 70.5 23.7
20 | 2 | Performance data (cont) | 4 | TC SHC kW | 73.7 65.0 24.6 | 81.2 54.6 25.3 | 89.4 44.0 26.1 | 75.2 69.7 24.7 | 83.0 58.1 25.5 | 91.1 46.0 26.3 | 76.7 74.1 24.9 | 84.2 61.8 25.7 | 92.7 48.1 26.5 | 78.1 77.7 25.1 | 85.5 64.8 25.8 | 94.0 50.1 26.7 | 80.3 80.2 25.4 | 86.6 68.9 26.0
20 | 2 | Performance data (cont) | 5 | TC SHC kW | 70.5 63.3 27.0 | 77.8 53.3 27.8 | 85.4 42.6 28.6 | 71.9 68.0 27.2 | 79.2 56.5 28.0 | 87.2 44.7 28.8 | 73.5 72.0 27.4 | 80.4 60.1 28.1 | 88.6 46.6 29.0 | 75.0 75.0 27.6 | 81.4 63.3 28.3 | 89.6 48.8 29.2 | 77.2 77.1 27.9 | 82.5 67.2 28.4
20 | 2 | Performance data (cont) | 6 | TC SHC kW | 67.1 61.9 29.5 | 74.0 51.8 30.3 | 81.2 41.0 31.1 | 68.4 66.2 29.7 | 75.3 55.0 30.5 | 82.5 43.1 31.3 | 70.0 69.8 30.0 | 76.4 58.4 30.7 | 83.6 44.9 31.5 | 71.9 71.8 30.2 | 77.3 61.7 30.8 | — — — | 73.8 73.8 30.5 | 78.2 65.4 31.0
20 | 2 | Performance data (cont) | 7 | TC SHC kW | 66.1 61.4 30.3 | 72.7 51.3 31.1 | — — — | 67.4 65.6 30.5 | 73.9 54.5 31.2 | — — — | 68.9 68.8 30.7 | 74.8 57.8 31.4 | — — — | 70.6 70.5 31.0 | 75.5 61.1 31.5 | — — — | 72.4 72.4 31.2 | — — —
20 | 2 | Performance data (cont) | 8 | TC SHC kW | 65.2 60.9 30.8 | — — — | — — — | 66.6 65.2 31.0 | — — — | — — — | 68.4 68.4 31.3 | — — — | — — — | 70.0 70.0 31.5 | — — — | — — — | — — — | — — —
20 | 3 | Performance data (cont) | 1 | col_1: 3304/0.05; col_2: 3776/0.06; col_3: 4248/0.07; col_4: 4720/0.08
20 | 4 | Performance data (cont) | 1 |  | 17 | 19 | 22 | 17 | 19 | 22 | 17 | 19 | 22 | 17 | 19 | 22 | 17 | 19
20 | 4 | Performance data (cont) | 2 | TC SHC kW | 82.3 69.1 18.2 | 90.8 58.8 18.8 | 100.5 47.8 19.4 | 84.4 74.1 18.4 | 93.2 62.6 19.0 | 102.8 50.3 19.6 | 85.6 79.7 18.5 | 94.6 66.9 19.1 | 104.0 54.3 19.7 | 87.3 83.2 18.6 | 95.8 70.2 19.2 | 105.8 56.6 19.9 | 89.1 87.9 18.8 | 97.3 75.3 19.4
20 | 4 | Performance data (cont) | 3 | TC SHC kW | 79.7 68.0 20.3 | 87.9 57.4 20.8 | 97.3 46.6 21.5 | 81.7 73.0 20.4 | 90.5 61.1 21.0 | 99.6 49.1 21.7 | 83.2 77.6 20.6 | 92.0 65.0 21.2 | 101.7 51.4 21.8 | 84.7 81.7 20.8 | 93.2 68.0 21.4 | 102.8 53.7 22.0 | 86.7 85.8 20.9 | 94.3 73.2 21.4
20 | 4 | Performance data (cont) | 4 | TC SHC kW | 76.8 66.5 22.6 | 85.3 56.2 23.1 | 93.8 45.6 23.7 | 78.5 71.5 22.6 | 87.0 59.7 23.3 | 95.8 47.8 23.9 | 80.3 75.6 22.8 | 88.5 63.1 23.4 | 97.6 49.9 24.1 | 81.7 79.4 23.0 | 90.0 66.6 23.6 | 99.0 52.0 24.2 | 83.5 82.9 23.1 | 91.1 70.6 23.6
20 | 4 | Performance data (cont) | 5 | TC SHC kW | 73.8 65.1 24.9 | 81.7 54.7 25.5 | 90.0 44.2 26.1 | 75.6 69.6 25.0 | 83.5 58.5 25.7 | 91.7 46.4 26.3 | 77.1 74.1 25.2 | 85.0 61.6 25.8 | 93.5 48.4 26.5 | 78.5 77.4 25.3 | 86.1 65.0 25.9 | 94.6 50.5 26.5 | 80.9 80.6 25.5 | 87.0 69.4 26.0
20 | 4 | Performance data (cont) | 6 | TC SHC kW | 70.3 63.5 27.3 | 77.9 53.3 27.9 | 85.6 42.7 28.5 | 72.1 68.0 27.5 | 79.7 57.0 28.1 | 87.6 44.8 28.7 | 73.8 71.8 27.7 | 80.9 60.4 28.3 | 88.8 47.0 28.9 | 75.6 75.0 27.8 | 81.7 63.5 28.3 | 90.2 49.5 28.9 | 77.6 77.4 28.0 | 82.9 67.8 28.5
20 | 4 | Performance data (cont) | 7 | TC SHC kW | 67.0 61.8 29.9 | 73.8 51.9 30.4 | 81.5 41.2 31.1 | 68.6 66.1 30.0 | 75.6 55.4 30.6 | 82.9 43.2 31.2 | 70.3 69.1 30.2 | 76.5 58.5 30.7 | 84.1 45.3 31.3 | 71.8 71.8 30.4 | 77.4 61.6 30.7 | 85.3 47.1 31.5 | 73.8 73.8 30.6 | 77.9 65.6 30.9
21 | 1 | COOLING CAPACITIES — ENGLISH | 1 | col_1: 4500/0.12; col_2: 5250/0.14; col_3: 6000/0.15; col_4: 6750/0.17
21 | 2 | COOLING CAPACITIES — ENGLISH | 1 |  | 62 | 67 | 72 | 62 | 67 | 72 | 62 | 67 | 72 | 62 | 67 | 72 | 62 | 67
21 | 2 | COOLING CAPACITIES — ENGLISH | 2 | TC SHC kW | 167 142 11.3 | 182 121 11.7 | 200 98 13.3 | 172 154 11.5 | 188 129 11.9 | 206 104 13.4 | 177 162 11.6 | 193 137 12.0 | 209 109 13.5 | 180 171 11.7 | 195 147 12.0 | 211 118 13.6 | 184 180 11.7 | 197 154 12.1
21 | 2 | COOLING CAPACITIES — ENGLISH | 3 | TC SHC kW | 162 139 12.7 | 177 118 13.0 | 193 96 14.7 | 167 150 12.8 | 182 126 13.2 | 198 101 14.9 | 171 159 12.9 | 186 134 13.3 | 204 107 15.0 | 175 168 13.0 | 189 141 13.4 | 206 113 15.1 | 178 176 13.1 | 191 151 13.5
21 | 2 | COOLING CAPACITIES — ENGLISH | 4 | TC SHC kW | 157 137 14.1 | 171 115 14.5 | 188 94 16.3 | 162 147 14.3 | 176 124 14.6 | 193 99 16.5 | 165 157 14.4 | 180 131 14.7 | 197 103 16.6 | 169 166 14.5 | 182 139 14.9 | 200 108 16.7 | 172 172 14.6 | 186 146 15.0
21 | 2 | COOLING CAPACITIES — ENGLISH | 5 | TC SHC kW | 148 130 15.7 | 162 111 16.2 | 177 89 18.1 | 153 140 15.9 | 166 119 16.3 | 180 94 18.3 | 156 150 16.0 | 169 126 16.4 | 184 99 18.4 | 159 158 16.1 | 172 133 16.5 | 188 103 18.5 | 163 163 16.2 | 174 140 16.6
21 | 2 | COOLING CAPACITIES — ENGLISH | 6 | TC SHC kW | 139 125 17.4 | 152 106 17.9 | 166 85 18.4 | 143 135 17.6 | 155 113 18.0 | 170 90 18.6 | 146 144 17.7 | 158 121 18.1 | 173 94 18.7 | 150 150 17.9 | 161 127 18.3 | 174 98 18.7 | 153 154 18.0 | 163 134 18.3
21 | 2 | COOLING CAPACITIES — ENGLISH | 7 | TC SHC kW | 133 121 18.4 | 145 102 18.9 | 159 82 19.4 | 136 131 18.5 | 148 110 19.0 | 163 86 19.6 | 140 139 18.7 | 151 117 19.1 | 165 91 19.8 | 143 144 18.8 | 154 124 19.2 | 166 95 19.8 | 147 148 18.9 | 155 129 19.3
21 | 2 | COOLING CAPACITIES — ENGLISH | 8 | TC SHC kW | 127 117 19.3 | 138 99 19.7 | 151 81 20.3 | 130 126 19.4 | 141 106 19.9 | — — — | 134 134 19.6 | 144 113 20.1 | — — — | 137 138 19.7 | 146 119 20.1 | — — — | 140 142 19.9 | 148 125 20.1
21 | 3 | COOLING CAPACITIES — ENGLISH | 1 | col_1: 6000/0.075; col_2: 7000/0.085; col_3: 8000/0.10; col_4: 9000/0.11
21 | 4 | COOLING CAPACITIES — ENGLISH | 1 |  | 62 | 67 | 72 | 62 | 67 | 72 | 62 | 67 | 72 | 62 | 67 | 72 | 62 | 67
21 | 4 | COOLING CAPACITIES — ENGLISH | 2 | TC SHC kW | 219.5 188.0 15.1 | 242.0 158.6 15.6 | 262.6 125.9 16.5 | 224.9 203.2 15.2 | 248.0 169.6 15.8 | 268.8 132.7 16.7 | 229.2 217.0 15.4 | 252.8 180.7 15.9 | 274.0 139.3 16.9 | 233.3 229.5 15.5 | 256.1 191.1 16.0 | 277.5 146.1 17.0 | 238.0 237.6 15.7 | 258.8 201.7 16.1
21 | 4 | COOLING CAPACITIES — ENGLISH | 3 | TC SHC kW | 211.9 184.5 16.7 | 233.6 154.9 17.2 | 253.5 122.7 18.2 | 217.1 199.3 16.9 | 239.6 166.7 17.4 | 259.8 129.6 18.5 | 221.4 212.9 17.0 | 243.8 177.0 17.6 | 264.6 136.1 18.6 | 225.2 224.0 17.2 | 246.8 187.2 17.7 | 267.9 142.3 18.7 | 231.3 230.7 17.4 | 249.5 197.6 17.8
21 | 4 | COOLING CAPACITIES — ENGLISH | 4 | TC SHC kW | 204.1 180.8 18.5 | 224.9 151.7 19.0 | 244.2 119.4 20.1 | 208.8 194.9 18.7 | 229.9 162.7 19.2 | 249.8 126.3 20.3 | 213.0 208.3 18.8 | 234.0 173.2 19.3 | 253.9 132.7 20.4 | 217.6 217.2 19.0 | 236.8 183.0 19.4 | 256.9 138.7 20.5 | 222.9 222.4 19.1 | 239.1 193.4 19.5
21 | 4 | COOLING CAPACITIES — ENGLISH | 5 | TC SHC kW | 194.5 176.2 20.3 | 215.0 147.8 20.8 | 233.7 115.7 22.0 | 199.5 190.4 20.5 | 219.8 158.7 21.0 | 238.9 122.5 22.2 | 203.8 202.5 20.6 | 223.0 168.7 21.1 | 242.7 128.8 22.3 | 209.6 209.3 20.8 | 225.6 179.6 21.2 | 245.5 134.9 22.4 | 214.3 213.8 21.0 | 227.6 189.0 21.3
21 | 4 | COOLING CAPACITIES — ENGLISH | 6 | TC SHC kW | 185.1 171.5 22.1 | 204.6 143.3 22.7 | 222.6 111.9 23.9 | 189.8 185.2 22.3 | 208.9 154.7 22.8 | 227.3 118.5 24.1 | 194.8 194.3 22.5 | 211.8 164.9 23.0 | 230.6 124.5 24.2 | 200.4 199.9 22.7 | 214.0 174.3 23.1 | 233.2 130.7 24.3 | 204.6 204.2 22.9 | 215.8 183.3 23.2
21 | 4 | COOLING CAPACITIES — ENGLISH | 7 | TC SHC kW | 174.9 166.2 24.0 | 193.1 138.7 24.6 | — — — | 179.9 178.5 24.2 | 196.7 149.5 24.7 | — — — | 185.3 184.9 24.4 | 199.5 160.3 24.9 | — — — | 190.6 190.2 24.6 | 201.4 169.4 25.0 | — — — | 194.7 194.0 24.8 | 202.8 177.7 25.0
22 | 1 | Performance data (cont) | 1 | col_1: 7000/0.05; col_2: 8000/0.06; col_3: 9000/0.07; col_4: 10,000/0.08
22 | 2 | Performance data (cont) | 1 |  | 62 | 67 | 72 | 62 | 67 | 72 | 62 | 67 | 72 | 62 | 67 | 72 | 62 | 67
22 | 2 | Performance data (cont) | 2 | TC SHC kW | 270.9 231.2 20.1 | 298.9 195.1 20.8 | 329.5 158.8 21.6 | 277.1 247.7 20.3 | 305.7 207.1 21.0 | 336.5 165.1 21.8 | 282.2 264.4 20.4 | 310.5 219.8 21.2 | 342.2 174.6 22.0 | 286.2 278.8 20.6 | 313.6 234.5 21.3 | 346.8 181.9 22.2 | 292.5 292.1 20.8 | 318.6 247.9 21.5
22 | 2 | Performance data (cont) | 3 | TC SHC kW | 261.5 226.8 22.2 | 288.5 190.8 23.0 | 317.7 153.6 23.8 | 267.1 243.1 22.4 | 295.0 202.9 23.2 | 324.2 161.9 24.0 | 272.5 257.9 22.6 | 300.2 214.6 23.4 | 329.8 168.8 24.2 | 276.5 272.2 22.8 | 304.2 226.7 23.5 | 334.8 176.0 24.4 | 283.5 283.3 23.0 | 308.4 240.5 23.7
22 | 2 | Performance data (cont) | 4 | TC SHC kW | 251.5 221.8 24.6 | 277.2 186.4 25.3 | 305.1 150.1 26.1 | 256.6 237.9 24.7 | 283.3 198.3 25.5 | 311.0 157.1 26.3 | 261.9 252.7 24.9 | 287.3 211.0 25.7 | 316.5 164.2 26.5 | 266.4 265.2 25.1 | 291.9 221.3 25.8 | 320.8 171.0 26.7 | 274.0 273.7 25.4 | 295.4 235.0 26.0
22 | 2 | Performance data (cont) | 5 | TC SHC kW | 240.6 215.9 27.0 | 265.7 181.8 27.8 | 291.4 145.2 28.6 | 245.5 231.9 27.2 | 270.5 192.9 28.0 | 297.8 152.5 28.8 | 250.7 245.8 27.4 | 274.6 205.0 28.1 | 302.2 159.2 29.0 | 256.0 255.9 27.6 | 277.9 216.1 28.3 | 305.7 166.5 29.2 | 263.4 263.2 27.9 | 281.4 229.5 28.4
22 | 2 | Performance data (cont) | 6 | TC SHC kW | 229.0 211.2 29.5 | 252.4 176.8 30.3 | 277.3 140.0 31.1 | 233.5 225.9 29.7 | 256.9 187.6 30.5 | 281.5 147.1 31.3 | 239.0 238.3 30.0 | 260.6 199.4 30.7 | 285.4 153.4 31.5 | 245.2 245.0 30.2 | 263.7 210.6 30.8 | — — — | 252.0 251.9 30.5 | 267.0 223.2 31.0
22 | 2 | Performance data (cont) | 7 | TC SHC kW | 225.6 209.6 30.3 | 248.0 175.1 31.1 | — — — | 230.0 223.9 30.5 | 252.3 186.0 31.2 | — — — | 235.1 234.7 30.7 | 255.3 197.4 31.4 | — — — | 240.9 240.5 31.0 | 257.5 208.6 31.5 | — — — | 247.2 247.1 31.2 | — — —
22 | 2 | Performance data (cont) | 8 | TC SHC kW | 222.6 208.0 30.8 | — — — | — — — | 227.4 222.5 31.0 | — — — | — — — | 233.6 233.3 31.3 | — — — | — — — | 239.0 239.0 31.5 | — — — | — — — | — — — | — — —
22 | 3 | Performance data (cont) | 1 | col_1: 7000/0.05; col_2: 8000/0.06; col_3: 9000/0.07; col_4: 10,000/0.08
22 | 4 | Performance data (cont) | 1 |  | 62 | 67 | 72 | 62 | 67 | 72 | 62 | 67 | 72 | 62 | 67 | 72 | 62 | 67
22 | 4 | Performance data (cont) | 2 | TC SHC kW | 281 236 18.2 | 310 201 18.8 | 343 163 19.4 | 288 253 18.4 | 318 214 19.0 | 351 172 19.6 | 292 272 18.5 | 323 228 19.1 | 355 185 19.7 | 298 284 18.6 | 327 240 19.2 | 361 193 19.9 | 304 300 18.8 | 332 257 19.4
22 | 4 | Performance data (cont) | 3 | TC SHC kW | 272 232 20.3 | 300 196 20.8 | 332 159 21.5 | 279 249 20.4 | 309 209 21.0 | 340 168 21.7 | 284 265 20.6 | 314 222 21.2 | 347 176 21.8 | 289 279 20.8 | 318 232 21.4 | 351 183 22.0 | 296 293 20.9 | 322 250 21.4
22 | 4 | Performance data (cont) | 4 | TC SHC kW | 262 227 22.6 | 291 192 23.1 | 320 156 23.7 | 268 244 22.6 | 297 204 23.3 | 327 163 23.9 | 274 258 22.8 | 302 216 23.4 | 333 170 24.1 | 279 271 23.0 | 307 227 23.6 | 338 178 24.2 | 285 283 23.1 | 311 241 23.6
22 | 4 | Performance data (cont) | 5 | TC SHC kW | 252 222 24.9 | 279 187 25.5 | 307 151 26.1 | 258 238 25.0 | 285 200 25.7 | 313 158 26.3 | 263 253 25.2 | 290 210 25.8 | 319 165 26.5 | 268 264 25.3 | 294 222 25.9 | 323 172 26.5 | 276 275 25.5 | 297 237 26.0
22 | 4 | Performance data (cont) | 6 | TC SHC kW | 240 217 27.3 | 266 182 27.9 | 292 146 28.5 | 246 232 27.5 | 272 194 28.1 | 299 153 28.7 | 252 245 27.7 | 276 206 28.3 | 303 160 28.9 | 258 256 27.8 | 279 217 28.3 | 308 169 28.9 | 265 264 28.0 | 283 231 28.5
22 | 4 | Performance data (cont) | 7 | TC SHC kW | 229 211 29.9 | 252 177 30.4 | 278 141 31.1 | 234 226 30.0 | 258 189 30.6 | 283 148 31.2 | 240 236 30.2 | 261 200 30.7 | 287 155 31.3 | 245 245 30.4 | 264 210 30.7 | 291 161 31.5 | 252 252 30.6 | 266 224 30.9

## Fan_Performance
source_page | table_no | page_title | table_row | col_1 | col_2 | col_3 | col_4 | col_5 | col_6 | col_7 | col_8 | col_9 | col_10 | col_11 | col_12 | col_13 | col_14 | col_15 | col_16 | col_17 | col_18 | col_19 | col_20 | col_21 | col_22 | col_23
24 | 1 | Performance data (cont) | 1 | col_1: 50; col_4: 100; col_7: 149; col_10: 199; col_13: 249
24 | 1 | Performance data (cont) | 2 | r/s | BkW | kW | r/s | BkW | kW | r/s | BkW | kW | r/s | BkW | kW | r/s | BkW | kW | r/s | BkW
24 | 1 | Performance data (cont) | 3 | 11.4 11.9 12.4 13.0 13.5 14.1 14.6 15.2 15.8 16.3 16.9 | 0.95 1.09 1.24 1.40 1.58 1.77 1.98 2.20 2.44 2.69 2.95 | 1.10 1.26 1.44 1.64 1.84 2.07 2.31 2.57 2.84 3.13 3.44 | 13.2 13.6 14.1 14.5 15.0 15.5 16.0 16.5 17.0 17.6 18.1 | 1.10 1.24 1.40 1.57 1.75 1.95 2.16 2.39 2.62 2.88 3.15 | 1.28 1.45 1.63 1.83 2.04 2.27 2.52 2.78 3.06 3.36 3.67 | 14.8 15.2 15.6 16.0 16.4 16.9 17.3 17.8 18.3 18.8 — | 1.26 1.41 1.57 1.74 1.93 2.13 2.34 2.57 2.81 3.07 — | 1.47 1.64 1.83 2.03 2.25 2.48 2.73 2.99 3.28 3.58 — | 16.3 16.6 17.0 17.3 17.7 18.1 18.5 19.0 19.4 — — | 1.42 1.57 1.73 1.91 2.10 2.30 2.52 2.75 3.00 — — | 1.65 1.83 2.02 2.23 2.45 2.69 2.94 3.21 3.50 — — | 17.7 18.0 18.3 18.6 19.0 19.3 19.7 20.1 20.5 — — | 1.58 1.73 1.90 2.08 2.28 2.48 2.70 2.94 3.19 — — | 1.84 2.02 2.22 2.43 2.65 2.89 3.15 3.43 3.72 — — | 19.0 19.2 19.5 19.8 20.1 20.5 20.8 21.2 — — — | 1.75 1.90 2.07 2.26 2.45 2.66 2.89 3.13 — — —
24 | 2 | Performance data (cont) | 1 | col_1: 349; col_4: 399; col_7: 448; col_10: 473
24 | 2 | Performance data (cont) | 2 | r/s | BkW | kW | r/s | BkW | kW | r/s | BkW | kW | r/s | BkW | kW | r/s | BkW
24 | 2 | Performance data (cont) | 3 | 20.2 20.5 20.7 21.0 21.3 21.6 21.9 — — — — | 1.91 2.07 2.25 2.43 2.63 2.84 3.07 — — — — | 2.23 2.42 2.62 2.83 3.07 3.32 3.58 — — — — | 21.4 21.6 21.8 22.1 22.4 22.7 — — — — — | 2.08 2.25 2.42 2.61 2.81 3.03 — — — — — | 2.43 2.62 2.82 3.04 3.28 3.53 — — — — — | 22.6 22.7 22.9 23.2 23.4 23.7 — — — — — | 2.26 2.42 2.60 2.79 3.00 3.21 — — — — — | 2.63 2.82 3.03 3.25 3.49 3.75 — — — — — | 23.1 23.3 23.5 23.7 23.9 — — — — — — | 2.35 2.51 2.69 2.88 3.09 — — — — — — | 2.74 2.93 3.14 3.36 3.60 — — — — — — | 23.6 23.8 24.0 24.2 24.4 — — — — — — | 2.44 2.60 2.78 2.97 3.18 — — — — — —
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 1 | col_1: 50; col_4: 100; col_7: 149; col_10: 199; col_13: 249; col_16: 299; col_19: 349
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | r/s | BkW | kW | r/s | BkW | kW | r/s | BkW | kW | r/s | BkW | kW | r/s | BkW | kW | r/s | BkW | kW | r/s | BkW | kW | r/s | BkW
25 | 1 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | 11.4 12.2 13.0 13.8 14.6 15.5 16.3 17.2 18.0 18.9 | 1.49 1.76 2.09 2.45 2.84 3.27 3.74 4.24 4.78 5.36 | 1.68 2.01 2.37 2.78 3.23 3.72 4.24 4.82 5.43 6.09 | 12.7 13.4 14.1 14.9 15.6 16.4 17.2 18.0 18.8 19.7 | 1.71 1.99 2.31 2.68 3.07 3.51 3.98 4.49 5.03 5.62 | 1.92 2.26 2.63 3.04 3.49 3.99 4.52 5.10 5.72 6.38 | 13.9 14.5 15.2 15.9 16.6 17.3 18.1 18.9 19.6 20.4 | 1.94 2.21 2.55 2.91 3.31 3.75 4.22 4.74 5.29 5.87 | 2.18 2.52 2.89 3.31 3.77 4.26 4.80 5.38 6.01 6.68 | 15.0 15.6 16.2 16.8 17.5 18.2 18.9 19.7 20.4 21.2 | 2.17 2.45 2.78 3.15 3.56 4.00 4.48 4.99 5.54 6.13 | 2.44 2.78 3.16 3.58 4.04 4.54 5.09 5.67 6.30 6.97 | 16.1 16.6 17.2 17.8 18.4 19.1 19.7 20.4 21.2 21.9 | 2.41 2.69 3.03 3.40 3.81 4.25 4.73 5.25 5.80 6.40 | 2.71 3.06 3.44 3.86 4.33 4.83 5.38 5.96 6.60 7.27 | 17.1 17.6 18.1 18.7 19.3 19.9 20.5 21.2 21.9 22.6 | 2.66 2.94 3.28 3.65 4.06 4.51 4.99 5.51 6.07 6.67 | 2.99 3.34 3.72 4.15 4.61 5.12 5.67 6.26 6.90 7.57 | 18.1 18.5 19.0 19.6 20.1 20.7 21.3 21.9 22.6 23.3 | 2.91 3.19 3.53 3.91 4.32 4.77 5.25 5.77 6.33 6.93 | 3.28 3.62 4.01 4.44 4.91 5.41 5.97 6.56 7.20 7.88 | 19.0 19.4 19.9 20.4 20.9 21.5 22.1 22.7 23.3 24.0 | 3.17 3.45 3.79 4.16 4.58 5.03 5.52 6.04 6.60 7.21
25 | 2 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 1 | col_1: 448; col_4: 473
25 | 2 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 2 | col_1: r/s; col_2: BkW; col_3: kW; col_4: r/s; col_5: BkW; col_6: kW; col_7: r/s; col_8: BkW
25 | 2 | FAN PERFORMANCE — 50TJ016-028 — SI (cont) | 3 | col_1: 20.0 20.3 20.7 21.2 21.7 22.2 22.8 23.4 24.0 24.6; col_2: 3.43 3.71 4.05 4.43 4.84 5.30 5.78 6.31 6.88 7.48; col_3: 3.86 4.21 4.60 5.03 5.50 6.02 6.57 7.17 7.82 8.50; col_4: 20.4 20.8 21.2 21.6 22.1 22.6 23.2 23.7 24.3 —; col_5: 3.57 3.84 4.18 4.56 4.98 5.43 5.92 6.45 7.02 —; col_6: 4.02 4.36 4.75 5.18 5.66 6.17 6.73 7.33 7.97 —; col_7: 20.8 21.2 21.6 22.0 22.5 23.0 23.5 24.1 24.7 —; col_8: 3.71 3.97 4.32 4.70 5.11 5.57 6.06 6.59 7.15 —
26 | 1 | Performance data (cont) | 1 | col_1: 50; col_4: 100; col_7: 149; col_10: 199; col_13: 249; col_16: 299
26 | 1 | Performance data (cont) | 2 | r/s | BkW | kW | r/s | BkW | kW | r/s | BkW | kW | r/s | BkW | kW | r/s | BkW | kW | r/s | BkW | kW | r/s | BkW
26 | 1 | Performance data (cont) | 3 | 14.1 14.9 15.8 16.7 17.6 18.4 19.3 20.2 21.1 21.5 | 2.41 2.82 3.28 3.78 4.33 4.92 5.56 6.25 6.99 7.38 | 2009 2355 2735 3153 3608 4102 4635 5210 5826 6151 | 15.1 15.9 16.7 17.6 18.4 19.2 20.1 20.9 21.8 22.2 | 2.67 3.09 3.55 4.06 4.61 5.21 5.86 6.56 7.30 7.69 | 2222 2574 2961 3384 3845 4345 4884 5464 6086 6413 | 16.2 16.9 17.7 18.4 19.2 20.0 20.8 21.7 22.5 22.9 | 2.93 3.36 3.83 4.34 4.90 5.51 6.16 6.87 7.62 8.01 | 2441 2799 3191 3620 4087 4592 5137 5722 6349 6679 | 17.1 17.8 18.5 19.3 20.0 20.8 21.6 22.4 23.2 23.6 | 3.20 3.63 4.11 4.63 5.20 5.81 6.47 7.18 7.94 8.34 | 2666 3029 3427 3861 4332 4843 5393 5983 6616 6948 | 18.1 18.7 19.4 20.1 20.8 21.5 22.3 23.1 23.8 24.2 | 3.48 3.92 4.40 4.93 5.50 6.12 6.78 7.50 8.26 8.66 | 2897 3264 3667 4106 4582 5097 5652 6248 6885 7219 | 19.0 19.6 20.2 20.9 21.6 22.3 23.0 23.7 24.5 24.9 | 3.76 4.20 4.69 5.22 5.80 6.43 7.10 7.82 8.59 8.99 | 3133 3504 3911 4355 4836 5356 5915 6515 7157 7494 | 19.8 20.4 21.0 21.6 22.3 23.0 23.7 24.4 25.1 25.5 | 4.05 4.50 4.99 5.53 6.11 6.74 7.42 8.14 8.92 9.32
26 | 2 | Performance data (cont) | 1 | col_1: 399
26 | 2 | Performance data (cont) | 2 | col_1: r/s; col_2: BkW; col_3: kW; col_4: r/s; col_5: BkW
26 | 2 | Performance data (cont) | 3 | col_1: 20.7 21.2 21.8 22.4 23.0 23.7 24.4 25.1 25.8 —; col_2: 4.34 4.80 5.30 5.84 6.42 7.06 7.74 8.47 9.25 —; col_3: 3621 4000 4414 4866 5355 5883 6451 7060 7710 —; col_4: 21.5 22.0 22.5 23.1 23.7 24.4 25.0 25.7 — —; col_5: 3.63 4.11 4.63 5.20 5.81 6.47 7.18 7.94 — —
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 1 | col_1: 0.2; col_4: 0.4; col_7: 0.6; col_10: 0.8; col_13: 1
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | Rpm | Bhp | Watts | Rpm | Bhp | Watts | Rpm | Bhp | Watts | Rpm | Bhp | Watts | Rpm | Bhp | Watts | Rpm | Bhp
27 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 684 715 747 779 812 845 878 912 946 981 1016 | 1.28 1.47 1.67 1.90 2.14 2.40 2.68 2.98 3.29 3.63 3.99 | 1102 1265 1442 1635 1844 2068 2309 2566 2841 3133 3443 | 791 817 844 872 901 931 961 992 1023 1055 1087 | 1.49 1.68 1.89 2.12 2.37 2.64 2.92 3.22 3.55 3.89 4.25 | 1283 1451 1633 1831 2044 2273 2518 2780 3059 3355 3669 | 887 910 934 959 985 1011 1039 1067 1096 1125 — | 1.70 1.90 2.12 2.35 2.60 2.87 3.16 3.47 3.80 4.15 — | 1466 1638 1825 2027 2245 2478 2728 2994 3277 3578 — | 977 997 1018 1040 1063 1087 1112 1138 1165 — — | 1.92 2.12 2.34 2.58 2.84 3.11 3.41 3.72 4.05 — — | 1652 1828 2019 2226 2448 2685 2939 3209 3496 — — | 1061 1078 1097 1117 1138 1160 1183 1207 1232 — — | 2.13 2.34 2.57 2.81 3.07 3.35 3.65 3.97 4.31 — — | 1841 2021 2216 2426 2652 2893 3151 3425 3716 — — | 1139 1155 1171 1189 1209 1229 1250 1273 — — — | 2.36 2.57 2.80 3.05 3.31 3.60 3.90 4.22 — — —
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 1 | col_1: 1.4; col_4: 1.6; col_7: 1.8; col_10: 1.9
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 2 | Rpm | Bhp | Watts | Rpm | Bhp | Watts | Rpm | Bhp | Watts | Rpm | Bhp | Watts | Rpm | Bhp
27 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH | 3 | 1214 1228 1243 1259 1277 1295 1315 — — — — | 2.59 2.80 3.04 3.29 3.56 3.84 4.15 — — — — | 2230 2417 2618 2835 3067 3316 3580 — — — — | 1285 1297 1311 1326 1342 1359 — — — — — | 2.82 3.04 3.27 3.53 3.80 4.09 — — — — — | 2430 2619 2823 3043 3278 3530 — — — — — | 1353 1364 1376 1390 1405 1421 — — — — — | 3.05 3.27 3.51 3.77 4.05 4.34 — — — — — | 2633 2825 3031 3254 3492 3746 — — — — — | 1386 1396 1408 1421 1435 — — — — — — | 3.17 3.40 3.64 3.90 4.17 — — — — — — | 2736 2928 3136 3360 3600 — — — — — — | 1418 1428 1439 1452 1466 — — — — — — | 3.29 3.52 3.76 4.02 4.30 — — — — — —
28 | 1 | Performance data (cont) | 1 | col_1: 0.2; col_4: 0.4; col_7: 0.6; col_10: 0.8; col_13: 1; col_16: 1.2
28 | 1 | Performance data (cont) | 2 | Rpm | Bhp | Watts | Rpm | Bhp | Watts | Rpm | Bhp | Watts | Rpm | Bhp | Watts | Rpm | Bhp | Watts | Rpm | Bhp | Watts | Rpm | Bhp
28 | 1 | Performance data (cont) | 3 | 682 730 778 828 878 928 979 1030 1082 1134 | 1.99 2.38 2.82 3.31 3.84 4.42 5.05 5.73 6.46 7.25 | 1675 2005 2373 2780 3227 3715 4245 4817 5433 6093 | 760 802 846 892 938 985 1033 1082 1131 1180 | 2.29 2.68 3.13 3.62 4.15 4.74 5.38 6.06 6.80 7.59 | 1922 2257 2630 3042 3494 3986 4521 5098 5718 6382 | 832 871 911 953 996 1040 1085 1131 1178 1226 | 2.59 2.99 3.44 3.94 4.48 5.07 5.71 6.40 7.14 7.94 | 2177 2516 2893 3310 3766 4263 4801 5382 6007 6675 | 901 935 972 1011 1051 1093 1136 1180 1225 1270 | 2.90 3.31 3.76 4.26 4.81 5.40 6.05 6.74 7.49 8.29 | 2441 2783 3164 3583 4043 4544 5086 5671 6299 6971 | 965 997 1031 1067 1105 1144 1185 1227 1270 1313 | 3.22 3.63 4.09 4.59 5.14 5.74 6.39 7.09 7.84 8.65 | 2712 3057 3440 3863 4326 4830 5375 5964 6595 7271 | 1027 1056 1087 1121 1156 1194 1232 1272 1313 1356 | 3.56 3.97 4.43 4.93 5.49 6.09 6.74 7.44 8.20 9.01 | 2990 3337 3722 4148 4613 5120 5669 6260 6895 7574 | 1086 1112 1142 1173 1207 1242 1279 1317 1356 1397 | 3.89 4.31 4.77 5.28 5.83 6.44 7.10 7.80 8.56 9.37
28 | 2 | Performance data (cont) | 1 | col_1: 1.6; col_4: 1.8; col_7: 1.9
28 | 2 | Performance data (cont) | 2 | col_1: Rpm; col_2: Bhp; col_3: Watts; col_4: Rpm; col_5: Bhp; col_6: Watts; col_7: Rpm; col_8: Bhp; col_9: Watts; col_10: Rpm; col_11: Bhp
28 | 2 | Performance data (cont) | 3 | col_1: 1142 1167 1194 1224 1255 1289 1324 1360 1398 1438; col_2: 4.24 4.66 5.12 5.63 6.19 6.80 7.45 8.16 8.93 9.74; col_3: 3567 3915 4304 4733 5203 5714 6268 6865 7505 8190; col_4: 1197 1219 1245 1273 1302 1334 1368 1403 1440 1477; col_5: 4.59 5.01 5.47 5.98 6.55 7.16 7.82 8.53 9.29 10.11; col_6: 3864 4213 4602 5033 5504 6018 6573 7173 7815 8503; col_7: 1223 1245 1270 1296 1326 1357 1389 1424 1460 —; col_8: 4.77 5.19 5.65 6.17 6.73 7.34 8.00 8.71 9.48 —; col_9: 4015 4364 4754 5184 5657 6171 6728 7328 7972 —; col_10: 1249 1270 1294 1320 1348 1379 1411 1445 1480 —; col_11: 4.96 5.37 5.83 6.35 6.91 7.52 8.18 8.90 9.67 —
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 1 | col_1: 0.2; col_4: 0.4; col_7: 0.6; col_10: 0.8; col_13: 1; col_16: 1.2
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | Rpm | Bhp | Watts | Rpm | Bhp | Watts | Rpm | Bhp | Watts | Rpm | Bhp | Watts | Rpm | Bhp | Watts | Rpm | Bhp | Watts | Rpm | Bhp
29 | 1 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | 845 896 948 1001 1053 1106 1159 1213 1266 1293 | 3.26 3.82 4.43 5.11 5.85 6.65 7.52 8.45 9.45 9.97 | 2693 3156 3667 4226 4836 5498 6214 6984 7810 8245 | 909 956 1005 1054 1104 1155 1206 1257 1309 1334 | 3.60 4.17 4.80 5.49 6.23 7.04 7.92 8.86 9.87 10.40 | 2979 3450 3969 4537 5155 5824 6547 7325 8159 8597 | 969 1014 1060 1106 1154 1202 1251 1300 1350 1375 | 3.96 4.54 5.17 5.87 6.63 7.44 8.33 9.28 10.29 10.83 | 3272 3752 4278 4853 5478 6155 6886 7671 8511 8953 | 1028 1069 1112 1156 1202 1248 1295 1342 1391 1415 | 4.32 4.91 5.56 6.26 7.02 7.85 8.74 9.70 10.73 11.26 | 3574 4060 4593 5175 5808 6492 7229 8020 8868 9313 | 1083 1123 1163 1205 1248 1293 1338 1384 1431 1454 | 4.70 5.29 5.94 6.66 7.43 8.26 9.16 10.13 11.16 11.70 | 3883 4375 4915 5504 6142 6833 7577 8375 9229 9677 | 1137 1174 1213 1253 1294 1336 1380 1424 1470 1493 | 5.08 5.68 6.34 7.06 7.84 8.68 9.59 10.56 11.60 12.15 | 4,200 4,698 5,243 5,838 6,483 7,179 7,929 8,733 9,594 10,045 | 1189 1224 1261 1299 1338 1379 1421 1464 1508 1530 | 5.47 6.08 6.75 7.47 8.26 9.11 10.02 11.00 12.05 12.60
29 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 1 | col_1: 1.6
29 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 2 | col_1: Rpm; col_2: Bhp; col_3: Watts; col_4: Rpm; col_5: Bhp
29 | 2 | FAN PERFORMANCE — 50TJ016-028 — ENGLISH (cont) | 3 | col_1: 1239 1272 1307 1344 1382 1421 1461 1503 1546 —; col_2: 5.87 6.48 7.16 7.89 8.68 9.54 10.46 11.45 12.50 —; col_3: 4,854 5,362 5,917 6,523 7,179 7,887 8,648 9,464 10,336 —; col_4: 1288 1320 1353 1388 1424 1462 1501 1541 — —; col_5: 4.91 5.56 6.26 7.02 7.85 8.74 9.70 10.73 — —
30 | 1 | Performance data (cont) | 1 | col_1: FAN PERFORMANCE USING ACCESSORY POWER EXHAUST
30 | 1 | Performance data (cont) | 2
30 | 1 | Performance data (cont) | 3 | col_1: HORIZONTAL SUPPLY/RETURN FAN PERFORMANCE WITH CRRFCURB013A00 HIGH-STATIC REGAIN ADAPTER NOTE: The CRRFCURB013A00 high-static regain adapter accessory may be used to provide horizontal supply/return. NOTE: The CRRFCURB013A00 horizontal supply and return adapter accessory improves 50TJ fan performance by increasing external static pressure by amount shown above.
30 | 1 | Performance data (cont) | 4

## Static_Pressure_Accessories
source_page | table_no | page_title | table_row | col_1 | col_2 | col_3 | col_4 | col_5 | col_6 | col_7 | col_8 | col_9 | col_10 | col_11 | col_12 | col_13 | col_14 | col_15 | col_16 | col_17 | col_18 | col_19 | col_20 | col_21 | col_22 | col_23
31 | 1 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 1 | col_1: 2125; col_2: 2360; col_3: 2831; col_4: 3400
31 | 1 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 2 | col_1: 10; col_2: 12; col_3: 17; col_4: 22
31 | 1 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 3 | col_1: 55; col_2: 65; col_3: 87; col_4: 109
31 | 1 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 4
31 | 1 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 5 | col_1: 15 19 25; col_2: 17 22 27; col_3: 22 27 35; col_4: 27 35 46
31 | 2 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 1 | col_1: 4500; col_2: 5000; col_3: 6000; col_4: 7200
31 | 2 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 2 | col_1: 0.04; col_2: 0.05; col_3: 0.07; col_4: 0.09
31 | 2 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 3 | col_1: 0.22; col_2: 0.26; col_3: 0.35; col_4: 0.44
31 | 2 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 4
31 | 2 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 5 | col_1: 0.06 0.08 0.10; col_2: 0.07 0.09 0.11; col_3: 0.09 0.11 0.14; col_4: 0.11 0.14 0.18
31 | 3 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 1 | col_1: 2800; col_2: 3400; col_3: 4247; col_4: 4719
31 | 3 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 2 | col_1: 17; col_2: 22; col_3: 27; col_4: 30
31 | 3 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 3 | col_1: 86; col_2: 109; col_3: 144; col_4: 164
31 | 3 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 4
31 | 3 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 5 | col_1: 22 28 36; col_2: 27 35 46; col_3: 37 45 57; col_4: 43 53 65
31 | 4 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 1 | col_1: 6000; col_2: 7200; col_3: 9000; col_4: 10000
31 | 4 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 2 | col_1: 0.07; col_2: 0.09; col_3: 0.11; col_4: 0.12
31 | 4 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 3 | col_1: 0.35; col_2: 0.44; col_3: 0.58; col_4: 0.66
31 | 4 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 4
31 | 4 | ACCESSORY/FIOP STATIC PRESSURE (Pa) — 50TJ016 | 5 | col_1: 0.09 0.11 0.14; col_2: 0.11 0.14 0.18; col_3: 0.15 0.18 0.23; col_4: 0.17 0.21 0.26

## Fan_Motor_Performance
source_page | table_no | page_title | table_row | col_1 | col_2 | col_3 | col_4 | col_5 | col_6 | col_7 | col_8 | col_9 | col_10 | col_11 | col_12 | col_13 | col_14 | col_15 | col_16 | col_17 | col_18 | col_19 | col_20 | col_21 | col_22 | col_23
32 | 1 | Performance data (cont) | 1 | col_1: 0; col_2: 1/2; col_3: 1; col_4: 11/2; col_5: 2; col_6: 21/2; col_7: 3; col_8: 31/2; col_9: 4; col_10: 41/2; col_11: 5; col_12: 51/2
32 | 1 | Performance data (cont) | 2 | col_1: 16.38; col_2: 15.99; col_3: 15.58; col_4: 15.19; col_5: 14.78; col_6: 14.38; col_7: 13.98; col_8: 13.58; col_9: 13.18; col_10: 12.78; col_11: 12.38; col_12: †
32 | 1 | Performance data (cont) | 3 | col_1: 21.67; col_2: 21.2; col_3: 20.75; col_4: 20.28; col_5: 19.82; col_6: 19.37; col_7: 18.9; col_8: 18.43; col_9: 17.97; col_10: 17.52; col_11: 17.05; col_12: †
32 | 1 | Performance data (cont) | 4 | col_1: 15.15; col_2: 14.92; col_3: 14.68; col_4: 14.45; col_5: 14.22; col_6: 13.98; col_7: 13.75; col_8: 13.52; col_9: 13.28; col_10: 13.05; col_11: 12.82; col_12: †
32 | 1 | Performance data (cont) | 5 | col_1: 20.27; col_2: 19.97; col_3: 19.66; col_4: 19.35; col_5: 19.03; col_6: 18.73; col_7: 18.42; col_8: 18.12; col_9: 17.8; col_10: 17.5; col_11: 17.19; col_12: 16.88
32 | 1 | Performance data (cont) | 6 | col_1: 17.82; col_2: 17.52; col_3: 17.21; col_4: 16.91; col_5: 16.61; col_6: 16.31; col_7: 16.01; col_8: 15.71; col_9: 15.4; col_10: 15.1; col_11: 14.8; col_12: †
32 | 1 | Performance data (cont) | 7 | col_1: 22.35; col_2: 21.97; col_3: 21.59; col_4: 21.22; col_5: 20.84; col_6: 20.46; col_7: 20.08; col_8: 19.7; col_9: 19.32; col_10: 18.95; col_11: 18.57; col_12: †
32 | 2 | Performance data (cont) | 1 | col_1: 0; col_2: 1/2; col_3: 1; col_4: 11/2; col_5: 2; col_6: 21/2; col_7: 3; col_8: 31/2; col_9: 4; col_10: 41/2; col_11: 5; col_12: 51/2
32 | 2 | Performance data (cont) | 2 | col_1: 983; col_2: 959; col_3: 935; col_4: 911; col_5: 887; col_6: 863; col_7: 839; col_8: 815; col_9: 791; col_10: 767; col_11: 743; col_12: †
32 | 2 | Performance data (cont) | 3 | col_1: 1300; col_2: 1272; col_3: 1245; col_4: 1217; col_5: 1189; col_6: 1162; col_7: 1134; col_8: 1106; col_9: 1078; col_10: 1051; col_11: 1023; col_12: †
32 | 2 | Performance data (cont) | 4 | col_1: 909; col_2: 895; col_3: 881; col_4: 867; col_5: 853; col_6: 839; col_7: 825; col_8: 811; col_9: 797; col_10: 783; col_11: 769; col_12: †
32 | 2 | Performance data (cont) | 5 | col_1: 1216; col_2: 1198; col_3: 1179; col_4: 1161; col_5: 1142; col_6: 1124; col_7: 1105; col_8: 1087; col_9: 1068; col_10: 1050; col_11: 1031; col_12: 1013
32 | 2 | Performance data (cont) | 6 | col_1: 1069; col_2: 1051; col_3: 1033; col_4: 1015; col_5: 997; col_6: 979; col_7: 960; col_8: 942; col_9: 924; col_10: 906; col_11: 888; col_12: †
32 | 2 | Performance data (cont) | 7 | col_1: 1341; col_2: 1318; col_3: 1296; col_4: 1273; col_5: 1250; col_6: 1228; col_7: 1205; col_8: 1182; col_9: 1159; col_10: 1137; col_11: 1114; col_12: †
32 | 3 | Performance data (cont) | 1 | col_1: UNIT RATED VOLTAGE; col_2: MAXIMUM ACCEPTABLE CONTINUOUS BHP*; col_3: MAXIMUM ACCEPTABLE CONTINUOUS BkW*; col_4: MAXIMUM ACCEPTABLE OPERATING WATTS
32 | 3 | Performance data (cont) | 2 | col_1: 220; col_2: 3.45; col_3: 3.17; col_4: 3065
32 | 3 | Performance data (cont) | 3 | col_1: 400; col_2: 4.25; col_3: 3.17; col_4: 3775
32 | 3 | Performance data (cont) | 4 | col_1: 220; col_2: 10.3; col_3: 7.68; col_4: 8640
32 | 3 | Performance data (cont) | 5 | col_1: 400; col_2: 10.3; col_3: 7.68; col_4: 8640
32 | 3 | Performance data (cont) | 6 | col_1: 220; col_2: 11.5; col_3: 8.6; col_4: 9600
32 | 3 | Performance data (cont) | 7 | col_1: 400; col_2: 13.3; col_3: 9.92; col_4: 11000

## Accessory_Dimensions
source_page | table_no | page_title | table_row | col_1 | col_2 | col_3 | col_4 | col_5 | col_6 | col_7 | col_8 | col_9 | col_10 | col_11 | col_12 | col_13 | col_14 | col_15 | col_16 | col_17 | col_18 | col_19 | col_20 | col_21 | col_22 | col_23
14 | 1 | Accessory dimensions | 1 | col_1: NOTES: 1. Roof curb accessory is shipped unassembled. 2. Insulated panels, 1″ thick neoprene coated, 11/ lb density.
14 | 1 | Accessory dimensions | 2 | col_2: OTES: 1. Roof curb accessory is shipped unassembled. 2. Insulated panels, 1″ thick neoprene coated, 11/ lb density.
14 | 2 | Accessory dimensions | 1 | col_1: CURB HEIGHT
14 | 2 | Accessory dimensions | 2 | col_1: 1′-2″ (305)
14 | 2 | Accessory dimensions | 3 | col_1: 2′-0″ (610)
14 | 2 | Accessory dimensions | 4 | col_1: 2′-0″ (610)
14 | 3 | Accessory dimensions | 1 | bar: col_1
14 | 3 | Accessory dimensions | 2 | col_1: DEG.; col_2: IN.; col_3: DEG.
14 | 3 | Accessory dimensions | 3 | col_1: .28; col_2: .45; col_3: .28
15 | 1 | HORIZONTAL SUPPLY/RETURN ADAPTER INSTALLATION | 1 | col_1: HORIZONTAL SUPPLY/RETURN ADAPTER INSTALLATION NOTE: CRRFCURB013A00 is a fully factory preassembled horizontal adapter and includes an insulated high static regain transition duct which substantially improves fan static performance. The Barometric Relief Damper and Power Exhaust accessories are not available with the horizontal adapter. ACCESSORY CURB DESCRIPTION PACKAGE NO. HEIGHT 1′-11″ Pre-Assembled, High Static, CRRFCURB013A00 (584) Horizontal Adapter
15 | 1 | HORIZONTAL SUPPLY/RETURN ADAPTER INSTALLATION | 2
15 | 1 | HORIZONTAL SUPPLY/RETURN ADAPTER INSTALLATION | 3 | col_1: BAROMETRIC RELIEF/POWER EXHAUST 2'-1 5/8" (650.9) 2'-2 1/16" (662) 1'-6 5/16" (465.1)
15 | 1 | HORIZONTAL SUPPLY/RETURN ADAPTER INSTALLATION | 4
15 | 2 | HORIZONTAL SUPPLY/RETURN ADAPTER INSTALLATION | 1 | col_1: CURB HEIGHT
15 | 2 | HORIZONTAL SUPPLY/RETURN ADAPTER INSTALLATION | 2 | col_1: 1′-11″ (584)
16 | 1 | Accessory dimensions (cont) | 1 | col_1: FACTORY-INSTALLED NON-FUSED DISCONNECT COMPRESSOR TOP CONTROL BOX DISCONNECT SECTION DOOR SECTION DOOR HANDLE 2'-5 1/4" (743) FRONT VIEW 1'-1 11/16" (347)
16 | 1 | Accessory dimensions (cont) | 2

## Electrical_Data
source_page | table_no | page_title | table_row | col_1 | col_2 | col_3 | col_4 | col_5 | col_6 | col_7 | col_8 | col_9 | col_10 | col_11 | col_12 | col_13 | col_14 | col_15 | col_16 | col_17 | col_18 | col_19 | col_20 | col_21 | col_22 | col_23
33 | 1 | Electrical data | 1 | col_1: NOMINAL VOLTAGE; col_2: VOLTAGE RANGE; col_4: COMPRESSOR; col_8: OFM; col_11: IFM; col_13: POWER EXHAUST; col_15: ELECTRIC HEAT*
33 | 1 | Electrical data | 2 | col_4: No. 1; col_6: No. 2
33 | 1 | Electrical data | 3 |  | Min | Max | RLA | LRA | RLA | LRA | Qty | Hp | FLA (ea) | Hp | FLA | FLA | LRA | kW | FLA | MCA
33 | 1 | Electrical data | 4 | 220 | 198 | 242 | 30.1 | 196 | 30.1 | 196 | 2 | 1 | 6.3 | 3 | 9.8 | — 4.7 | — 10.5 | — — | — — | 90 95
33 | 1 | Electrical data | 5 | 400 | 360 | 440 | 15.5 | 111 | 15.5 | 111 | 2 | 1 | 3.4 | 3 | 4.8 | — 4.7 | — 10.5 | — — | — — | 47 51
33 | 1 | Electrical data | 6 | col_13: 4.7; col_14: 10.5; col_15: 22.5 22.5; col_16: 32.5 32.5; col_17: 47 53
33 | 1 | Electrical data | 7 | col_13: — 4.7; col_14: — 10.5; col_15: 38.2 38.2; col_16: 55.1 55.1; col_17: 75 81
33 | 1 | Electrical data | 8 | col_13: — 4.7; col_14: — 10.5; col_15: 55.4** 55.4**; col_16: 80.0 80.0; col_17: 86 92
33 | 1 | Electrical data | 9 | 220 | 198 | 242 | 38.5 | 293 | 37.7 | 220 | 2 | 1 | 6.3 | 7.5 | 23.5 | — 4.7 | — 10.5 | — — | — — | 121 126
33 | 1 | Electrical data | 10 | 400 | 360 | 440 | 21.8 | 167 | 17.2 | 118 | 2 | 1 | 3.4 | 7.5 | 12.1 | — 4.7 | — 10.5 | — — | — — | 63 68
33 | 1 | Electrical data | 11 | col_13: — 4.7; col_14: — 10.5; col_15: 22.5 22.5; col_16: 32.5 32.5; col_17: 63 68
33 | 1 | Electrical data | 12 | col_13: 4.7; col_14: 10.5; col_15: 38.2 38.2; col_16: 55.1 55.1; col_17: 84 90
33 | 1 | Electrical data | 13 | col_13: — 4.7; col_14: — 10.5; col_15: 55.4** 55.4**; col_16: 80.0 80.0; col_17: 95 101
33 | 1 | Electrical data | 14 | 220 | 198 | 242 | 45.4 | 345 | 38.5 | 293 | 2 | 1 | 6.3 | 10 | 32 | — 4.7 | — 10.5 | — — | — — | 139 144
33 | 1 | Electrical data | 15 | 400 | 360 | 440 | 23.7 | 198 | 21.8 | 167 | 2 | 1 | 3.4 | 10 | 14 | — 4.7 | — 10.5 | — — | — — | 72 77
33 | 1 | Electrical data | 16 | col_13: — 4.7; col_14: — 10.5; col_15: 22.5 22.5; col_16: 32.5 32.5; col_17: 72 77
33 | 1 | Electrical data | 17 | col_13: — 4.7; col_14: — 10.5; col_15: 38.2 38.2; col_16: 55.1 55.1; col_17: 86 92
33 | 1 | Electrical data | 18 | col_13: — 4.7; col_14: — 10.5; col_15: 55.4** 55.4**; col_16: 80.0 80.0; col_17: 98 103
33 | 1 | Electrical data | 19 | 400 | 360 | 440 | 23.7 | 198 | 21.8 | 167 | 2 | 5 | 7.3 | 10 | 14 | — 4.7 | — 10.5 | — — | — — | 80 85
33 | 1 | Electrical data | 20 | col_13: — 4.7; col_14: — 10.5; col_15: 22.5 22.5; col_16: 32.5 32.5; col_17: 80 85
33 | 1 | Electrical data | 21 | col_13: — 4.7; col_14: — 10.5; col_15: 38.2 38.2; col_16: 55.1 55.1; col_17: 86 92
33 | 1 | Electrical data | 22 | col_13: — 4.7; col_14: — 10.5; col_15: 55.4** 55.4**; col_16: 80.0 80.0; col_17: 98 103