## README
Field | Value
Source file | 50TJSProductCatalog.pdf
Source pages | 27
Source period | Jan 2005 / Form 50TJS-02PD-50HZ C
Series | 50LJS/TJS 007-014
Application | Single-package rooftop cooling units, 50 Hz, 6 to 12.5 nominal tons
Workbook purpose | Structured database extracted from the supplied product catalog; full page text is preserved in Page_Text.
Data handling | Blank/dash values are retained as blank or "—" where the source indicates not applicable/unavailable.
Image-only pages | Pages 8-9 (base-unit dimensions) and 17-23 (piping/wiring diagrams) are referenced in Page_Index; see original PDF for drawings.
Important | Values are transcribed from the historical catalog and should be checked against current manufacturer documentation before engineering use.
Audit status | Electrical dash corrected; 50TJS014 technical rating retained as 12 tons with 12.5-ton cover/title discrepancy documented; suspected OCR anomalies flagged without altering raw text.

## Models
Model | Model family | Nominal tons | Standard CFM | Gross cooling Btuh | Net cooling Btuh | Input kW | EER | Sound rating Bels | Size family | Compressor quantity | Compressor type | Refrigerant circuits | Refrigerant | Charge circuit 1 lb-oz | Charge circuit 2 lb-oz | Nominal CFM | Catalog year
50LJS007 | LJS007 | 6 | 2200 | 67600 | 65000 | 6.6 | 9.8 | 8.4 | LJ | 1 | Scroll | 1 | R-22 | 8-3 | — | 2200 | 2005
50TJS008 | TJS008 | 7 | 2800 | 85300 | 82200 | 9.8 | 8.4 | 8.6 | TJ | 2 | Hermetic, Reciprocating | 2 | R-22 | 5-4 | 5-4 | 2800 | 2005
50TJS009 | TJS009 | 9 | 3000 | 106600 | 103200 | 10.9 | 9.5 | 8.6 | TJ | 2 | Hermetic, Reciprocating | 2 | R-22 | 6-3 | 6-3 | 3000 | 2005
50TJS012 | TJS012 | 10 | 4000 | 122500 | 117350 | 13.4 | 8.8 | 8.8 | TJ | 2 | Hermetic, Reciprocating | 2 | R-22 | 6-5 | 6-5 | 4000 | 2005
50TJS014 | TJS014 | 12 | 4750 | 146700 | 138050 | 14.1 | 9.8 | 8.8 | TJ | 2 | Scroll | 2 | R-22 | 7-12 | 7-12 | 4750 | 2005

## ARI_Capacity
Model | Nominal tons | Standard CFM | Gross cooling Btuh | Net cooling Btuh | Input kW | EER | Sound rating Bels | Source page | Rating basis
50LJS007 | 6 | 2200 | 67600 | 65000 | 6.6 | 9.8 | 8.4 | 3 | ARI 210/240-89 or 360-86 and 270-84
50TJS008 | 7 | 2800 | 85300 | 82200 | 9.8 | 8.4 | 8.6 | 3 | ARI 210/240-89 or 360-86 and 270-84
50TJS009 | 9 | 3000 | 106600 | 103200 | 10.9 | 9.5 | 8.6 | 3 | ARI 210/240-89 or 360-86 and 270-84
50TJS012 | 10 | 4000 | 122500 | 117350 | 13.4 | 8.8 | 8.8 | 3 | ARI 210/240-89 or 360-86 and 270-84
50TJS014 | 12 | 4750 | 146700 | 138050 | 14.1 | 9.8 | 8.8 | 3 | ARI 210/240-89 or 360-86 and 270-84

## Physical_English
Model | Electrical configuration V-Ph-Hz | Nominal tons | Nominal capacity Kbtu/hr | Unit weight lb | Economizer weight lb | Roof curb weight lb | Compressor type | Compressor qty | Oil per compressor oz | Refrigerant | Charge circuit 1 lb-oz | Charge circuit 2 lb-oz | Condenser fan type | Condenser fan qty x diameter in | Condenser nominal CFM | Condenser motor hp x rpm | Condenser coil | Condenser rows x fins/in | Condenser face area sq ft | Evaporator fan type | Evaporator fan qty x size in | Drive type | Evaporator nominal CFM | Input watts | Evaporator motor hp x rpm | Max continuous bhp | Motor pulley pitch dia in | Fan pulley pitch dia in | Evaporator rows x fins/in | Evaporator face area sq ft | Outdoor air inlet screens | Return air filters
50LJS007 | 400-3-50 +/-10% | 6 | 72 | 520 | 34 | 115 | Scroll | 1 | 77 | R-22 | 8-3 | — | Propeller | 1 x 26 | 4300 | 1/3 x 960 | Enhanced copper tubes, aluminum double-wavy fins | 2 x 17 | 12.25 | Centrifugal | 1 x 10 x 10 | Belt driven | 2200 | 800 | 1.5 x 1425 | 2.4 | 4.4 | 5.19 | 4 x 15 | 5.5 | 1 x 20 x 24 x 1 | 2 x 16 x 25 x 2
50TJS008 | 400-3-50 +/-10% | 7.0 | 84 | 755 | 44 | 143 | Hermetic, Reciprocating | 2 | 52 | R-22 | 5-4 | 5-4 | Propeller | 2 x 22 | 8650 | 1/2 x 1100 | Enhanced copper tubes, aluminum double-wavy fins | 1 x 17 | 20.5 | Centrifugal | 1 x 15 x 15 | Belt driven | 2800 | 900 | 1.5 x 1425 | 2.4 | 3.4 | 5.5 | 3 x 15 | 8 | 1 x 20 x 25 x 1 + 1 x 16 x 25 x 1 | 4 x 16 x 20 x 2
50TJS009 | 400-3-50 +/-10% | 9.0 | 108 | 760 | 44 | 143 | Hermetic, Reciprocating | 2 | 52 | R-22 | 6-3 | 6-3 | Propeller | 2 x 22 | 8650 | 1/2 x 1100 | Enhanced copper tubes, aluminum double-wavy fins | 2 x 17 | 18 | Centrifugal | 1 x 15 x 15 | Belt driven | 3000 | 1000 | 1.5 x 1425 | 2.4 | 3.4 | 5.5 | 3 x 15 | 8 | 1 x 20 x 25 x 1 + 1 x 16 x 25 x 1 | 4 x 16 x 20 x 2
50TJS012 | 400-3-50 +/-10% | 10 | 120 | 915 | 44 | 143 | Hermetic, Reciprocating | 2 | 62 | R-22 | 6-5 | 6-5 | Propeller | 2 x 22 | 9225 | 1/2 x 1100 | Enhanced copper tubes, aluminum double-wavy fins | 2 x 17 | 17.42 | Centrifugal | 1 x 15 x 15 | Belt driven | 4000 | 1500 | 2 x 1425 | 2.9 | 4.4 | 7 | 3 x 15 | 10 | 1 x 20 x 25 x 1 + 1 x 16 x 25 x 1 | 4 x 20 x 20 x 2
50TJS014 | 400-3-50 +/-10% | 12.0 | 144 | 930 | 44 | 143 | Scroll | 2 | 77 | R-22 | 7-12 | 7-12 | Propeller | 2 x 22 | 9225 | 1/2 x 1100 | Enhanced copper tubes, aluminum double-wavy fins | 2 x 17 | 25 | Centrifugal | 1 x 15 x 15 | Belt driven | 4750 | 2000 | 3 x 1425 | 3.7 | 5 | 7 | 4 x 15 | 11.1 | 1 x 20 x 25 x 1 + 1 x 16 x 25 x 1 | 4 x 20 x 20 x 2

## Physical_SI
Model | Nominal tons | Nominal capacity kW | Unit weight kg | Economizer weight kg | Roof curb weight kg | Compressor type | Compressor qty | Oil per compressor ml | Charge circuit 1 kg | Charge circuit 2 kg | Condenser fan type | Condenser fan qty x diameter mm | Condenser airflow L/s | Condenser motor kW x rps | Evaporator airflow L/s | Input watts | Evaporator motor kW x rps | Max continuous BkW | Motor pulley pitch dia mm | Fan pulley pitch dia mm | Evaporator coil face area sq m
50LJS007 | 6 | 21.1 | 236.3 | 15.45 | 52.2 | Scroll | 1 | 2277 | 3.7 | — | Propeller | 1 x 660.4 | 2029 | 0.25 x 16 | 1038 | 800 | 1.1 x 23.8 | 1.8 | 111.8 | 132 | 0.51
50TJS008 | 7.0 | 24.6 | 343.1 | 20 | 65 | Hermetic, Reciprocating | 2 | 1538 | 2.4 | 2.4 | Propeller | 2 x 558.8 | 4082 | 0.37 x 18.33 | 1321 | 900 | 1.1 x 23.8 | 1.8 | 86.4 | 139.7 | 0.74
50TJS009 | 9.0 | 31.6 | 345.4 | 20 | 65 | Hermetic, Reciprocating | 2 | 1538 | 2.8 | 2.8 | Propeller | 2 x 558.8 | 4082 | 0.37 x 18.33 | 1416 | 1000 | 1.1 x 23.8 | 1.8 | 86.4 | 139.7 | 0.74
50TJS012 | 10 | 36.2 | 415.9 | 20 | 65 | Hermetic, Reciprocating | 2 | 1834 | 2.9 | 2.9 | Propeller | 2 x 558.8 | 4353 | 0.37 x 18.33 | 1887 | 1500 | 1.5 x 23.8 | 2.1 | 111.8 | 177.8 | 0.929
50TJS014 | 12.0 | 42.0 | 422.7 | 20 | 65 | Scroll | 2 | 2277 | 3.5 | 3.5 | Propeller | 2 x 558.8 | 4353 | 0.37 x 18.33 | 2242 | 2000 | 2.2 x 23.8 | 2.7 | 127 | 177.8 | 1.03

## Fan_RPM
Model | Pulley turns open 0 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4 | 4.5 | 5
50LJS007 | 1205 | 1180 | 1150 | 1125 | 1095 | 1070 | 1040 | 1015 | 985 | 960 | 930
50TJS008 | 880 | 855 | 830 | 800 | 775 | 750 | 725 | 700 | 675 | 650 | 620
50TJS009 | 880 | 855 | 830 | 800 | 775 | 750 | 725 | 700 | 675 | 650 | 620
50TJS012 | 900 | 875 | 855 | 835 | 815 | 795 | 775 | 755 | 735 | 715 | 690
50TJS014 | 1017 | 992 | 972 | 952 | 932 | 912 | 892 | 872 | 852 | 832 | 814

## Sound_Power
Model | Sound rating Bels | 63 Hz | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz | 8000 Hz | Source page
50LJS007 | 8.2 | 78.5 | 84 | 77.5 | 73 | 70.5 | 72 | 65 | 58.5 | 15
50TJS008 | 8.6 | 83.2 | 87.4 | 83.5 | 82.8 | 83 | 77.7 | 71.8 | 67 | 15
50TJS009 | 8.6 | 83.2 | 87.4 | 83.5 | 82.8 | 83 | 77.7 | 71.8 | 67 | 15
50TJS012 | 8.8 | 97.6 | 90.4 | 85.7 | 84.8 | 83.9 | 77.5 | 71.3 | 65.8 | 15
50TJS014 | 8.8 | 83.7 | 87.2 | 83.4 | 82.8 | 83 | 77.7 | 71.8 | 67 | 15

## Electrical_Data
Model | Nominal supply V-Ph-Hz | Voltage min | Voltage max | Compressor RLA each | Compressor LRA each | Compressor qty | OFM hp each | OFM FLA each | IFM FLA | Electric heat nominal kW | Electric heat FLA | MCA | MOCP | Disconnect FLA | Disconnect LRA | Source page
50LJS007 | 400-3-50 | 342 | 440 | 12 | 100 | 1 | 1/3 | 1.5 | 2.6 | - | - | 19.1 | 25 | — | — | 16
50LJS007 | 400-3-50 | 342 | 440 | 12 | 100 | 1 | 1/3 | 1.5 | 2.6 | 4.2 | 6.1 | 19.1 | 25 | — | — | 16
50LJS007 | 400-3-50 | 342 | 440 | 12 | 100 | 1 | 1/3 | 1.5 | 2.6 | 8 | 11.5 | 19.2 | 25 | — | — | 16
50LJS007 | 400-3-50 | 342 | 440 | 12 | 100 | 1 | 1/3 | 1.5 | 2.6 | 9.7 | 14 | 23 | 25 | — | — | 16
50LJS007 | 400-3-50 | 342 | 440 | 12 | 100 | 1 | 1/3 | 1.5 | 2.6 | 16 | 23.2 | 35 | 30 | — | — | 16
50LJS007 | 400-3-50 | 342 | 440 | 12 | 100 | 1 | 1/3 | 1.5 | 2.6 | 17.7 | 25.6 | 37.5 | 40 | — | — | 16
50TJS008 | 400-3-50 | 342 | 440 | 6.6 | 53 | 2 | 1/2 | 1.8 | 3.4 | - | - | 18.8 | 20 | 19 | 130 | 16
50TJS008 | 400-3-50 | 342 | 440 | 6.6 | 53 | 2 | 1/2 | 1.8 | 3.4 | 9.7 | 13.9 | 21.7 | 20 | 19 | 130 | 16
50TJS008 | 400-3-50 | 342 | 440 | 6.6 | 53 | 2 | 1/2 | 1.8 | 3.4 | 11.5 | 16.5 | 24.9 | 25 | 22 | 130 | 16
50TJS008 | 400-3-50 | 342 | 440 | 6.6 | 53 | 2 | 1/2 | 1.8 | 3.4 | 19.3 | 27.8 | 39.1 | 40 | 35 | 130 | 16
50TJS008 | 400-3-50 | 342 | 440 | 6.6 | 53 | 2 | 1/2 | 1.8 | 3.4 | 22.9 | 33.1 | 45.6 | 45 | 41 | 130 | 16
50TJS008 | 400-3-50 | 342 | 440 | 6.6 | 53 | 2 | 1/2 | 1.8 | 3.4 | 29 | 41.8 | 56.5 | 60 | 51 | 130 | 16
50TJS009 | 400-3-50 | 342 | 440 | 7.5 | 62 | 2 | 1/2 | 1.8 | 3.4 | - | - | 21.5 | 25 | 21 | 147 | 16
50TJS009 | 400-3-50 | 342 | 440 | 7.5 | 62 | 2 | 1/2 | 1.8 | 3.4 | 9.7 | 13.9 | 21.7 | 25 | 21 | 147 | 16
50TJS009 | 400-3-50 | 342 | 440 | 7.5 | 62 | 2 | 1/2 | 1.8 | 3.4 | 11.5 | 16.5 | 24.9 | 25 | 22 | 147 | 16
50TJS009 | 400-3-50 | 342 | 440 | 7.5 | 62 | 2 | 1/2 | 1.8 | 3.4 | 19.3 | 27.8 | 39.1 | 40 | 35 | 147 | 16
50TJS009 | 400-3-50 | 342 | 440 | 7.5 | 62 | 2 | 1/2 | 1.8 | 3.4 | 22.9 | 33.1 | 45.6 | 45 | 41 | 147 | 16
50TJS009 | 400-3-50 | 342 | 440 | 7.5 | 62 | 2 | 1/2 | 1.8 | 3.4 | 29 | 41.8 | 56.5 | 60 | 51 | 147 | 16
50TJS012 | 400-3-50 | 342 | 440 | 9 | 82 | 2 | 1/2 | 1.8 | 3.4 | - | - | 23.2 | 30 | 24 | 158 | 16
50TJS012 | 400-3-50 | 342 | 440 | 9 | 82 | 2 | 1/2 | 1.8 | 3.4 | 9.7 | 16.5 | 23.9 | 30 | 24 | 158 | 16
50TJS012 | 400-3-50 | 342 | 440 | 9 | 82 | 2 | 1/2 | 1.8 | 3.4 | 19.3 | 27.8 | 38.1 | 40 | 35 | 158 | 16
50TJS012 | 400-3-50 | 342 | 440 | 9 | 82 | 2 | 1/2 | 1.8 | 3.4 | 22.9 | 33.1 | 44.6 | 45 | 41 | 158 | 16
50TJS012 | 400-3-50 | 342 | 440 | 9 | 82 | 2 | 1/2 | 1.8 | 3.4 | 29 | 41.8 | 55.5 | 60 | 51 | 158 | 16
50TJS012 | 400-3-50 | 342 | 440 | 9 | 82 | 2 | 1/2 | 1.8 | 3.4 | 34.7 | 50.1 | 65.9 | 70 | 61 | 158 | 16
50TJS014 | 400-3-50 | 342 | 440 | 12 | 100 | 2 | 1/2 | 1.8 | 4.8 | - | - | 33.3 | 40 | 35 | 232 | 16
50TJS014 | 400-3-50 | 342 | 440 | 12 | 100 | 2 | 1/2 | 1.8 | 4.8 | 11.5 | 18 | 33.3 | 40 | 35 | 232 | 16
50TJS014 | 400-3-50 | 342 | 440 | 12 | 100 | 2 | 1/2 | 1.8 | 4.8 | 19.3 | 30.3 | 43.9 | 45 | 40 | 232 | 16
50TJS014 | 400-3-50 | 342 | 440 | 12 | 100 | 2 | 1/2 | 1.8 | 4.8 | 22.9 | 36.1 | 51.1 | 60 | 47 | 232 | 16
50TJS014 | 400-3-50 | 342 | 440 | 12 | 100 | 2 | 1/2 | 1.8 | 4.8 | 29 | 45.5 | 62.8 | 70 | 58 | 232 | 16
50TJS014 | 400-3-50 | 342 | 440 | 12 | 100 | 2 | 1/2 | 1.8 | 4.8 | 34.7 | 54.6 | 74.2 | 80 | 68 | 232 | 16

## Page_Index
PDF page | Content type | Page preview | Extracted line count | Reference
1 | Text / tables | 50LJS/TJS 007-014 Product Single-Package Data | 62 | Original PDF page 1
2 | Text / tables | Model Number Nomenclature 50 TJ S 008 – 9 3 3 SR 50–Cooling Only/Cooling NE – S | 52 | Original PDF page 2
3 | Text / tables | ARI Capacity Rating* GROSS NET INPUT SOUND NOMINAL STANDARD COOLING COOLIN | 36 | Original PDF page 3
4 | Text / tables | Physical data (50 Hz) — English UNIT MODEL 50 SERIES LJS007 TJS008 | 55 | Original PDF page 4
5 | Text / tables | Physical data (50 Hz)— SI UNIT MODEL 50 SERIES LJS007 TJS008 | 55 | Original PDF page 5
6 | Text / tables | Performance data COOLING CAPACITIES 50LJS007 (6 TONS) Temp (F) Eva | 81 | Original PDF page 6
7 | Text / tables | COOLING CAPACITIES (Cont.) 50TJS012 (10 TONS) Temp (F) Eva | 84 | Original PDF page 7
8 | Drawing / diagram page (text labels may be incomplete) | Base unit dimensions — 50LJS007 8 | 6 | Original PDF page 8
9 | Drawing / diagram page (text labels may be incomplete) | Base unit dimensions — 50TJS008-014 9 | 6 | Original PDF page 9
10 | Text / tables | Performance data (cont) FAN PERFORMANCE — HORIZONTAL DISCHARGE UNITS 50LJS007 (6 TONS) — STANDARD MOTOR (BELT DRIVE) | 60 | Original PDF page 10
11 | Text / tables | Performance data (cont) FAN PERFORMANCE — HORIZONTAL DISCHARGE UNITS 50TJS008 (712/TONS) — STANDARD MOTOR (BELT DRIVE)* | 69 | Original PDF page 11
12 | Text / tables | Performance data (cont) FAN PERFORMANCE — HORIZONTAL DISCHARGE UNITS 50TJS009 (8 1/2 TONS) STANDARD MOTOR (BELT DRIVE)* | 75 | Original PDF page 12
13 | Text / tables | Performance data (cont) FAN PERFORMANCE — HORIZONTAL DISCHARGE UNITS 50TJS012 (10 TONS) STANDARD MOTOR (BELT DRIVE)* Ext | 75 | Original PDF page 13
14 | Text / tables | Performance data (cont) FAN PERFORMANCE — HORIZONTAL DISCHARGE UNITS 50TJS014 (121 /2 TONS) STANDARD MOTOR (BELT DRIVE)* | 83 | Original PDF page 14
15 | Text / tables | FAN RPM AT MOTOR PULLEY SETTINGS*— 50 Hz MOTOR PULLEY TURNS OPEN UNIT 0 1/2 1 1 1/2 2 | 30 | Original PDF page 15
16 | Text / tables | Electrical Data – 50LJS007, 50TJS008 – 014 ( 50 Hz ) VOLTAGE COMPRESSOR | 85 | Original PDF page 16
17 | Drawing / diagram page (text labels may be incomplete) | Typical piping and wiring — 50LJS007 (50TJS 008-014 shown) VERTICAL DISCHARGE DUCTING HORIZONTAL DISCHARGE DUCTING LEGEN | 19 | Original PDF page 17
18 | Drawing / diagram page (text labels may be incomplete) | Typical wiring schematic — 50LJS007 18 | 6 | Original PDF page 18
19 | Drawing / diagram page (text labels may be incomplete) | Typical wiring schematic — 50LJS007 (Cont.) 19 | 6 | Original PDF page 19
20 | Drawing / diagram page (text labels may be incomplete) | Typical wiring schematic — 50LJS007 (Cont.) 20 | 6 | Original PDF page 20
21 | Drawing / diagram page (text labels may be incomplete) | Typical wiring schematic — 50TJS008-014 21 | 6 | Original PDF page 21
22 | Drawing / diagram page (text labels may be incomplete) | Typical wiring schematic — 50TJS008-014 (Cont.) 22 | 6 | Original PDF page 22
23 | Drawing / diagram page (text labels may be incomplete) | Typical wiring schematic — 50TJS008-014 (Cont.) 23 | 6 | Original PDF page 23
24 | Text / tables | Controls the minimum position. If the supply air temperature is above 57 F, the damper continues to open until it reache | 56 | Original PDF page 24
25 | Text / tables | and forklift slots shall be provided to facilitate Guide specifications maneuvering. P | 62 | Original PDF page 25
26 | Text / tables | thick fiberglass filters of commercially 3. Optional crankcase heater should be available sizes. | 42 | Original PDF page 26
27 | Text / tables | Manufacturer reserves the right to discontinue, or change at any time, specifications or designs without notice and with | 4 | Original PDF page 27

## Page_Text
PDF page | Line | Extracted text
1 | 1 | 50LJS/TJS 007-014
1 | 2 | Product Single-Package
1 | 3 | Data Rooftop Units
1 | 4 | 50 Hz
1 | 5
1 | 6
1 | 7 | 6 to 12.5 Nominal Tons
1 | 8
1 | 9
1 | 10
1 | 11 | Single package rooftop cooling units with electric heat option. Compact, horizontal discharge units (vertical discharge
1 | 12 | option), combining installation flexibility with efficient performance.
1 | 13
1 | 14
1 | 15
1 | 16 | Features / Benefits
1 | 17 | • Higher Cooling Capacity.
1 | 18 | • Standard cooling operation at outdoor ambient
1 | 19 | temperature as high as 52 C (125 F).
1 | 20 | • F – Class Outdoor Condenser Motor
1 | 21 | • Galvanized steel cabinet with powder paint coat.
1 | 22 | • 2-inch (51 mm) return-air filters.
1 | 23 | • Commercial strength base rails (full perimeter).
1 | 24 | • Corrosion-resistant sloped condensate pan.
1 | 25 | • Single power entry to the unit.
1 | 26 | • Commercial duty motors with permanently
1 | 27 | lubricated bearings.
1 | 28 | All units feature sloped condensate drain pans in
1 | 29 | accordance with ASHRAE Standard 62. Also, the new
1 | 30 | sloped condensate pan permits either an external drain
1 | 31 | (outside the roof curb) or an internal bottom drain (inside
1 | 32 | the roof curb). Both options require an external, field-
1 | 33 | supplied disconnect, if desired.
1 | 34
1 | 35 | In addition, these units have a standard filter access door,
1 | 36 | which permits tool less changes and provides an opening
1 | 37 | for outdoor air options and accessories (models 007-014).
1 | 38 | Field installed electrical heaters are available in a wide
1 | 39 | range of capacities. Single point wiring kit makes
1 | 40 | installation simple.
1 | 41
1 | 42 | Simple electrical connections: Terminal boards, located in
1 | 43 | the base unit control box, facilitate connections to room
1 | 44 | thermostat, outdoor thermostat (s), economizer, and
1 | 45 | electrical heat permitting easy servicing.
1 | 46
1 | 47 | Thru-the-curb service connections accessory allow power
1 | 48 | and control wiring to be routed through the curb,
1 | 49 | minimizing roof penetrations. Both power and control
1 | 50 | connections are made on the same side of the unit to
1 | 51 | simplify installation.
1 | 52
1 | 53 | Quite and efficient operation is provided by belt-driven
1 | 54 | evaporator fans. The belt-driven evaporator fan with
1 | 55 | variable pitch pulleys allows adjustment to available static
1 | 56 | pressure to meet the job requirements of even the most
1 | 57 | demanding applications.
1 | 58
1 | 59
1 | 60
1 | 61
1 | 62 | 50TJS-02 PD 50HZ C 2005 1
2 | 1 | Model Number Nomenclature
2 | 2
2 | 3 | 50 TJ S 008 – 9 3 3 SR
2 | 4
2 | 5
2 | 6 | 50–Cooling Only/Cooling NE – Standard Unit, Size 007.
2 | 7 | with Optional Electric Heat SR – Standard Unit, Size 008-024.
2 | 8 | (Field Installed)
2 | 9 | Packaging
2 | 10 | LJ–Constant Volume, Size 007. 1–Standard.
2 | 11 | TJ–Constant Volume, Size 008-014. 3– Export.
2 | 12
2 | 13 | S - SAMCO
2 | 14 | Design Series
2 | 15 | Nominal Capacity in Tons (kW) 3 – With Fixed Orifice Expantion.
2 | 16 | 007 - 6 Tons (21 kW)
2 | 17 | 008 - 7 Tons (24.6 kW) Voltage
2 | 18 | 009 - 9 Tons (31.7 kW) 9 – 400/420-3-50
2 | 19 | 012 - 10 Tons (35 kW)
2 | 20 | 014 - 12 Tons (44 kW) Coil Fin Option
2 | 21 | – – AL Evaporator, AL Condenser.
2 | 22 | P – Pre-Coated Condenser Coil
2 | 23 | ( Aluminum Fins ).
2 | 24
2 | 25
2 | 26
2 | 27
2 | 28 | LEGEND
2 | 29 | AL Aluminum
2 | 30
2 | 31
2 | 32 | Quality Assurance
2 | 33
2 | 34
2 | 35
2 | 36
2 | 37 | Table of Contents
2 | 38 | Page
2 | 39 | Model Number Nomenclature. …………………………………………………………………. . 2
2 | 40 | ARI Capacity Rating………………………………………………………………………………. 3
2 | 41 | Physical Data………………………………………………………………………………………. 4
2 | 42 | Performance Data…………………………………………………………………………………. 6
2 | 43 | Base Unit Dimensions……………………………………………………………………………. 8
2 | 44 | Fan Performance Data……………………………………………………………………………. 10
2 | 45 | Electrical Data……………………………………………………………………………………… 16
2 | 46 | Typical Piping and Wiring……………………………………………………………………….. 17
2 | 47 | Typical Wiring Schematic………………………………………………………………………… 18
2 | 48 | Controls……………………………………………………………………………………………… 24
2 | 49 | Guide Specifications……………………………………………………………………………… 25
2 | 50
2 | 51
2 | 52 | 2
3 | 1 | ARI Capacity Rating*
3 | 2 | GROSS NET
3 | 3 | INPUT SOUND
3 | 4 | NOMINAL STANDARD COOLING COOLING
3 | 5 | UNIT TOTAL EER RATING
3 | 6 | TONS CFM CAPACITY CAPACITY
3 | 7 | kw (Bels)
3 | 8 | (Btuh) (Btuh)
3 | 9 | 50LJS007 6 2200 67,600 65,000 6.6 9.8 8.4
3 | 10 | 50TJS008 7 2800 85,300 82,200 9.8 8.4 8.6
3 | 11 | 50TJS009 9 3000 106,600 103,200 10.9 9.5 8.6
3 | 12 | 50TJS012 10 4000 122,500 117,350 13.4 8.8 8.8
3 | 13 | 50TJS014 12 4750 146,700 138,050 14.1 9.8 8.8
3 | 14
3 | 15 | Bels - Sound Levels (1 bel = 10 decibels)
3 | 16 | db - dry bulb
3 | 17 | EER - Energy Efficiency Ratio
3 | 18
3 | 19 | *ARI - Air Conditioning and Refrigeration Institute.
3 | 20
3 | 21
3 | 22
3 | 23 | 1. Rated in accordance with ARI Standards 210/240-89 or 360-86 and 270-84.
3 | 24 | 2. Net values reflecting the effects of circulating fan heat.
3 | 25 | 3. Ratings are based on:
3 | 26
3 | 27
3 | 28
3 | 29
3 | 30 | Cooling Standard: 80 F db, 67 wb indoor entering-air temperature and 95 F db air entering outdoor
3 | 31 | unit, Horizontal Discharge, 0.4 iwg External Static.
3 | 32
3 | 33
3 | 34
3 | 35
3 | 36 | 3
4 | 1 | Physical data (50 Hz) — English
4 | 2 | UNIT MODEL 50 SERIES LJS007 TJS008 TJS009 TJS012 TJS014
4 | 3 | Electrical Configuration V-PH-Hz 400 - 3 – 50 (+/- 10%)
4 | 4 | Nominal Cooling Capacity TR 6 7.0 9.0 10 12.0
4 | 5 | Kbtu/hr 72 84 108 120 144
4 | 6 | OPERATING WEIGHT
4 | 7 | Unit lbs 520 755 760 915 930
4 | 8 | Economizer lbs 34 44 44 44 44
4 | 9 | Roof Curb lbs 115 143 143 143 143
4 | 10 | COMPRESSOR type Scroll Hermetic, Reciprocating Scroll
4 | 11 | Quantity no. 1 2 2 2 2
4 | 12 | Oil (per compressor) oz 77 52 52 62 77
4 | 13 | REFRIGERANT type R -22
4 | 14 | Operating Charge
4 | 15 | Circuit 1 lbs-oz 8-3 5-4 6-3 6-5 7 - 12
4 | 16 | Circuit 2 lbs-oz - 5-4 6-3 6-5 7 - 12
4 | 17 | CONDENSER FAN type Propellar
4 | 18 | Quantity …. Diameter no….in. 1 …. 26 2 …. 22 2 …. 22 2 …. 22 2 …. 22
4 | 19 | Nominal CFM CFM 4300 8650 8650 9225 9225
4 | 20 | Motor* hp … rpm hp…rpm 1/3 ….960 1/2 …. 1100 1/2 …. 1100 1/2 …. 1100 1/2 …. 1100
4 | 21 | CONDENSER COIL type Enhanced Copper Tubes, Aluminum Double-Wavy Fins
4 | 22 | Rows … Fins/inch no….per in. 2 …17 1 …17 2 …17 2 …17 2 …17
4 | 23 | Total Face Area sq. ft 12.25 20.5 18 17.42 25
4 | 24 | EVAPORATOR FAN type Centrifugal Type
4 | 25 | Quantity …. Size no….in. 1 …10 x 10 1 …. 15 x15 1 …. 15 x15 1 …. 15 x15 1 …. 15 x15
4 | 26 | Drive Type type Belt Driven
4 | 27 | Nominal CFM CFM 2200 2800 3000 4000 4750
4 | 28 | Input Watts @ Nominal CFM Watts 800 900 1000 1500 2000
4 | 29 | Motor hp, rpm** hp , rpm 1.5, 1425 1.5 , 1425 1.5 , 1425 2 , 1425 3 , 1425
4 | 30 | Max. Continuous Bhp hp 2.4 2.4 2.4 2.9 3.7
4 | 31 | Motor Pulley Pitch Dia. in. 4.4 3.4 3.4 4.4 5
4 | 32 | Fan Pulley Pitch Dia. in. 5.19 5.5 5.5 7 7
4 | 33 | HIGH PRESSURE SWITCH Psig
4 | 34 | Standard Compressor IPRV setting 400 - 500
4 | 35 | Cutout / Reset (Auto) 463 - 477 / 300 - 340
4 | 36 | LOW PRESSURE SWITCH Psig
4 | 37 | Cutout / Reset (Manual) 4 – 10 / 17 – 27 14 / 20 - 30
4 | 38 | 0
4 | 39 | FREEZE-PROTECTION SWITCH F
4 | 40 | Opens / Closes 25 - 35 / 40 - 50
4 | 41 | EVAPORATOR COIL type Enhanced Copper Tubes, Aluminum Double-Wavy Fins
4 | 42 | Rows … Fins / inch no…per in. 4 …15 3 ….15 3 …..15 3 …. 15 4 …. 15
4 | 43 | Total Face Area sq. ft 5.5 8 8 10 11.1
4 | 44 | OUTDOOR AIR INLET SCREENS type Cleanable
4 | 45 | (With Optional Economizer)
4 | 46 | Quantity …. Size no….in. 1 ….20x24x1 1 … 20x25x1 + 1 ….16x25x1
4 | 47 | RETURN AIR FILTERS type Throw away
4 | 48 | Quantity …. Size no….in. 2 ….16x25x2 4 …. 16x20x2 4 … 20x20x2
4 | 49 | * Condenser Motor Efficiency: 80%.
4 | 50 | **Evaporator Motor Efficiency: LJ007 = 81%. TJ008-014 = 85%.
4 | 51
4 | 52
4 | 53
4 | 54
4 | 55 | 4
5 | 1 | Physical data (50 Hz)— SI
5 | 2 | UNIT MODEL 50 SERIES LJS007 TJS008 TJS009 TJS012 TJS014
5 | 3 | Electrical Configuration V-PH-Hz 400 - 3 – 50 (+/- 10%)
5 | 4 | Nominal Cooling Capacity TR 6 7.0 9.0 10 12.0
5 | 5 | KW 21.1 24.6 31.6 36.2 42.0
5 | 6 | OPERATING WEIGHT
5 | 7 | Unit Kg 236.3 343.1 345.4 415.9 422.7
5 | 8 | Economizer kg 15.45 20 20 20 20
5 | 9 | Roof Curb kg 52.2 65 65 65 65
5 | 10 | COMPRESSOR type Scroll Hermetic, Reciprocating Scroll
5 | 11 | Quantity no. 1 2 2 2 2
5 | 12 | Oil (per compressor) ml 2277 1538 1538 1834 2277
5 | 13 | REFRIGERANT type R -22
5 | 14 | Operating Charge
5 | 15 | Circuit 1 kg 3.7 2.4 2.8 2.9 3.5
5 | 16 | Circuit 2 kg - 2.4 2.8 2.9 3.5
5 | 17 | CONDENSER FAN type Propellar
5 | 18 | Quantity …. Diameter no …mm 1 …. 660.4 2 …. 558.8 2 …. 558.8 2 …. 558.8 2 …. 558.8
5 | 19 | Nominal Airflow L/s 2029 4082 4082 4353 4353
5 | 20 | Motor*KW … rps KW …rps 0.25 ….16 0.37 …. 18.33 0.37 …. 18.33 0.37 …. 18.33 0.37 …. 18.33
5 | 21 | CONDENSER COIL type Enhanced Copper Tubes, Aluminum Double-Wavy Fins
5 | 22 | Rows … Fins/inch no ….per 25 mm 2 …17 1 …17 2 …17 2 …17 2 …17
5 | 23 | Total Face Area sq. m 1.14 1.9 1.67 1.61 2.32
5 | 24 | EVAPORATOR FAN type Centrifugal Type
5 | 25 | Quantity …. Size no….mm x mm 1 …254 x 254 1 …. 381 x381 1 …. 381 x381 1 …. 381 x381 1 …. 381 x381
5 | 26 | Drive Type type Belt Driven
5 | 27 | Nominal Airflow L/s 1.38 1321 1416 1887 2242
5 | 28 | Input Watts @ Nominal L/s Watts 800 900 1000 1500 2000
5 | 29 | Motor Kw, rps** Kw , rps 1.1 , 23.8 1.1 , 23.8 1.1 , 23.8 1.5 , 23.8 2.2 , 23.8
5 | 30 | Max. Continuous BkW kW 1.8 1.8 1.8 2.1 2.7
5 | 31 | Motor Pulley Pitch Dia. mm 111.8 86.4 86.4 111.8 127
5 | 32 | Fan Pulley Pitch Dia. mm 132 139.7 139.7 177.8 177.8
5 | 33 | HIGH PRESSURE SWITCH kPa
5 | 34 | Standard Compressor IPRV setting 2758 - 3448
5 | 35 | Cutout / Reset (Auto) 3192 - 3289 / 2068 - 2344
5 | 36 | LOW PRESSURE SWITCH kPa
5 | 37 | Cutout / Reset (Manual) 28 - 69 / 117 - 186 97 / 138 - 207
5 | 38 | 0
5 | 39 | FREEZE-PROTECTION SWITCH C
5 | 40 | Opens / Closes (-)4 to 1.66 / 4.44 to 10
5 | 41 | EVAPORATOR COIL type Enhanced Copper Tubes, Aluminum Double-Wavy Fins
5 | 42 | Rows … Fins / inch no…per 25 mm 4 …15 3 ….15 3 …..15 3 …. 15 4 …. 15
5 | 43 | Total Face Area sq. m 0.51 0.74 0.74 0.929 1.03
5 | 44 | OUTDOOR AIR INLET SCREENS type Cleanable
5 | 45 | (With Optional Economizer)
5 | 46 | Quantity …. Size no….mm 1 ….508x609.6x25.4 1 … 508x635x25.4 + 1 ….406.4x635x25.4
5 | 47 | RETURN AIR FILTERS type Throw away
5 | 48 | Quantity …. Size no….mm 2 ….406.4x635x50.8 4 …. 406.4x508x50.8 4 … 508x508x50.8
5 | 49 | * Condenser Motor Efficiency: 80%.
5 | 50 | **Evaporator Motor Efficiency: LJ007 = 81%. TJ008-014 = 85%.
5 | 51
5 | 52
5 | 53
5 | 54
5 | 55 | 5
6 | 1 | Performance data
6 | 2 | COOLING CAPACITIES
6 | 3 | 50LJS007 (6 TONS)
6 | 4 | Temp (F) Evaporator Air Quantity — Cfm/BF
6 | 5 | Air Entering 1060/0.04 2200/0.06 2750/0.07
6 | 6 | Condenser Evaporator Air — Ewb (F)
6 | 7 | (Edb) 72 67 62 72 67 62 72 67 62
6 | 8 | TC 77.6 71.0 64.8 81.8 74.6 67.7 85.7 76.1 69.9
6 | 9 | 75 SHC 37.3 46.4 55.1 41.5 53.1 64.3 45.7 58.8 69.8
6 | 10 | kW 4.37 4.35 4.32 4.39 4.36 4.33 4.41 4.37 4.35
6 | 11 | TC 74.7 67.7 60.5 78.6 71.1 63.8 80.8 72.7 67.3
6 | 12 | 85 SHC 36.3 45.1 53.2 40.6 52.0 62.1 44.5 58.0 67.2
6 | 13 | kW 4.77 4.73 4.67 4.81 4.76 4.71 4.83 4.78 4.74
6 | 14 | TC 71.8 64.4 56.2 75.4 67.6 59.9 76.9 69.3 65.6
6 | 15 | 95 SHC 35.3 43.9 51.4 39.7 50.9 59.9 43.3 57.3 64.5
6 | 16 | kW 5.18 5.11 5.02 5.23 5.16 5.08 5.25 5.18 5.13
6 | 17 | TC 68.4 60.3 50.8 71.4 63.8 56.2 73.4 65.4 61.2
6 | 18 | 105 SHC 34.2 42.3 48.8 38.4 49.5 56.2 42.5 56.1 61.1
6 | 19 | kW 5.59 5.48 5.37 5.64 5.55 5.46 5.68 5.59 5.53
6 | 20 | TC 64.7 54.6 45.0 67.7 57.6 52.0 69.4 60.6 57.3
6 | 21 | 115 SHC 32.9 40.1 45.0 37.3 47.3 51.9 41.5 45.2 57.3
6 | 22 | kW 5.99 5.86 5.74 6.06 5.93 5.85 6.10 5.97 5.93
6 | 23 | TC 60.9 48.9 39.3 64.1 51.5 47.7 65.3 55.8 53.4
6 | 24 | 125 SHC 31.7 37.9 39.3 36.1 45.0 47.7 40.4 52.4 53.4
6 | 25 | kW 6.39 6.23 6.12 6.48 6.31 6.24 6.53 6.36 6.32
6 | 26
6 | 27
6 | 28 | 50TJS008 (7.0 TONS)
6 | 29 | Evaporator Air Quantity — Cfm/BF
6 | 30 | Temp (F) Air Entering 2250/0.07 2800/0.09 3000/0.10 3750/0.12
6 | 31 | Condenser (Edb) Evaporator Air — Ewb (F)
6 | 32 | 72 67 62 72 67 62 72 67 62 72 67 62
6 | 33 | TC 99.2 91.5 83.2 102.1 94.8 86.9 102.7 95.5 87.6 107.5 100.0 92.1
6 | 34 | 75 SHC 47.7 59.6 70.6 50.8 65.4 78.7 51.7 67.4 81.1 57.3 76.2 90.8
6 | 35 | kW 7.40 7.07 6.74 7.55 7.24 6.93 7.59 7.30 6.97 7.74 7.45 7.11
6 | 36 | TC 94.8 87.0 78.7 98.2 90.3 82.2 99.0 91.1 83.0 103.0 95.3 88.2
6 | 37 | 85 SHC 46.3 58.1 68.7 49.8 64.1 76.8 51.0 66.2 79.1 55.9 74.8 88.0
6 | 38 | kW 7.94 7.61 7.26 8.11 7.78 7.45 8.15 7.82 7.49 8.28 7.96 7.67
6 | 39 | TC 90.5 82.2 73.9 93.6 85.3 77.2 94.2 85.9 78.4 97.8 89.8 83.9
6 | 40 | 95 SHC 44.8 56.2 66.4 48.4 62.3 74.5 49.6 64.5 76.2 54.7 73.2 83.9
6 | 41 | kW 8.48 8.13 7.76 8.67 8.30 7.92 8.71 8.34 7.98 8.81 8.46 8.21
6 | 42 | TC 85.3 77.0 68.3 87.8 79.9 72.0 88.4 80.5 73.3 92.3 84.1 79.3
6 | 43 | 105 SHC 43.0 54.2 63.7 46.5 60.4 71.6 47.7 62.5 73.0 53.3 71.3 79.3
6 | 44 | kW 9.00 8.61 8.28 9.13 8.77 8.44 9.19 8.81 8.50 9.31 8.96 8.73
6 | 45 | TC 82.8 73.8 66.0 85.2 76.8 69.6 85.6 77.4 71.0 89.4 81.0 77.5
6 | 46 | 115 SHC 42.6 53.8 63.2 46.4 60.4 69.6 47.8 62.6 71.0 53.9 71.8 77.3
6 | 47 | kW 9.50 9.10 8.73 9.64 9.25 8.96 9.69 9.29 9.04 9.83 9.44 9.27
6 | 48 | TC 81.0 71.6 64.4 83.4 74.6 67.9 83.6 75.2 69.4 87.3 78.8 76.2
6 | 49 | 122 SHC 42.3 53.5 62.9 46.3 60.4 68.2 47.9 62.6 69.6 54.2 72.2 75.9
6 | 50 | kW 9.85 9.45 9.05 10.01 9.58 9.32 10.03 9.63 9.42 10.19 9.77 9.65
6 | 51
6 | 52
6 | 53
6 | 54 | 50TJS009 (9.0 TONS)
6 | 55 | Evaporator Air Quantity — Cfm/BF
6 | 56 | Temp (F) Air Entering 2550/0.08 3000/0.10 3400/0.11 4250/0.135
6 | 57 | Condenser (Edb) Evaporator Air — Ewb (F)
6 | 58 | 72 67 62 72 67 62 72 67 62 72 67 62
6 | 59 | TC 121.8 113.3 103.5 124.6 116.3 106.4 125.5 117.9 108.3 130.4 122.4 113.3
6 | 60 | 75 SHC 75.1 64.7 79.3 78.6 68.0 85.1 84.1 71.1 89.5 34.9 78.8 100.6
6 | 61 | kW 7.82 7.62 7.42 7.91 10.74 7.48 7.94 6.76 7.56 8.02 7.85 7.65
6 | 62 | TC 118.4 108.9 98.2 120.9 111.7 101.4 122.5 113.6 103.2 128.0 118.3 108.5
6 | 63 | 85 SHC 56.4 70.7 84.0 58.8 75.8 91.0 60.8 79.8 96.7 67.0 89.7 107.7
6 | 64 | kW 8.51 8.27 8.01 5.57 8.36 8.09 8.65 8.43 8.17 8.77 8.53 8.28
6 | 65 | TC 114.0 103.8 91.2 116.2 106.6 95.5 117.6 108.3 97.9 122.9 112.8 114.5
6 | 66 | 95 SHC 55.0 68.9 80.9 57.5 74.1 88.7 59.7 78.5 94.4 66.3 88.7 103.7
6 | 67 | kW 8.95 9.02 8.73 9.04 9.11 8.84 9.11 9.17 8.91 4.79 9.30 9.05
6 | 68 | TC 107.9 98.2 85.1 110.7 100.6 88.4 112.2 102.1 91.9 116.6 106.5 98.9
6 | 69 | 105 SHC 52.8 56.4 77.9 55.9 72.2 85.1 58.3 76.4 90.5 64.4 86.8 98.9
6 | 70 | kW 9.80 9.49 9.13 9.91 9.60 9.27 9.98 9.66 9.35 10.09 9.78 9.54
6 | 71 | TC 97.7 87.9 75.9 99.9 90.4 78.8 101.3 91.8 82.4 105.0 95.7 90.1
6 | 72 | 115 SHC 48.7 61.7 71.9 51.8 66.9 78.1 54.0 71.2 82.3 59.7 81.0 90.0
6 | 73 | kW 10.33 9.97 9.61 10.46 10.10 9.75 10.54 10.18 9.88 10.61 10.30 10.10
6 | 74 | TC 90.5 80.7 69.5 92.4 83.2 72.1 93.6 84.6 75.8 96.8 88.1 83.9
6 | 75 | 122 SHC 45.8 65.4 67.7 48.9 63.2 73.2 51.0 67.6 76.6 56.4 76.9 83.7
6 | 76 | kW 10.70 10.31 9.94 10.85 10.45 10.09 10.93 10.55 10.25 10.97 10.67 10.49
6 | 77
6 | 78
6 | 79
6 | 80
6 | 81 | 6
7 | 1 | COOLING CAPACITIES (Cont.)
7 | 2 | 50TJS012 (10 TONS)
7 | 3 | Temp (F) Evaporator Air Quantity — Cfm/BF
7 | 4 | Air Entering 3000/0.095 4000/0.125 5000/0.15
7 | 5 | Condenser Evaporator Air — Ewb (F)
7 | 6 | (Edb) 72 67 62 72 67 62 72 67 62
7 | 7 | TC 139.8 128.4 115.3 146.6 134.5 123.3 153.8 140.8 129.8
7 | 8 | 75 SHC 68.7 85.0 100.2 75.3 96.2 116.0 83.7 109.6 129.2
7 | 9 | kW 9.86 9.50 9.19 10.10 9.71 9.36 10.27 9.85 9.50
7 | 10 | TC 133.8 123.1 107.0 140.0 128.8 117.8 147.0 134.2 124.7
7 | 11 | 85 SHC 66.1 82.8 96.5 73.1 94.5 113.4 81.3 106.9 124.6
7 | 12 | kW 10.51 10.17 9.84 10.78 10.38 10.04 10.95 10.51 10.19
7 | 13 | TC 127.7 117.0 99.5 133.3 122.5 110.0 139.4 128.1 119.7
7 | 14 | 95 SHC 64.0 80.7 92.6 71.1 92.5 109.0 78.6 105.1 119.6
7 | 15 | kW 11.24 10.89 10.50 11.49 11.10 10.74 11.64 11.25 10.94
7 | 16 | TC 121.5 107.6 90.4 126.3 115.2 101.4 132.3 120.9 113.3
7 | 17 | 105 SHC 62.1 77.0 87.7 68.8 90.3 101.4 76.7 103.1 113.3
7 | 18 | kW 12.05 11.64 11.21 12.25 11.86 11.52 12.39 12.01 11.77
7 | 19 | TC 111.5 94.9 81.6 116.3 100.7 90.5 121.2 108.5 101.6
7 | 20 | 115 SHC 57.6 70.2 80.8 64.4 82.3 90.5 72.0 95.5 101.6
7 | 21 | kW 12.63 12.17 11.74 12.85 12.42 12.13 12.98 12.57 12.36
7 | 22 | TC 104.5 86.1 75.4 109.3 90.6 82.9 113.5 99.9 93.5
7 | 23 | 122 SHC 54.4 65.4 76.0 61.2 76.6 82.9 68.6 90.1 93.5
7 | 24 | kW 13.03 12.55 12.11 13.28 12.82 12.56 13.39 12.96 12.78
7 | 25
7 | 26
7 | 27
7 | 28
7 | 29 | 50TJS014 (12.5 TONS)
7 | 30 | Evaporator Air Quantity — Cfm/BF
7 | 31 | Temp (F) Air
7 | 32 | 3750/0.10 4500/0.125 5000/0.15 6250/0.15
7 | 33 | Entering
7 | 34 | Condenser (Edb) Evaporator Air — Ewb (F)
7 | 35 | 72 67 62 72 67 62 72 67 62 72 67 62
7 | 36 | TC 166.5 153.9 141.5 171.7 158.8 146.3 173.5 161.5 148.3 181.1 169.0 156.5
7 | 37 | 75 SHC 81.2 101.8 121.5 86.7 110.2 133.1 89.3 115.9 139.0 98.8 130.9 155.5
7 | 38 | kW 9.96 9.68 9.40 10.06 9.78 9.49 10.15 9.87 9.49 10.25 9.96 9.68
7 | 39 | TC 160.6 147.7 133.3 165.2 152.5 139.4 167.8 154.6 142.0 175.6 161.8 150.8
7 | 40 | 85 SHC 79.6 99.4 117.6 85.0 108.0 130.0 87.9 113.6 136.2 97.6 129.1 150.5
7 | 41 | kW 10.81 10.43 10.15 10.90 10.62 10.34 11.00 10.72 10.34 11.19 10.81 10.53
7 | 42 | TC 153.6 141.2 125.2 158.2 145.6 131.9 160.8 147.7 135.4 167.6 154.3 144.8
7 | 43 | 95 SHC 77.2 96.7 113.7 82.6 105.4 126.3 86.0 111.2 133.0 95.1 126.6 144.8
7 | 44 | kW 11.66 11.28 10.90 11.84 11.47 11.09 11.94 11.56 11.19 12.03 11.66 11.37
7 | 45 | TC 146.9 134.0 116.7 150.6 137.9 123.5 152.7 140.0 128.0 159.9 146.3 138.6
7 | 46 | 105 SHC 75.0 94.1 109.5 80.1 102.6 121.5 83.3 108.4 127.9 93.5 123.7 138.5
7 | 47 | kW 12.60 12.13 11.75 12.69 12.31 11.84 12.78 12.41 11.94 12.97 12.50 12.22
7 | 48 | TC 128.7 116.4 99.5 132.4 120.6 107.7 134.0 122.7 112.5 139.3 128.1 122.1
7 | 49 | 115 SHC 67.0 84.2 97.1 71.9 92.6 107.6 74.8 98.2 112.4 83.4 112.2 122.0
7 | 50 | kW 13.87 13.39 12.90 14.07 13.58 13.10 14.07 13.68 13.19 14.16 13.77 13.48
7 | 51 | TC 115.9 104.0 87.5 119.7 108.5 96.7 121.0 110.5 101.7 124.9 115.3 110.5
7 | 52 | 122 SHC 61.5 77.3 88.4 66.2 85.6 97.9 68.9 91.1 101.6 76.3 104.1 110.4
7 | 53 | kW 14.76 14.27 13.71 15.03 14.47 13.97 14.96 14.57 14.07 15.00 14.66 14.37
7 | 54
7 | 55
7 | 56 | LEGEND hIdb = hedb - Total capacity (Btuh)
7 | 57 | 4.5 x cfm
7 | 58 | BF – Bypass factor Where: hewb = Enthalpy of air entering evaporator coil
7 | 59 | Edb – Entering Dry-Bulb 3. The SHC is based on 80 F edb temperature of air entering
7 | 60 | Ewd – Entering Wet-Bulb evaporator coil.
7 | 61 | KW – Compressor Motor Power Input Below 80 F edb, subtract (corr factor x cfm) from SHC.
7 | 62 | Idb – Leaving Dry-Bulb Above 80 F edb, add (corr factor x cfm) to SHC.
7 | 63 | Iwb – Leaving Wet-Bulb ENTERING AIR DRY-BULB TEMP (F)
7 | 64 | SHC – Sensible Heat Capacity (1000 Rtuh) Gross BYPASS
7 | 65 | 79 78 77 76 75 Under 75
7 | 66 | TC – Total Capacity (1000 Btuh) Gross FACTOR
7 | 67 | (BF) 81 82 83 84 85 Over 85
7 | 68 | NOTES: Correction factor
7 | 69 | 1. Direct interpolation is permissible. Do not extrapolate. .05 1.04 2.07 3.11 4.14 5.18
7 | 70 | Use formula
7 | 71 | 2. the following formulas may be used: .10 .98 1.96 2.94 3.92 4.90
7 | 72 | shown
7 | 73 | .20 .87 1.74 2.62 3.49 4.36
7 | 74 | below.
7 | 75 | Sensible capacity (Btuh) .30 .76 1.53 2.29 3.05 3.82
7 | 76 | tIdb = tedb -
7 | 77 | 1.10 x cfm Interpolation is permissible.
7 | 78 | TIwb = Wet-bulb temperature corresponding to enthalpy of Correction factor = 1.10 x (1-BF) x (edb – 80)
7 | 79 | air leaving evaporator coil.
7 | 80
7 | 81
7 | 82
7 | 83
7 | 84 | 7
8 | 1 | Base unit dimensions — 50LJS007
8 | 2
8 | 3
8 | 4
8 | 5
8 | 6 | 8
9 | 1 | Base unit dimensions — 50TJS008-014
9 | 2
9 | 3
9 | 4
9 | 5
9 | 6 | 9
10 | 1 | Performance data (cont)
10 | 2 | FAN PERFORMANCE — HORIZONTAL DISCHARGE UNITS
10 | 3 | 50LJS007 (6 TONS) — STANDARD MOTOR (BELT DRIVE)*
10 | 4 | External Static Pressure (in. wg)
10 | 5 | Airflow
10 | 6 | 0.1 0.2 0.4 0.6 0.8
10 | 7 | (Cfm)
10 | 8 | Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts
10 | 9 | 1800 765 0.45 487 821 0.51 532 923 0.65 638 1019 0.81 843 1099 0.96 883
10 | 10 | 1900 802 0.45 539 854 0.58 585 953 0.73 700 1046 0.90 835 1126 1.06 965
10 | 11 | 2000 840 0.60 600 888 0.66 646 984 0.82 771 1073 0.99 907 1154 1.16 1047
10 | 12 | 2100 878 0.69 669 923 0.75 716 1015 0.91 843 1101 1.08 981 1182 1.27 1140
10 | 13 | 2200 916 0.78 739 958 0.85 795 1046 1.01 924 1129 1.19 1072 1209 1.39 1241
10 | 14 | 2300 954 0.89 827 993 0.96 883 1079 1.13 1022 1160 1.31 1173 1237 1.51 1344
10 | 15 | 2400 993 1.00 916 1029 1.07 973 1112 1.25 1123 1190 1.43 1275 1264 1.63 1447
10 | 16 | 2500 1031 1.13 1022 1066 1.20 1081 1145 1.39 1241 1220 1.57 1396 1292 1.77 1569
10 | 17 | 2600 1070 1.26 1131 1103 1.34 1199 1179 1.52 1353 1251 1.71 1517 1322 1.92 1700
10 | 18 | 2700 1109 1.41 1258 1140 1.48 1318 1212 1.67 1482 1283 1.87 1656 1352 2.09 1849
10 | 19 | 2800 1148 1.57 1396 1177 1.64 1456 1246 1.83 1621 1316 2.04 1805 1383 2.26 1997
10 | 20 | 2900 1188 1.74 1543 1215 1.81 1604 1281 2.00 1770 1349 2.22 1962 1413 2.44 2154
10 | 21 | 3000 1227 1.92 1700 1253 2.00 1770 1316 2.19 1936 1382 2.42 2136 1444 2.63 2317
10 | 22
10 | 23
10 | 24 | 50LJS007 (6 TONS) — STANDARD MOTOR (BELT DRIVE)* (cont)
10 | 25 | External Static Pressure (in. wg)
10 | 26 | Airflow 1.0 1.2 1.4 1.6
10 | 27 | (Cfm)
10 | 28 | Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts
10 | 29 | 1800 1178 1.14 1031 1249 1.32 1182 1316 1.52 1353 1382 1.72 1526
10 | 30 | 1900 1201 1.23 1106 1274 1.43 1275 1338 1.62 1439 1402 1.83 1621
10 | 31 | 2000 1226 1.33 1990 1297 1.53 1361 1363 1.73 1534 1424 1.94 1718
10 | 32 | 2100 1252 1.45 1292 1320 1.64 1456 1388 1.85 1639 1448 2.07 1831
10 | 33 | 2200 1280 1.58 1404 1345 1.77 1569 1410 1.97 1744 1473 2.20 1945
10 | 34 | 2300 1309 1.71 1517 1372 1.91 1691 1434 2.11 1866 1496 2.34 2067
10 | 35 | 2400 1336 1.85 1639 1400 2.06 1823 1459 2.26 1997 1519 2.48 2188
10 | 36 | 2500 1363 2.00 1770 1428 2.22 1962 1486 2.43 2145 1543 2.65 2335
10 | 37 | 2600 1390 2.15 1901 1456 2.38 2102 1514 2.61 2300 1569 2.83 2487
10 | 38 | 2700 1418 2.31 2041 1483 2.56 2257 1543 2.80 2462 — — —
10 | 39 | 2800 1446 2.48 2188 1510 2.73 2403 — — — — — —
10 | 40 | 2900 1476 2.67 2352 1537 2.92 2562 — — — — — —
10 | 41 | 3000 1506 2.88 2529 — — — — — — — — —
10 | 42 | LEGEND 2. Maximum usable watts input is 2120 and maximum continuous bhp
10 | 43 | Bhp — Brake Horsepower Input to Fan is 2.40. Extensive motor and electrical testing on these units
10 | 44 | FIOP — Factory-Installed Option ensures that the full range of the motor can be utilized with confi-
10 | 45 | Watts — Input Watts to Motor dence. Using your fan motors up to the wattage ratings shown will
10 | 46 | not result in nuisance tripping or premature motor failure. Unit war-
10 | 47 | *Motor drive range: 1070 to 1460 rpm. All other rpms require field- ranty will not be affected.
10 | 48 | supplied drive.
10 | 49 | NOTES:
10 | 50 | 3. Values include losses for filters, unit casing, and wet coils.
10 | 51 | 1. Boldface Out of Drive Package or Motor range .
10 | 52 | 4. Use of a field-supplied motor may affect wire sizing. Contact your
10 | 53 | Carrier representative for details.
10 | 54 | 5. Interpolation is permissible. Do not extrapolate.
10 | 55 | 6. Motor Efficiency: 81%.
10 | 56
10 | 57
10 | 58
10 | 59
10 | 60 | 10
11 | 1 | Performance data (cont)
11 | 2 | FAN PERFORMANCE — HORIZONTAL DISCHARGE UNITS
11 | 3 | 50TJS008 (712/TONS) — STANDARD MOTOR (BELT DRIVE)*
11 | 4 | External Static Pressure (in. wg)
11 | 5 | Airflow
11 | 6 | 0.2 0.4 0.6 0.8 1.0
11 | 7 | (Cfm)
11 | 8 | Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts
11 | 9 | 2250 465 0.43 473 554 0.64 630 630 0.86 803 695 1.09 989 757 1.34 1199
11 | 10 | 2300 471 0.45 487 559 0.66 646 635 0.89 827 699 1.12 1014 760 1.37 1224
11 | 11 | 2400 482 0.50 524 569 0.71 684 645 0.95 875 708 1.18 1064 768 1.44 1284
11 | 12 | 2500 494 0.54 554 581 0.76 723 654 1.01 924 717 1.25 1123 776 1.51 1344
11 | 13 | 2550 501 0.57 577 587 0.79 747 659 1.05 956 722 1.29 1156 780 1.55 1378
11 | 14 | 2660 507 0.59 592 592 0.82 771 663 1.08 981 727 1.32 1182 784 1.58 1404
11 | 15 | 2700 520 0.65 638 604 0.89 827 672 1.14 1031 737 1.40 1250 793 1.66 1473
11 | 16 | 2800 533 0.71 684 615 0.95 875 683 1.20 1081 747 1.49 1327 802 1.75 1552
11 | 17 | 2900 546 0.77 731 626 1.02 932 693 1.27 1140 756 1.57 1396 813 1.84 1630
11 | 18 | 3000 559 0.83 779 637 1.09 989 704 1.35 1207 765 1.66 1473 823 1.94 1718
11 | 19 | 3100 572 0.90 835 648 1.17 1056 715 1.43 1275 775 1.74 1543 832 2.05 1814
11 | 20 | 3200 585 0.96 883 660 1.24 1114 727 1.52 1353 785 1.83 1627 841 2.15 1901
11 | 21 | 3300 598 1.03 940 671 1.32 1182 739 1.62 1439 795 1.91 1691 851 2.26 1997
11 | 22 | 3400 610 1.10 998 682 1.41 1258 750 1.72 1526 806 2.01 1779 860 2.36 2084
11 | 23 | 3500 623 1.17 1056 694 1.50 1335 761 1.82 1613 817 2.11 1866 870 2.47 2180
11 | 24 | 3600 636 1.25 1123 707 1.60 1422 772 1.93 1709 828 2.23 1971 880 2.57 2266
11 | 25 | 3700 649 1.33 1190 720 1.71 1517 783 2.03 1796 840 2.35 2076 890 2.69 2369
11 | 26 | 3750 655 1.37 1224 727 1.77 1569 789 2.09 1849 846 2.42 2136 896 2.75 2420
11 | 27
11 | 28
11 | 29 | 50TJS008 (712/TONS — STANDARD MOTOR (BELT DRIVE)* (cont)
11 | 30 | External Static Pressure (in. wg)
11 | 31 | Airflow
11 | 32 | 1.2 1.4 1.6 1.8 2.0
11 | 33 | (Cfm)
11 | 34 | Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts
11 | 35 | 2250 810 1.62 1439 850 1.91 1691 873 2.20 1945 883 2.50 2206 895 2.78 2445
11 | 36 | 2300 816 1.65 1465 859 1.94 1718 888 2.24 1980 903 2.55 2249 911 2.85 2504
11 | 37 | 2400 824 1.72 1526 872 2.01 1779 909 2.32 2050 931 2.64 2326 935 2.96 2595
11 | 38 | 2500 832 1.79 1587 882 2.09 1849 925 2.40 2119 955 2.72 2394 972 3.06 2678
11 | 39 | 2550 836 1.83 1621 887 2.13 1884 931 2.45 2162 964 2.77 2436 986 3.11 2718
11 | 40 | 2660 839 1.87 1656 891 2.17 1919 936 2.49 2197 973 2.82 2479 999 3.16 2759
11 | 41 | 2700 846 1.95 1726 898 2.26 1997 946 2.58 2275 987 2.91 2554 1019 3.26 2839
11 | 42 | 2800 855 2.04 1805 906 2.35 2076 954 2.67 2352 997 3.01 2637 1034 3.36 2917
11 | 43 | 2900 863 2.13 1884 913 2.44 2154 961 2.77 2436 1006 3.12 2727 — — —
11 | 44 | 3000 872 2.22 1962 921 2.54 2240 969 2.88 2529 1014 3.22 2807 — — —
11 | 45 | 3100 882 2.33 2058 930 2.65 2335 976 2.99 2620 1021 3.34 2902 — — —
11 | 46 | 3200 892 2.45 2162 939 2.76 2428 984 3.10 2710 — — — — — —
11 | 47 | 3300 902 2.57 2266 948 2.88 2529 993 3.21 2799 — — — — — —
11 | 48 | 3400 912 2.69 2369 958 3.01 2637 1002 3.34 2902 — — — — — —
11 | 49 | 3500 921 2.82 2479 968 3.15 2751 — — — — — — — — —
11 | 50 | 3600 930 2.95 2587 978 3.29 2862 — — — — — — — — —
11 | 51 | 3700 940 3.07 2686 — — — — — — — — — — — —
11 | 52 | 3750 945 3.14 2743 — — — — — — — — — — — —
11 | 53 | LEGEND 2. Maximum usable watts input is 2120 and maximum continuous bhp
11 | 54 | Bhp — Brake Horsepower Input to Fan is 2.90. Extensive motor and electrical testing on these units
11 | 55 | FIOP — Factory-Installed Option ensures that the full range of the motor can be utilized with confi-
11 | 56 | Watts — Input Watts to Motor dence. Using your fan motors up to the wattage ratings shown will
11 | 57 | not result in nuisance tripping or premature motor failure. Unit war-
11 | 58 | *Motor drive range: 590 to 840 rpm. ranty will not be affected.
11 | 59 | All other rpms require field-supplied drive.
11 | 60 | NOTES: 3. Values include losses for filters, unit casing, and wet coils.
11 | 61 | 1. Boldface Out of Drive Package or Motor range . 4. Use of a field-supplied motor may affect wire sizing. Contact your
11 | 62 | Carrier representative for details.
11 | 63 | 5. Interpolation is permissible. Do not extrapolate.
11 | 64 | 6. Motor Efficiency: 85%.
11 | 65
11 | 66
11 | 67
11 | 68
11 | 69 | 11
12 | 1 | Performance data (cont)
12 | 2 | FAN PERFORMANCE — HORIZONTAL DISCHARGE UNITS
12 | 3 | 50TJS009 (8 1/2 TONS) STANDARD MOTOR (BELT DRIVE)*
12 | 4 | External Static Pressure (in. wg)
12 | 5 | Airflow
12 | 6 | 0.2 0.4 0.6 0.8 1.0
12 | 7 | (Cfm)
12 | 8 | Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts
12 | 9 | 2550 501 0.57 577 587 0.79 747 659 1.05 956 722 1.29 1156 780 1.55 1378
12 | 10 | 2660 507 0.59 592 592 0.82 771 663 1.08 981 727 1.32 1182 784 1.58 1404
12 | 11 | 2700 520 0.65 638 604 0.89 827 672 1.14 1031 737 1.40 1250 793 1.66 1473
12 | 12 | 2800 533 0.71 684 615 0.95 875 683 1.20 1081 747 1.49 1327 802 1.75 1552
12 | 13 | 2900 546 0.77 731 626 1.02 932 693 1.27 1140 756 1.57 1396 813 1.84 1630
12 | 14 | 3000 559 0.83 779 637 1.09 989 704 1.35 1207 765 1.66 1473 823 1.94 1718
12 | 15 | 3100 572 0.90 835 648 1.17 1056 715 1.43 1275 775 1.74 1543 832 2.05 1814
12 | 16 | 3200 585 0.96 883 660 1.24 1114 727 1.52 1353 785 1.83 1321 841 2.15 1901
12 | 17 | 3300 598 1.03 940 671 1.32 1182 739 1.62 1439 795 1.91 1691 851 2.26 1997
12 | 18 | 3400 610 1.10 998 682 1.41 1258 750 1.72 1526 806 2.01 1779 860 2.36 2084
12 | 19 | 3500 623 1.17 1056 694 1.50 1335 761 1.82 1613 817 2.11 1866 870 2.47 2180
12 | 20 | 3600 636 1.25 1123 707 1.60 1422 772 1.93 1709 828 2.23 1971 880 2.57 2266
12 | 21 | 3700 649 1.33 1190 720 1.71 1517 783 2.03 1796 840 2.35 2076 890 2.69 2369
12 | 22 | 3750 655 1.37 1224 727 1.77 1569 789 2.09 1849 846 2.42 2136 896 2.75 2420
12 | 23 | 3800 661 1.41 1258 733 1.82 1613 795 2.15 1901 852 2.48 2188 901 2.80 2462
12 | 24 | 3900 674 1.49 1327 746 1.93 1709 806 2.26 1997 863 2.61 2300 912 2.93 2571
12 | 25 | 4000 687 1.57 1396 759 2.05 1814 817 2.38 2102 874 2.75 2420 923 3.08 2694
12 | 26 | 4100 699 1.60 1473 772 2.17 1919 828 2.50 2206 885 2.88 2529 935 3.23 2815
12 | 27 | 4200 712 1.75 1552 785 2.30 2032 840 2.64 2326 897 3.03 2653 947 3.39 2940
12 | 28 | 4250 719 1.80 1595 792 2.37 2093 846 2.71 2386 903 3.10 2710 — — —
12 | 29
12 | 30
12 | 31 | 50TJS009 (8 1/2 TONS) STANDARD MOTOR (BELT DRIVE)* (cont)
12 | 32 | External Static Pressure (in. wg)
12 | 33 | Airflow
12 | 34 | 1.2 1.4 1.6 1.8 2.0
12 | 35 | (Cfm)
12 | 36 | Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts
12 | 37 | 2550 836 1.83 1621 887 2.13 1884 931 2.45 2162 964 2.77 2436 986 3.11 2718
12 | 38 | 2660 839 1.87 1656 891 2.17 1919 936 2.49 2197 973 2.82 2479 999 3.16 2759
12 | 39 | 2700 846 1.95 1726 898 2.26 1997 946 2.58 2275 987 2.91 2554 1019 3.26 2839
12 | 40 | 2800 855 2.04 1805 906 2.35 2076 954 2.67 2352 997 3.01 2637 1034 3.36 2917
12 | 41 | 2900 863 2.13 1884 913 2.44 2154 961 2.77 2436 1006 3.12 2727 — — —
12 | 42 | 3000 872 2.22 1962 921 2.54 2240 969 2.88 2529 1014 3.22 2807 — — —
12 | 43 | 3100 882 2.33 2058 930 2.65 2335 976 2.99 2620 1021 3.34 2902 — — —
12 | 44 | 3200 892 2.45 2162 939 2.76 2428 984 3.10 2710 — — — — — —
12 | 45 | 3300 902 2.57 2266 948 2.88 2529 993 3.21 2799 — — — — — —
12 | 46 | 3400 912 2.69 2369 958 3.01 2637 1002 3.34 2902 — — — — — —
12 | 47 | 3500 921 2.82 2479 968 3.15 2751 — — — — — — — — —
12 | 48 | 3600 930 2.95 2587 978 3.29 2862 — — — — — — — — —
12 | 49 | 3700 940 3.07 2686 — — — — — — — — — — — —
12 | 50 | 3750 945 3.14 2743 — — — — — — — — — — — —
12 | 51 | 3800 949 3.20 2781 — — — — — — — — — — — —
12 | 52 | 3900 959 3.33 2894 — — — — — — — — — — — —
12 | 53 | 4000 — — — — — — — — — — — — — — —
12 | 54 | 4100 — — — — — — — — — — — — — — —
12 | 55 | 4200 — — — — — — — — — — — — — — —
12 | 56 | 4250 — — — — — — — — — — — — — — —
12 | 57 | LEGEND 2. Maximum usable watts input is 2120 and maximum continuous bhp
12 | 58 | Bhp — Brake Horsepower Input to Fan is 2.90. Extensive motor and electrical testing on these units
12 | 59 | FIOP — Factory-Installed Option ensures that the full range of the motor can be utilized with confi-
12 | 60 | Watts — Input Watts to Motor dence. Using your fan motors up to the wattage ratings shown will
12 | 61 | not result in nuisance tripping or premature motor failure. Unit war-
12 | 62 | *Motor drive range: 685 to 935 rpm. All other rpms require field- ranty will not be affected.
12 | 63 | supplied drive.
12 | 64 | NOTES:
12 | 65 | 3. Values include losses for filters, unit casing, and wet coils.
12 | 66 | 1. Boldface Out of Drive Package or Motor range .
12 | 67 | 4. Use of a field-supplied motor may affect wire sizing. Contact your
12 | 68 | Carrier representative for details.
12 | 69 | 5. Interpolation is permissible. Do not extrapolate.
12 | 70 | 6. Motor Efficiency: 85%.
12 | 71
12 | 72
12 | 73
12 | 74
12 | 75 | 12
13 | 1 | Performance data (cont)
13 | 2 | FAN PERFORMANCE — HORIZONTAL DISCHARGE UNITS
13 | 3 | 50TJS012 (10 TONS) STANDARD MOTOR (BELT DRIVE)*
13 | 4 | External Static Pressure (in. wg)
13 | 5 | Airflow
13 | 6 | 0.2 0.4 0.6 0.8 1.0 1.2
13 | 7 | (Cfm
13 | 8 | Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts
13 | 9 | 3000 532 0.64 630 605 0.81 763 670 0.97 891 725 1.12 1014 778 1.28 1148 825 1.43 1275
13 | 10 | 3100 544 0.70 677 616 0.86 803 680 1.03 940 735 1.20 1081 787 1.36 1216 835 1.52 1353
13 | 11 | 3200 557 0.75 716 628 0.93 859 690 1.10 998 746 1.28 1148 796 1.44 1284 844 1.61 1430
13 | 12 | 3300 570 0.81 763 639 0.99 907 700 1.18 1064 757 1.36 1216 805 1.52 1353 854 1.70 1508
13 | 13 | 3400 583 0.88 818 651 1.06 965 711 1.25 1123 767 1.44 1284 815 1.61 1430 863 1.79 1587
13 | 14 | 3500 596 0.94 867 663 1.14 1031 721 1.33 1190 777 1.52 1353 826 1.71 1517 871 1.88 1665
13 | 15 | 3600 609 1.01 924 674 1.22 1097 732 1.42 1267 787 1.61 1430 836 1.80 1595 880 1.98 1753
13 | 16 | 3700 622 1.09 989 686 1.30 1165 744 1.50 1335 797 1.70 1508 847 1.91 1691 890 2.09 1849
13 | 17 | 3800 635 1.16 1047 698 1.39 1241 755 1.59 1413 808 1.80 1595 857 2.01 1779 901 2.20 1945
13 | 18 | 3900 649 1.25 1123 713 1.48 1318 767 1.68 1491 818 1.90 1683 867 2.11 1866 912 2.32 2050
13 | 19 | 4000 662 1.33 1190 722 1.57 1396 778 1.78 1578 829 2.01 1779 878 2.22 1962 922 2.44 2203
13 | 20 | 4100 675 1.42 1267 734 1.67 1482 790 1.89 1674 839 2.12 1875 888 2.33 2058 933 2.56 2309
13 | 21 | 4200 689 1.52 1353 746 1.77 1569 801 1.99 1761 851 2.23 1971 898 2.45 2212 943 2.69 2424
13 | 22 | 4300 702 1.61 1430 759 1.88 1665 813 2.11 1866 862 2.34 2067 908 2.58 2326 953 2.81 2533
13 | 23 | 4400 715 1.72 1526 772 1.99 1761 825 2.22 1962 873 2.46 2221 919 2.71 2442 963 2.94 2651
13 | 24 | 4500 729 1.83 1621 785 2.10 1858 837 2.35 2076 885 2.59 2335 929 2.85 2569 973 3.08 2782
13 | 25 | 4600 742 1.94 1718 797 2.22 1962 848 2.48 2238 896 2.72 2451 940 2.98 2688 984 3.22 2914
13 | 26 | 4700 756 2.06 1823 810 2.34 2067 860 2.61 2353 908 2.86 2578 951 3.12 2727 994 3.38 3068
13 | 27 | 4800 770 2.18 1927 823 2.46 2221 872 2.75 2505 919 3.00 2707 963 3.27 2847 1003 3.43 3202
13 | 28 | 4900 783 2.31 2041 836 2.60 2344 884 2.89 2605 931 3.14 2838 974 3.41 2956 1013 3.59 3349
13 | 29 | 5000 797 2.44 2203 849 2.73 2460 897 3.04 2661 943 3.30 2870 984 3.44 3211 1023 3.75 3501
13 | 30
13 | 31
13 | 32 | 50TJS012 (10 TONS) STANDARD MOTOR (BELT DRIVE)* (cont)
13 | 33 | External Static Pressure (in. wg)
13 | 34 | Airflow
13 | 35 | 1.4 1.6 1.8 2.0
13 | 36 | (Cfm)
13 | 37 | Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts
13 | 38 | 3000 874 1.60 1422 926 1.82 1613 974 2.11 1920 1012 2.41 2134
13 | 39 | 3100 880 1.68 1491 933 1.87 1656 983 2.16 1963 1017 2.44 2177
13 | 40 | 3200 888 1.77 1569 934 1.94 1718 988 2.18 1980 1025 2.47 2230
13 | 41 | 3300 897 1.86 1648 940 2.03 1853 989 2.24 2031 1032 2.53 2282
13 | 42 | 3400 907 1.97 1744 947 2.14 1946 991 2.32 2099 1038 2.57 2318
13 | 43 | 3500 916 2.07 1831 956 2.25 2039 997 2.43 2195 1043 2.64 2380
13 | 44 | 3600 926 2.18 1927 966 2.41 2134 1004 2.54 2291 1045 2.74 2478
13 | 45 | 3700 934 2.28 2015 976 2.48 2238 1013 2.66 2397 1051 2.85 2569
13 | 46 | 3800 943 2.41 2160 985 2.60 2334 1023 2.79 2514 1059 2.98 2688
13 | 47 | 3900 952 2.51 2265 994 2.72 2451 1032 2.92 2633 1068 3.12 2819
13 | 48 | 4000 962 2.63 2371 1003 2.84 2560 1042 3.06 2763 1078 3.26 2952
13 | 49 | 4100 973 2.77 2496 1011 2.97 2679 1051 3.20 2895 1087 3.41 3097
13 | 50 | 4200 983 2.91 2624 1021 3.11 2810 1060 3.34 3029 1090 3.51 3276
13 | 51 | 4300 994 3.05 2754 1031 3.25 2943 1068 3.48 3166 1097 3.70 3453
13 | 52 | 4400 1004 3.19 2885 1042 3.41 3097 1080 3.63 3388 1105 3.91 3642
13 | 53 | 4500 1015 3.33 2020 1051 3.45 3218 1090 3.75 3493 1112 4.12 3843
13 | 54 | 4600 1025 3.48 3166 1060 3.61 3369 1100 3.92 3655 1119 4.35 4057
13 | 55 | 4700 1037 3.58 3335 1070 3.84 3325 1111 4.10 3822 1126 4.59 4284
13 | 56 | 4800 1048 3.75 3494 1080 3.95 3686 1121 4.28 3995 1133 4.85 4523
13 | 57 | 4900 1060 3.92 3659 1089 4.13 3854 1132 4.48 4174 1140 5.12 4775
13 | 58 | 5000 1072 4.11 3830 1099 4.32 4027 1144 4.67 4359 — — —
13 | 59 | LEGEND electrical testing on these units ensures that the full range of the
13 | 60 | Bhp — Brake Horsepower Input to Fan motor can be utilized with confidence. Using your fan motors up to
13 | 61 | FIOP — Factory-Installed Option the wattage ratings shown will not result in nuisance tripping or
13 | 62 | Watts — Input Watts to Motor premature motor failure. Unit warranty will not be affected.
13 | 63
13 | 64 | *Standard motor drive range: 685 to 935 rpm.
13 | 65 | 3. Values include losses for filters, unit casings, and wet coils.
13 | 66 | All other rpms require field-supplied drive. 4. Use of a field-supplied motor may affect wire sizing. Contact your
13 | 67 | NOTES: Carrier representative for details.
13 | 68 | 1. Boldface Out of Motor and Drive Package range. 5. Interpolation is permissible. Do not extrapolate.
13 | 69 | 2. Maximum usable watts input is 2120 with standard motor, 6. Motor Efficiency: 85%
13 | 70 | Maximum continuous bhp is 2.90 with standard motor.
13 | 71
13 | 72
13 | 73
13 | 74
13 | 75 | 13
14 | 1 | Performance data (cont)
14 | 2 | FAN PERFORMANCE — HORIZONTAL DISCHARGE UNITS
14 | 3 | 50TJS014 (121 /2 TONS) STANDARD MOTOR (BELT DRIVE)*
14 | 4 | External Static Pressure (in. wg)
14 | 5 | Airflow 0.2 0.4 0.6 0.8 1.0
14 | 6 | (Cfm)
14 | 7 | Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts
14 | 8 | 3700 607 0.97 947 670 1.18 1113 732 1.37 1267 782 1.56 1423 833 1.73 1565
14 | 9 | 3800 621 1.05 1010 681 1.25 1170 742 1.45 1332 795 1.66 1506 842 1.82 1641
14 | 10 | 3900 636 1.13 1073 693 1.32 1226 751 1.53 1398 808 1.76 1590 851 1.92 1725
14 | 11 | 4000 650 1.21 1137 705 1.40 1291 761 1.61 1464 819 1.86 1674 861 2.02 1811
14 | 12 | 4100 665 1.30 1210 717 1.48 1357 772 1.71 1548 830 1.96 1759 871 2.13 1905
14 | 13 | 4200 680 1.39 1283 728 1.57 1431 783 1.81 1632 839 2.05 1836 883 2.25 2009
14 | 14 | 4300 696 1.49 1365 739 1.66 1506 794 1.91 1717 848 2.14 1914 896 2.38 2123
14 | 15 | 4400 711 1.60 1456 750 1.75 1582 805 2.02 1811 857 2.24 2000 908 2.51 2237
14 | 16 | 4500 727 1.70 1540 762 1.85 1666 817 2.12 1897 867 2.35 2096 919 2.63 2343
14 | 17 | 4600 742 1.82 1641 774 1.96 1759 828 2.23 1992 877 2.46 2193 929 2.75 2450
14 | 18 | 4700 758 1.94 1742 786 2.07 1854 840 2.34 2088 888 2.59 2307 938 2.87 2557
14 | 19 | 4800 773 2.06 1845 799 2.18 1948 852 2.46 2193 899 2.72 2423 947 2.98 2656
14 | 20 | 4900 789 2.19 1957 812 2.30 2053 863 2.57 2290 910 2.86 2548 957 3.11 2773
14 | 21 | 5000 805 2.32 2070 826 2.43 2166 875 2.70 2405 921 2.99 2665 966 3.24 2891
14 | 22 | 5100 821 2.47 2202 840 2.57 2290 887 2.83 2521 932 3.13 2792 976 3.38 3019
14 | 23 | 5200 837 2.61 2325 854 2.71 2414 898 2.96 2638 943 3.28 2928 987 3.53 3157
14 | 24 | 5300 853 2.76 2459 868 2.85 2539 909 3.09 2755 955 3.42 3056 998 3.69 3304
14 | 25 | 5400 869 2.92 2602 882 3.01 2683 920 3.24 2891 967 3.57 3193 1009 3.86 3461
14 | 26 | 5500 885 3.09 2755 897 3.17 2828 932 3.38 3019 978 3.72 3331 1029 4.03 3618
14 | 27 | 5600 901 3.26 2910 911 3.33 2973 943 3.54 3166 990 3.87 3470 1031 4.20 3775
14 | 28 | 5700 917 3.44 3074 926 3.50 3129 956 3.70 3313 1002 4.03 3618 1042 4.38 3943
14 | 29 | 5800 933 3.62 3239 941 3.68 3294 968 3.87 3470 1013 4.20 3775 1053 4.56 4111
14 | 30 | 5900 949 3.81 3414 956 3.87 3470 981 4.05 3637 1025 4.37 3934 1065 4.74 4279
14 | 31 | 6000 965 4.01 3600 972 4.06 3646 995 4.23 3804 1037 4.55 4102 1076 4.92 4447
14 | 32 | 6100 981 4.21 3785 987 4.26 3832 1008 4.42 3981 1042 4.73 4270 1088 5.10 4614
14 | 33 | 6200 997 4.42 3981 1002 4.46 4018 1022 4.62 4167 1058 4.91 4437 — — —
14 | 34 | 6300 1014 4.64 4186 1018 4.68 4223 1036 4.83 4363 1070 5.11 4624 — — —
14 | 35
14 | 36
14 | 37 | 50TJS014 (121 /2 TONS) STANDARD MOTOR (BELT DRIVE)* (cont)
14 | 38 | External Static Pressure (in. wg)
14 | 39 | Airflow 1.2 1.4 1.6 1.8 2.0
14 | 40 | (Cfm)
14 | 41 | Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts
14 | 42 | 3700 879 1.95 1751 927 2.17 1940 973 2.38 2123 1013 2.57 2290 1046 2.73 2432
14 | 43 | 3800 889 2.03 1819 934 2.26 2018 980 2.48 2210 1022 2.69 2396 1058 2.87 2557
14 | 44 | 3900 898 2.12 1897 942 2.36 2105 987 2.59 2307 1030 2.81 2503 1068 3.01 2683
14 | 45 | 4000 908 2.21 1974 950 2.46 2193 994 2.70 2405 1037 2.92 2602 1077 3.14 2801
14 | 46 | 4100 917 2.32 2070 960 2.55 2272 1001 2.81 2503 1045 3.04 2710 1085 3.21 2919
14 | 47 | 4200 925 2.44 2175 969 2.65 2370 1009 2.92 2602 1051 3.17 2828 1092 3.40 3037
14 | 48 | 4300 935 2.56 2281 979 2.77 2468 1018 3.03 2701 1058 3.29 2937 1100 3.53 3157
14 | 49 | 4400 945 2.68 2387 988 2.89 2575 1028 3.14 2801 1066 3.41 3047 1106 3.67 3285
14 | 50 | 4500 955 2.82 2512 996 3.02 2692 1037 3.25 2901 1074 3.54 3166 1113 3.81 3414
14 | 51 | 4600 967 2.96 2638 1005 3.16 2819 1046 3.38 3019 1084 3.66 3276 1121 3.95 3544
14 | 52 | 4700 980 3.11 2773 1015 3.30 2946 1056 3.52 3147 1093 3.79 3396 1129 4.09 3674
14 | 53 | 4800 992 3.26 2910 1025 3.45 3083 1064 3.67 3285 1103 3.92 3516 1137 4.22 3795
14 | 54 | 4900 1003 3.41 3047 1036 3.61 3230 1073 3.83 3433 1112 4.07 3655 1147 4.36 3925
14 | 55 | 5000 1014 3.56 3184 1049 3.79 3396 1083 4.00 3590 1121 4.23 3804 1157 4.50 4055
14 | 56 | 5100 1024 3.71 3322 1061 3.96 3553 1093 4.17 3748 1129 4.40 3962 1166 4.66 4202
14 | 57 | 5200 1033 3.84 3442 1073 4.14 3720 1103 4.34 3906 1138 4.58 4130 1175 4.82 4354
14 | 58 | 5300 1042 3.98 3572 1084 4.31 3878 1115 4.53 4157 1148 4.76 4326 1184 5.01 4531
14 | 59 | 5400 1051 4.14 3720 1095 4.49 4046 1128 4.74 4279 1158 4.95 4475 1193 5.20 4707
14 | 60 | 5500 1061 4.30 3818 1105 4.66 4204 1140 4.94 4465 1168 5.15 4661 — — —
14 | 61 | 5600 1071 4.46 4018 1114 4.81 4344 1152 5.14 4652 — — — — — —
14 | 62 | 5700 1081 4.64 4186 1123 4.98 4503 — — — — — — — — —
14 | 63 | 5800 1092 4.84 4372 1132 5.15 4661 — — — — — — — — —
14 | 64 | 5900 1103 5.04 4558 — — — — — — — — — — — —
14 | 65 | 6000 1114 5.24 4745 — — — — — — — — — — — —
14 | 66 | 6100 — — — — — — — — — — — — — — —
14 | 67 | 6200 — — — — — — — — — — — — — — —
14 | 68 | 6300 — — — — — — — — — — — — — — —
14 | 69 | LEGEND 2. Maximum usable watts input is 3313 with standard motor.
14 | 70 | Bhp — Brake Horsepower Input to Fan Maximum continuous bhp is 3.70 with standard motor.
14 | 71 | FIOP — Factory-Installed Option Extensive motor and electrical testing on these units ensures that the full
14 | 72 | Watts — Input Watts to Motor range of the motor can be utilized with confidence.
14 | 73 | Using your fan motors up to the wattage ratings shown will not result
14 | 74 | *Standard motor drive range: 860 to 1080 rpm. Alternate motor drive range: in nuisance tripping or premature motor failure. Unit warranty
14 | 75 | 900 to 1260 rpm. All other rpms require field-supplied drive. will not be affected.
14 | 76 | 3. Values include losses for filters, unit casing, and wet coils.
14 | 77 | NOTES:
14 | 78 | 1. Boldface Out of Drive Package or Motor range . 4. Use of a field-supplied motor may affect wire sizing. Contact your Carrier
14 | 79 | representative for details.
14 | 80
14 | 81 | 5. Interpolation is permissible. Do not extrapolate.
14 | 82 | 6. Motor Efficiency: 85%
14 | 83 | 14
15 | 1 | FAN RPM AT MOTOR PULLEY SETTINGS*— 50 Hz
15 | 2 | MOTOR PULLEY TURNS OPEN
15 | 3 | UNIT
15 | 4 | 0 1/2 1 1 1/2 2 2 1/2 3 3 1/2 4 4 1/2 5
15 | 5 | 50LJS007 1205 1180 1150 1125 1095 1070 1040 1015 985 960 930
15 | 6 | 50TJS008 880 855 830 800 775 750 725 700 675 650 620
15 | 7 | 50TJS009 880 855 830 800 775 750 725 700 675 650 620
15 | 8 | 50TJS012 900 875 855 835 815 795 775 755 735 715 690
15 | 9 | 50TJS014 1017 992 972 952 932 912 892 872 852 832 814
15 | 10 | * Approximate fan RPM shown
15 | 11
15 | 12 | OUTDOORS SOUND POWER
15 | 13 | SOUND OCTAVE BANDS
15 | 14 | UNIT RATING
15 | 15 | (Bels)
15 | 16 | 63 125 250 500 1000 2000 4000 8000
15 | 17 | 50LJS007 8.2 78.5 84 77.5 73 70.5 72 65 58.5
15 | 18 | 50TJS008,009 8.6 83.2 87.4 83.5 82.8 83 77.7 71.8 67
15 | 19 | 50TJS012 8.8 97.6 90.4 85.7 84.8 83.9 77.5 71.3 65.8
15 | 20 | 50TJS014 8.8 83.7 87.2 83.4 82.8 83 77.7 71.8 67
15 | 21
15 | 22
15 | 23
15 | 24 | DURABLADE ECONOMIZER BAROMETRIC RELIEF
15 | 25 | DAMPER CHARACTERISTICS
15 | 26
15 | 27
15 | 28
15 | 29
15 | 30 | 15
16 | 1 | Electrical Data – 50LJS007, 50TJS008 – 014 ( 50 Hz )
16 | 2 | VOLTAGE COMPRESSOR DISCONNECT
16 | 3 | UNIT NOMINAL IFM OFM (ea) IFM ELECTRIC HEAT* POWER SUPPLY
16 | 4 | RANGE (ea) SIZE
16 | 5 | MODEL V-Ph-Hz TYPE
16 | 6 | MIN MAX RLA LRA Qty Hp FLA FLA NOMINAL KW** FLA MCA MOCP FLA LRA
16 | 7 | - - 19.1 25 --
16 | 8 | 4.2 6.1 19.1 25 --
16 | 9 | 50LJS 8 11.5 19.2 25 --
16 | 10 | 400-3-50 STD 342 440 12 100 1 1/3 1.5 2.6 --
16 | 11 | 007 9.7 14 23 25 --
16 | 12 | 16 23.2 35 30 --
16 | 13 | 17.7 25.6 37.5 40 --
16 | 14 | - - 18.8 20 19
16 | 15 | 9.7 13.9 21.7 20 19
16 | 16 | 50TJS 11.5 16.5 24.9 25 22
16 | 17 | 400-3-50 STD 342 440 6.6 53 2 1/2 1.8 3.4 130
16 | 18 | 008 19.3 27.8 39.1 40 35
16 | 19 | 22.9 33.1 45.6 45 41
16 | 20 | 29 41.8 56.5 60 51
16 | 21 | - - 21.5 25 21
16 | 22 | 9.7 13.9 21.7 25 21
16 | 23 | 50TJS 11.5 16.5 24.9 25 22
16 | 24 | 400-3-50 STD 342 440 7.5 62 2 1/2 1.8 3.4 147
16 | 25 | 009 19.3 27.8 39.1 40 35
16 | 26 | 22.9 33.1 45.6 45 41
16 | 27 | 29 41.8 56.5 60 51
16 | 28 | - - 23.2 30 24
16 | 29 | 9.7 16.5 23.9 30 24
16 | 30 | 50TJS 19.3 27.8 38.1 40 35
16 | 31 | 400-3-50 STD 342 440 9 82 2 1/2 1.8 3.4 158
16 | 32 | 012 22.9 33.1 44.6 45 41
16 | 33 | 29 41.8 55.5 60 51
16 | 34 | 34.7 50.1 65.9 70 61
16 | 35 | - - 33.3 40 35
16 | 36 | 11.5 18 33.3 40 35
16 | 37 | 50TJS 19.3 30.3 43.9 45 40
16 | 38 | 400-3-50 STD 342 440 12 100 2 1/2 1.8 4.8 232
16 | 39 | 014 22.9 36.1 51.1 60 47
16 | 40 | 29 45.5 62.8 70 58
16 | 41 | 34.7 54.6 74.2 80 68
16 | 42
16 | 43 | LEGEND AND NOTES FOR ELECTRICAL DATA TABLES
16 | 44 | LEGEND Example: Supply voltage is 460-3-60.
16 | 45 | FLA — Full Load Amps
16 | 46 | HACR — Heating, Air Conditioning and Refrigeration AB = 452 v
16 | 47 | IFM — Indoor (Evaporator) Fan Motor BC = 464 v
16 | 48 | LRA — Locked Rotor Amps AC = 455 v
16 | 49 | MCA — Minimum Circuit Amps 452 + 464 + 455
16 | 50 | MOCP— Maximum Overcurrent Protection Average Voltage =
16 | 51 | 3
16 | 52 | NEC — National Electrical Code
16 | 53 | OFM — Outdoor (Condenser) Fan Motor 1371
16 | 54 | RLA — Rated Load Amps =
16 | 55 | 3
16 | 56 | *Heater capacity (kW) is based on heater voltage of 208 v, 240 v, = 457
16 | 57 | 480 v, and 600 v. Heaters are rated at 240 v, 480 v, or 600 v. If power Determine maximum deviation from average voltage.
16 | 58 | distribution voltage to unit varies from rated heater voltage, heater kW (AB) 457 – 452 = 5 v
16 | 59 | will vary accordingly. To determine heater capacity at actual unit volt- (BC) 464 – 457 = 7 v
16 | 60 | age, multiply 240 v, 480 v, or 600 v capacity by multipliers found in (AC) 457 – 455 = 2 v
16 | 61 | table on page 51.
16 | 62 | † Used to determine minimum disconnect size per NEC. Maximum deviation is 7 v.
16 | 63 | **Heaters are field installed only.
16 | 64 | †† Fuse or HACR circuit breaker. Determine percent of voltage imbalance.
16 | 65 | ¦¦Fusing in single point box provides the required branch circuit 7
16 | 66 | protection. % Voltage Imbalance = 100 x
16 | 67 | 457
16 | 68 | NOTES: = 1.53%
16 | 69 | 1. In compliance with NEC requirements for multimotor and combina- This amount of phase imbalance is satisfactory as it is below the
16 | 70 | tion load equipment (refer to NEC Articles 430 and 440), the overcur- maximum allowable 2%.
16 | 71 | rent protective device for the unit shall be fuse or HACR breaker. The
16 | 72 | Canadian units may be fuse or circuit breaker. IMPORTANT: If the supply voltage phase imbalance is more than 2%,
16 | 73 | 2. Unbalanced 3-Phase Supply Voltage contact your local electric utility company immediately.
16 | 74 | Never operate a motor where a phase imbalance in supply voltage is
16 | 75 | greater than 2%. Use the following formula to determine the percent
16 | 76 | of voltage imbalance.
16 | 77 | % Voltage Imbalance
16 | 78 | max voltage deviation from average voltage
16 | 79 | = 100 x
16 | 80 | average voltage
16 | 81
16 | 82
16 | 83
16 | 84
16 | 85 | 16
17 | 1 | Typical piping and wiring — 50LJS007
17 | 2 | (50TJS 008-014 shown)
17 | 3 | VERTICAL DISCHARGE DUCTING
17 | 4
17 | 5
17 | 6
17 | 7
17 | 8 | HORIZONTAL DISCHARGE DUCTING
17 | 9
17 | 10
17 | 11
17 | 12
17 | 13 | LEGEND
17 | 14 | NEC — National Electrical Code
17 | 15
17 | 16
17 | 17
17 | 18
17 | 19 | 17
18 | 1 | Typical wiring schematic — 50LJS007
18 | 2
18 | 3
18 | 4
18 | 5
18 | 6 | 18
19 | 1 | Typical wiring schematic — 50LJS007 (Cont.)
19 | 2
19 | 3
19 | 4
19 | 5
19 | 6 | 19
20 | 1 | Typical wiring schematic — 50LJS007 (Cont.)
20 | 2
20 | 3
20 | 4
20 | 5
20 | 6 | 20
21 | 1 | Typical wiring schematic — 50TJS008-014
21 | 2
21 | 3
21 | 4
21 | 5
21 | 6 | 21
22 | 1 | Typical wiring schematic — 50TJS008-014 (Cont.)
22 | 2
22 | 3
22 | 4
22 | 5
22 | 6 | 22
23 | 1 | Typical wiring schematic — 50TJS008-014 (Cont.)
23 | 2
23 | 3
23 | 4
23 | 5
23 | 6 | 23
24 | 1 | Controls
24 | 2 | the minimum position. If the supply air
24 | 3 | temperature is above 57 F, the damper
24 | 4 | continues to open until it reaches the fully
24 | 5 | Operating sequence open position or until the supply-air
24 | 6 | Cooling, units without economizer temperature drops below 57 F.
24 | 7 | -
24 | 8 | When thermostat calls for cooling, terminal When the supply-air temperature falls to
24 | 9 | G and Y1 are energized. The indoor between 57 F and 52 F, the damper will
24 | 10 | (evaporator) fan contactor (IFC), and remain at an intermediate open position. If
24 | 11 | compressor contactor no 1 (C1) are the supply –air temperature falls below 52
24 | 12 | energized and evaporator-fan motor, F, the damper will modulate closed until it
24 | 13 | compressor no. 1 (50TJS008-014), and reaches the minimum position or until the
24 | 14 | condenser fans start. The condenser-fan supply-air temperature is above 52 F. when
24 | 15 | motor runs continuously while unit is cooling. the thermostat is satisfied, the damper will
24 | 16 | On 50TJS008 – 014 units, if the thermostat move to the fully closed position.
24 | 17 | calls for a secondary stage of cooling by
24 | 18 | energizing Y2, compressor contactor no.2 If the outdoor air alone can not satisfy the
24 | 19 | (C2) is energized and compressor no. 2 cooling requirements of the conditioned
24 | 20 | starts. space, economizer cooling is integrated with
24 | 21 | mechanical cooling, providing second-stage
24 | 22 | Heating, units without economizer cooling. Compressor no. 1 and the
24 | 23 | (If Accessory or Optional Heater is condenser fan will be energized and the
24 | 24 | position of the economizer damper will be
24 | 25 | Installed) - determined by the supply-air temperature.
24 | 26 | Upon a call for heating through terminal W1, Compressor no. 2 (50TJS008 – 014) is
24 | 27 | IFC and heater contactor no. 1 (HC1) are locked out.
24 | 28 | energized. On units equipped for 2 stages of
24 | 29 | heat, when additional heat is needed, HC2 When the second stage of cooling is
24 | 30 | is energized through W2. satisfied, the compressor and condenser-fan
24 | 31 | motor will be deenergized. The damper
24 | 32 | Cooling, units with economizer position will be determined by the supply-air
24 | 33 | (50LJ007, 50TJS008 – 014) – temperature.
24 | 34 | When the outdoor-air temperature is above
24 | 35 | the outdoor-air thermostat (OAT) setting and When the first stage of cooling is satisfied,
24 | 36 | the room thermostat calls for cooling, the damper will move to fully closed position.
24 | 37 | compressor contactor no.1 is energized to
24 | 38 | start compressor no. 1and the condenser- Heating, units with economizer
24 | 39 | fan motor. The evaporator-fan motor is (50LJ007,50TJS008-014) (If Acces-
24 | 40 | energized and the economizer damper
24 | 41 | moves to the minimum position. Upon a sory or Optional Heater is Installed) -
24 | 42 | further call for cooling, compressor contactor When the room thermostat calls for heat
24 | 43 | no. 2 will be energized (50TJS008 – 014), through terminal W1, the evaporator-fan
24 | 44 | starting compressor no. 2. After the contactor and heater contactor no. 1are
24 | 45 | thermostat is satisfied, the damper moves to energized. On units equipped with 2 stages
24 | 46 | the fully closed position. of heat, when additional heat is needed,
24 | 47 | heater contactor no. 2 is energized through
24 | 48 | When the outdoor-air temperature is below W2. The economizer damper moves to the
24 | 49 | the OAT setting and the thermostats call for minimum position during heating. When the
24 | 50 | cooling, the economizer damper moves to thermostat is satisfied, the damper moves to
24 | 51 | the fully closed position.
24 | 52
24 | 53
24 | 54
24 | 55
24 | 56 | 24
25 | 1 | and forklift slots shall be provided to facilitate
25 | 2 | Guide specifications maneuvering.
25 | 3 | Packaged Rooftop Cooling Unit 5. Unit shall have a factory-installed, sloped
25 | 4 | condensate drain pan made of a noncorrosive
25 | 5 | with Electric plastic material, providing a minimum 3/4-in.
25 | 6 | Heat Option — Constant Volume connection with both vertical and horizontal
25 | 7 | Application drains and shall comply with ASHRAE 62.
25 | 8 | HVAC Guide Specifications 6. Unit shall have factory-installed filter access
25 | 9 | Carrier Model: 50LJS007/TJS008 - 014 panel to provide filter access with tool-less
25 | 10 | Part 1 — General removal.
25 | 11 | 1.01 SYSTEM DESCRIPTION
25 | 12 | Outdoor rooftop- or slab-mounted, electrically C. Fans:
25 | 13 | controlled cooling unit with optional heat utilizing 1. Indoor blower (evaporator fan) shall be of the
25 | 14 | a hermetic compressor for cooling duty and belt-driven, double inlet, forward curved,
25 | 15 | electric resistance coils for heating duty. Unit centrifugal type. Belt drive shall include an
25 | 16 | shall discharge supply air vertically or adjustable-pitch motor pulley.
25 | 17 | horizontally as shown on contract drawings, 2. Indoor blower (evaporator fan) shall be made
25 | 18 | Vertical discharge is a factory option Unit shall from steel with a corrosion-resistant finish and
25 | 19 | have Fixes Orifice for refrigerant control. shall be dynamically balanced.
25 | 20 | 3. Bearings shall be of the sealed, permanently
25 | 21 | 1.02 QUALITY ASSURANCE lubricated, ball-bearing type for longer life and
25 | 22 | A. Insulation and adhesive shall meet NFPA lower maintenance.
25 | 23 | 90A requirements for flame spread and smoke 4. Condenser fan shall be of the direct-driven
25 | 24 | generation. propeller type and shall discharge air vertically.
25 | 25 | B. Unit casing shall be capable of withstanding 5. Condenser fan shall have aluminum blades
25 | 26 | 500-hour salt spray exposure per ASTM B117 riveted to corrosion-resistant steel spiders and
25 | 27 | (scribed specimen). shall be dynamically balanced.
25 | 28 | C. Unit shall be manufactured in a facility
25 | 29 | registered to ISO 9001:2000. D. Compressor(s):
25 | 30 | 1. Reciprocating or scroll type, fully hermetic
25 | 31 | type, internally protected.
25 | 32 | 1.03 DELIVERY, STORAGE, AND HANDLING 2. Factory mounted on rubber grommets and
25 | 33 | Unit(s) shall be stored and handled as per internally spring mounted for vibration isolation.
25 | 34 | manufacturer’s recommendations. 3. Two independent circuits (TJ 008-014).
25 | 35
25 | 36 | Part 2 — Products E. Coils:
25 | 37 | 2.01 EQUIPMENT (STANDARD) 1. Condenser coils shall have aluminum plate
25 | 38 | A. General: fins mechanically bonded to enhanced copper
25 | 39 | Factory-assembled, single-piece cooling unit tubes with all joints brazed.
25 | 40 | with optional heat. Contained within the unit 2. Tube sheet openings shall be belled to
25 | 41 | enclosure shall be all factory wiring, piping, prevent tube wear.
25 | 42 | controls, refrigerant charge (R-22), and special 3. Evaporator coil shall be of the full face active
25 | 43 | features required prior to field startup. design.
25 | 44 | 4. Condenser coils shall be protected by a wire
25 | 45 | B. Unit Cabinet: grill.
25 | 46 | 1. Unit cabinet shall be constructed of
25 | 47 | galvanized steel, shall be bonderized and F. Refrigerant Components:
25 | 48 | coated with a baked enamel finish on all Refrigerant circuit components shall include:
25 | 49 | externally exposed surfaces. 1. Fixed Expansion Orifices.
25 | 50 | 2. Evaporator fan cabinet interior shall be 2. Refrigerant filter.
25 | 51 | insulated with a minimum 1/2-in. thick, 1-lb 3. Service gage connections on suction,
25 | 52 | density Aluminum faced, flexible fiberglass discharge, and liquid line.
25 | 53 | insulation.
25 | 54 | 3. Cabinet panels shall be easily removable for G. Filter Section:
25 | 55 | servicing. 1. Standard filter section shall consist of factory
25 | 56 | 4. Holes shall be provided in the base rails for installed low-velocity, throwaway 2-in.
25 | 57 | rigging shackles to facilitate overhead rigging,
25 | 58
25 | 59
25 | 60
25 | 61
25 | 62 | 25
26 | 1 | thick fiberglass filters of commercially 3. Optional crankcase heater should be
26 | 2 | available sizes. installed where temperature falls below 450F
26 | 3 | 2. Filter face velocity shall not exceed 320 and cooling operation is required.
26 | 4 | fpm at nominal airflows.
26 | 5 | 3. Filter section shall use only one size filter. J. Electrical Requirements:
26 | 6 | 4. Filters shall be accessible through an All unit power wiring shall enter unit cabinet
26 | 7 | access panel with “no-tool” removal. at a single factory-predrilled location.
26 | 8
26 | 9 | H. Controls and Safeties: K. Motors:
26 | 10 | 1. Unit Controls: 1. Compressor motors shall be cooled by
26 | 11 | Unit shall be complete with self-contained low refrigerant passing through motor windings
26 | 12 | voltage control circuit. and shall have line break thermal and current
26 | 13 | 2. Standard Safeties: overload protection.
26 | 14 | a. Unit shall incorporate compressor over 2. Indoor blower (evaporator fan) motor shall
26 | 15 | temperature and over current safety devices have permanently lubricated bearings and
26 | 16 | to shut off compressor. inherent automatic-reset thermal overload
26 | 17 | b. Contain high pressure as well as loss of protection.
26 | 18 | charge/low pressure and freeze protection 3. Totally enclosed condenser-fan motor
26 | 19 | switches. shall\ have permanently lubricated bearings,
26 | 20 | c. For models with Scroll compressors, unit and inherent automatic-reset thermal
26 | 21 | shall have phase monitor to prevent reverse overload protection.
26 | 22 | rotation. 4. (50TJS008-014): High-static motor(s) and
26 | 23 | d. Compressor Cycle Delay: drive(s) shall be factory- installed to provide
26 | 24 | Unit shall be prevented from restarting for a an additional performance range.
26 | 25 | minimum of 5 minutes after shutdown. 5. Outdoor motor shall have F – Class
26 | 26 | Insulation.
26 | 27 | I. Operating Characteristics:
26 | 28 | 1. Unit shall be capable of starting and L. Special Options:
26 | 29 | running at 125 F ambient outdoor 1. Condenser coil shall pre-coated aluminum-
26 | 30 | temperature, meeting maximum load criteria fin coils shall have a durable epoxy-phenolic
26 | 31 | of ARI Standard 210/ 240 or 360 at ±10% coating to provide protection in mildly
26 | 32 | voltage. corrosive coastal environments. Coating shall
26 | 33 | 2. Compressor with standard controls shall be applied to the aluminum fin stock prior to
26 | 34 | be capable of operation down to 40 F the fin stamping process to create an inert
26 | 35 | ambient outdoor temperature. barrier between the aluminum fin and copper
26 | 36 | tube. Epoxy-phenolic barrier shall minimize
26 | 37 | galvanic action between dissimilar metals.
26 | 38
26 | 39
26 | 40
26 | 41
26 | 42 | 26
27 | 1 | Manufacturer reserves the right to discontinue, or change at any time, specifications or designs without notice and without incurring obligations
27 | 2
27 | 3
27 | 4 | Jan 2005 Carrier Corporation • Syracuse, NY 13221 Form: 50TJS- 02PD -50HZ C

## Airflow_Summary
Model | Nominal tons | Nominal airflow CFM | Nominal airflow L/s | Input watts at nominal airflow | Evaporator motor | Max continuous bhp | Motor pulley pitch dia in | Fan pulley pitch dia in | Motor efficiency | Evaporator coil rows | Notes
50LJS007 | 6 | 2200 | 1038 | 800 | 1.5 hp x 1425 rpm | 2.4 | 4.4 | 5.19 | 81% | 4 | Horizontal discharge; standard motor belt drive
50TJS008 | 7 | 2800 | 1321 | 900 | 1.5 hp x 1425 rpm | 2.4 | 3.4 | 5.5 | 85% | 3 | Horizontal discharge; standard motor belt drive
50TJS009 | 9 | 3000 | 1416 | 1000 | 1.5 hp x 1425 rpm | 2.4 | 3.4 | 5.5 | 85% | 3 | Horizontal discharge; standard motor belt drive
50TJS012 | 10 | 4000 | 1887 | 1500 | 2 hp x 1425 rpm | 2.9 | 4.4 | 7 | 85% | 3 | Horizontal discharge; standard motor belt drive
50TJS014 | 12 | 4750 | 2242 | 2000 | 3 hp x 1425 rpm | 3.7 | 5 | 7 | 85% | 4 | Horizontal discharge; standard motor belt drive

## Blower_Performance_Raw
PDF page | Page line | Extracted blower-performance text
10 | 1 | Performance data (cont)
10 | 2 | FAN PERFORMANCE — HORIZONTAL DISCHARGE UNITS
10 | 3 | 50LJS007 (6 TONS) — STANDARD MOTOR (BELT DRIVE)*
10 | 4 | External Static Pressure (in. wg)
10 | 5 | Airflow
10 | 6 | 0.1 0.2 0.4 0.6 0.8
10 | 7 | (Cfm)
10 | 8 | Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts
10 | 9 | 1800 765 0.45 487 821 0.51 532 923 0.65 638 1019 0.81 843 1099 0.96 883
10 | 10 | 1900 802 0.45 539 854 0.58 585 953 0.73 700 1046 0.90 835 1126 1.06 965
10 | 11 | 2000 840 0.60 600 888 0.66 646 984 0.82 771 1073 0.99 907 1154 1.16 1047
10 | 12 | 2100 878 0.69 669 923 0.75 716 1015 0.91 843 1101 1.08 981 1182 1.27 1140
10 | 13 | 2200 916 0.78 739 958 0.85 795 1046 1.01 924 1129 1.19 1072 1209 1.39 1241
10 | 14 | 2300 954 0.89 827 993 0.96 883 1079 1.13 1022 1160 1.31 1173 1237 1.51 1344
10 | 15 | 2400 993 1.00 916 1029 1.07 973 1112 1.25 1123 1190 1.43 1275 1264 1.63 1447
10 | 16 | 2500 1031 1.13 1022 1066 1.20 1081 1145 1.39 1241 1220 1.57 1396 1292 1.77 1569
10 | 17 | 2600 1070 1.26 1131 1103 1.34 1199 1179 1.52 1353 1251 1.71 1517 1322 1.92 1700
10 | 18 | 2700 1109 1.41 1258 1140 1.48 1318 1212 1.67 1482 1283 1.87 1656 1352 2.09 1849
10 | 19 | 2800 1148 1.57 1396 1177 1.64 1456 1246 1.83 1621 1316 2.04 1805 1383 2.26 1997
10 | 20 | 2900 1188 1.74 1543 1215 1.81 1604 1281 2.00 1770 1349 2.22 1962 1413 2.44 2154
10 | 21 | 3000 1227 1.92 1700 1253 2.00 1770 1316 2.19 1936 1382 2.42 2136 1444 2.63 2317
10 | 24 | 50LJS007 (6 TONS) — STANDARD MOTOR (BELT DRIVE)* (cont)
10 | 25 | External Static Pressure (in. wg)
10 | 26 | Airflow 1.0 1.2 1.4 1.6
10 | 27 | (Cfm)
10 | 28 | Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts
10 | 29 | 1800 1178 1.14 1031 1249 1.32 1182 1316 1.52 1353 1382 1.72 1526
10 | 30 | 1900 1201 1.23 1106 1274 1.43 1275 1338 1.62 1439 1402 1.83 1621
10 | 31 | 2000 1226 1.33 1990 1297 1.53 1361 1363 1.73 1534 1424 1.94 1718
10 | 32 | 2100 1252 1.45 1292 1320 1.64 1456 1388 1.85 1639 1448 2.07 1831
10 | 33 | 2200 1280 1.58 1404 1345 1.77 1569 1410 1.97 1744 1473 2.20 1945
10 | 34 | 2300 1309 1.71 1517 1372 1.91 1691 1434 2.11 1866 1496 2.34 2067
10 | 35 | 2400 1336 1.85 1639 1400 2.06 1823 1459 2.26 1997 1519 2.48 2188
10 | 36 | 2500 1363 2.00 1770 1428 2.22 1962 1486 2.43 2145 1543 2.65 2335
10 | 37 | 2600 1390 2.15 1901 1456 2.38 2102 1514 2.61 2300 1569 2.83 2487
10 | 38 | 2700 1418 2.31 2041 1483 2.56 2257 1543 2.80 2462 — — —
10 | 39 | 2800 1446 2.48 2188 1510 2.73 2403 — — — — — —
10 | 40 | 2900 1476 2.67 2352 1537 2.92 2562 — — — — — —
10 | 41 | 3000 1506 2.88 2529 — — — — — — — — —
10 | 42 | LEGEND 2. Maximum usable watts input is 2120 and maximum continuous bhp
10 | 43 | Bhp — Brake Horsepower Input to Fan is 2.40. Extensive motor and electrical testing on these units
10 | 44 | FIOP — Factory-Installed Option ensures that the full range of the motor can be utilized with confi-
10 | 45 | Watts — Input Watts to Motor dence. Using your fan motors up to the wattage ratings shown will
10 | 46 | not result in nuisance tripping or premature motor failure. Unit war-
10 | 47 | *Motor drive range: 1070 to 1460 rpm. All other rpms require field- ranty will not be affected.
10 | 48 | supplied drive.
10 | 49 | NOTES:
10 | 50 | 3. Values include losses for filters, unit casing, and wet coils.
10 | 51 | 1. Boldface Out of Drive Package or Motor range .
10 | 52 | 4. Use of a field-supplied motor may affect wire sizing. Contact your
10 | 53 | Carrier representative for details.
10 | 54 | 5. Interpolation is permissible. Do not extrapolate.
10 | 55 | 6. Motor Efficiency: 81%.
10 | 60 | 10
11 | 1 | Performance data (cont)
11 | 2 | FAN PERFORMANCE — HORIZONTAL DISCHARGE UNITS
11 | 3 | 50TJS008 (712/TONS) — STANDARD MOTOR (BELT DRIVE)*
11 | 4 | External Static Pressure (in. wg)
11 | 5 | Airflow
11 | 6 | 0.2 0.4 0.6 0.8 1.0
11 | 7 | (Cfm)
11 | 8 | Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts
11 | 9 | 2250 465 0.43 473 554 0.64 630 630 0.86 803 695 1.09 989 757 1.34 1199
11 | 10 | 2300 471 0.45 487 559 0.66 646 635 0.89 827 699 1.12 1014 760 1.37 1224
11 | 11 | 2400 482 0.50 524 569 0.71 684 645 0.95 875 708 1.18 1064 768 1.44 1284
11 | 12 | 2500 494 0.54 554 581 0.76 723 654 1.01 924 717 1.25 1123 776 1.51 1344
11 | 13 | 2550 501 0.57 577 587 0.79 747 659 1.05 956 722 1.29 1156 780 1.55 1378
11 | 14 | 2660 507 0.59 592 592 0.82 771 663 1.08 981 727 1.32 1182 784 1.58 1404
11 | 15 | 2700 520 0.65 638 604 0.89 827 672 1.14 1031 737 1.40 1250 793 1.66 1473
11 | 16 | 2800 533 0.71 684 615 0.95 875 683 1.20 1081 747 1.49 1327 802 1.75 1552
11 | 17 | 2900 546 0.77 731 626 1.02 932 693 1.27 1140 756 1.57 1396 813 1.84 1630
11 | 18 | 3000 559 0.83 779 637 1.09 989 704 1.35 1207 765 1.66 1473 823 1.94 1718
11 | 19 | 3100 572 0.90 835 648 1.17 1056 715 1.43 1275 775 1.74 1543 832 2.05 1814
11 | 20 | 3200 585 0.96 883 660 1.24 1114 727 1.52 1353 785 1.83 1627 841 2.15 1901
11 | 21 | 3300 598 1.03 940 671 1.32 1182 739 1.62 1439 795 1.91 1691 851 2.26 1997
11 | 22 | 3400 610 1.10 998 682 1.41 1258 750 1.72 1526 806 2.01 1779 860 2.36 2084
11 | 23 | 3500 623 1.17 1056 694 1.50 1335 761 1.82 1613 817 2.11 1866 870 2.47 2180
11 | 24 | 3600 636 1.25 1123 707 1.60 1422 772 1.93 1709 828 2.23 1971 880 2.57 2266
11 | 25 | 3700 649 1.33 1190 720 1.71 1517 783 2.03 1796 840 2.35 2076 890 2.69 2369
11 | 26 | 3750 655 1.37 1224 727 1.77 1569 789 2.09 1849 846 2.42 2136 896 2.75 2420
11 | 29 | 50TJS008 (712/TONS — STANDARD MOTOR (BELT DRIVE)* (cont)
11 | 30 | External Static Pressure (in. wg)
11 | 31 | Airflow
11 | 32 | 1.2 1.4 1.6 1.8 2.0
11 | 33 | (Cfm)
11 | 34 | Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts
11 | 35 | 2250 810 1.62 1439 850 1.91 1691 873 2.20 1945 883 2.50 2206 895 2.78 2445
11 | 36 | 2300 816 1.65 1465 859 1.94 1718 888 2.24 1980 903 2.55 2249 911 2.85 2504
11 | 37 | 2400 824 1.72 1526 872 2.01 1779 909 2.32 2050 931 2.64 2326 935 2.96 2595
11 | 38 | 2500 832 1.79 1587 882 2.09 1849 925 2.40 2119 955 2.72 2394 972 3.06 2678
11 | 39 | 2550 836 1.83 1621 887 2.13 1884 931 2.45 2162 964 2.77 2436 986 3.11 2718
11 | 40 | 2660 839 1.87 1656 891 2.17 1919 936 2.49 2197 973 2.82 2479 999 3.16 2759
11 | 41 | 2700 846 1.95 1726 898 2.26 1997 946 2.58 2275 987 2.91 2554 1019 3.26 2839
11 | 42 | 2800 855 2.04 1805 906 2.35 2076 954 2.67 2352 997 3.01 2637 1034 3.36 2917
11 | 43 | 2900 863 2.13 1884 913 2.44 2154 961 2.77 2436 1006 3.12 2727 — — —
11 | 44 | 3000 872 2.22 1962 921 2.54 2240 969 2.88 2529 1014 3.22 2807 — — —
11 | 45 | 3100 882 2.33 2058 930 2.65 2335 976 2.99 2620 1021 3.34 2902 — — —
11 | 46 | 3200 892 2.45 2162 939 2.76 2428 984 3.10 2710 — — — — — —
11 | 47 | 3300 902 2.57 2266 948 2.88 2529 993 3.21 2799 — — — — — —
11 | 48 | 3400 912 2.69 2369 958 3.01 2637 1002 3.34 2902 — — — — — —
11 | 49 | 3500 921 2.82 2479 968 3.15 2751 — — — — — — — — —
11 | 50 | 3600 930 2.95 2587 978 3.29 2862 — — — — — — — — —
11 | 51 | 3700 940 3.07 2686 — — — — — — — — — — — —
11 | 52 | 3750 945 3.14 2743 — — — — — — — — — — — —
11 | 53 | LEGEND 2. Maximum usable watts input is 2120 and maximum continuous bhp
11 | 54 | Bhp — Brake Horsepower Input to Fan is 2.90. Extensive motor and electrical testing on these units
11 | 55 | FIOP — Factory-Installed Option ensures that the full range of the motor can be utilized with confi-
11 | 56 | Watts — Input Watts to Motor dence. Using your fan motors up to the wattage ratings shown will
11 | 57 | not result in nuisance tripping or premature motor failure. Unit war-
11 | 58 | *Motor drive range: 590 to 840 rpm. ranty will not be affected.
11 | 59 | All other rpms require field-supplied drive.
11 | 60 | NOTES: 3. Values include losses for filters, unit casing, and wet coils.
11 | 61 | 1. Boldface Out of Drive Package or Motor range . 4. Use of a field-supplied motor may affect wire sizing. Contact your
11 | 62 | Carrier representative for details.
11 | 63 | 5. Interpolation is permissible. Do not extrapolate.
11 | 64 | 6. Motor Efficiency: 85%.
11 | 69 | 11
12 | 1 | Performance data (cont)
12 | 2 | FAN PERFORMANCE — HORIZONTAL DISCHARGE UNITS
12 | 3 | 50TJS009 (8 1/2 TONS) STANDARD MOTOR (BELT DRIVE)*
12 | 4 | External Static Pressure (in. wg)
12 | 5 | Airflow
12 | 6 | 0.2 0.4 0.6 0.8 1.0
12 | 7 | (Cfm)
12 | 8 | Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts
12 | 9 | 2550 501 0.57 577 587 0.79 747 659 1.05 956 722 1.29 1156 780 1.55 1378
12 | 10 | 2660 507 0.59 592 592 0.82 771 663 1.08 981 727 1.32 1182 784 1.58 1404
12 | 11 | 2700 520 0.65 638 604 0.89 827 672 1.14 1031 737 1.40 1250 793 1.66 1473
12 | 12 | 2800 533 0.71 684 615 0.95 875 683 1.20 1081 747 1.49 1327 802 1.75 1552
12 | 13 | 2900 546 0.77 731 626 1.02 932 693 1.27 1140 756 1.57 1396 813 1.84 1630
12 | 14 | 3000 559 0.83 779 637 1.09 989 704 1.35 1207 765 1.66 1473 823 1.94 1718
12 | 15 | 3100 572 0.90 835 648 1.17 1056 715 1.43 1275 775 1.74 1543 832 2.05 1814
12 | 16 | 3200 585 0.96 883 660 1.24 1114 727 1.52 1353 785 1.83 1321 841 2.15 1901
12 | 17 | 3300 598 1.03 940 671 1.32 1182 739 1.62 1439 795 1.91 1691 851 2.26 1997
12 | 18 | 3400 610 1.10 998 682 1.41 1258 750 1.72 1526 806 2.01 1779 860 2.36 2084
12 | 19 | 3500 623 1.17 1056 694 1.50 1335 761 1.82 1613 817 2.11 1866 870 2.47 2180
12 | 20 | 3600 636 1.25 1123 707 1.60 1422 772 1.93 1709 828 2.23 1971 880 2.57 2266
12 | 21 | 3700 649 1.33 1190 720 1.71 1517 783 2.03 1796 840 2.35 2076 890 2.69 2369
12 | 22 | 3750 655 1.37 1224 727 1.77 1569 789 2.09 1849 846 2.42 2136 896 2.75 2420
12 | 23 | 3800 661 1.41 1258 733 1.82 1613 795 2.15 1901 852 2.48 2188 901 2.80 2462
12 | 24 | 3900 674 1.49 1327 746 1.93 1709 806 2.26 1997 863 2.61 2300 912 2.93 2571
12 | 25 | 4000 687 1.57 1396 759 2.05 1814 817 2.38 2102 874 2.75 2420 923 3.08 2694
12 | 26 | 4100 699 1.60 1473 772 2.17 1919 828 2.50 2206 885 2.88 2529 935 3.23 2815
12 | 27 | 4200 712 1.75 1552 785 2.30 2032 840 2.64 2326 897 3.03 2653 947 3.39 2940
12 | 28 | 4250 719 1.80 1595 792 2.37 2093 846 2.71 2386 903 3.10 2710 — — —
12 | 31 | 50TJS009 (8 1/2 TONS) STANDARD MOTOR (BELT DRIVE)* (cont)
12 | 32 | External Static Pressure (in. wg)
12 | 33 | Airflow
12 | 34 | 1.2 1.4 1.6 1.8 2.0
12 | 35 | (Cfm)
12 | 36 | Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts
12 | 37 | 2550 836 1.83 1621 887 2.13 1884 931 2.45 2162 964 2.77 2436 986 3.11 2718
12 | 38 | 2660 839 1.87 1656 891 2.17 1919 936 2.49 2197 973 2.82 2479 999 3.16 2759
12 | 39 | 2700 846 1.95 1726 898 2.26 1997 946 2.58 2275 987 2.91 2554 1019 3.26 2839
12 | 40 | 2800 855 2.04 1805 906 2.35 2076 954 2.67 2352 997 3.01 2637 1034 3.36 2917
12 | 41 | 2900 863 2.13 1884 913 2.44 2154 961 2.77 2436 1006 3.12 2727 — — —
12 | 42 | 3000 872 2.22 1962 921 2.54 2240 969 2.88 2529 1014 3.22 2807 — — —
12 | 43 | 3100 882 2.33 2058 930 2.65 2335 976 2.99 2620 1021 3.34 2902 — — —
12 | 44 | 3200 892 2.45 2162 939 2.76 2428 984 3.10 2710 — — — — — —
12 | 45 | 3300 902 2.57 2266 948 2.88 2529 993 3.21 2799 — — — — — —
12 | 46 | 3400 912 2.69 2369 958 3.01 2637 1002 3.34 2902 — — — — — —
12 | 47 | 3500 921 2.82 2479 968 3.15 2751 — — — — — — — — —
12 | 48 | 3600 930 2.95 2587 978 3.29 2862 — — — — — — — — —
12 | 49 | 3700 940 3.07 2686 — — — — — — — — — — — —
12 | 50 | 3750 945 3.14 2743 — — — — — — — — — — — —
12 | 51 | 3800 949 3.20 2781 — — — — — — — — — — — —
12 | 52 | 3900 959 3.33 2894 — — — — — — — — — — — —
12 | 53 | 4000 — — — — — — — — — — — — — — —
12 | 54 | 4100 — — — — — — — — — — — — — — —
12 | 55 | 4200 — — — — — — — — — — — — — — —
12 | 56 | 4250 — — — — — — — — — — — — — — —
12 | 57 | LEGEND 2. Maximum usable watts input is 2120 and maximum continuous bhp
12 | 58 | Bhp — Brake Horsepower Input to Fan is 2.90. Extensive motor and electrical testing on these units
12 | 59 | FIOP — Factory-Installed Option ensures that the full range of the motor can be utilized with confi-
12 | 60 | Watts — Input Watts to Motor dence. Using your fan motors up to the wattage ratings shown will
12 | 61 | not result in nuisance tripping or premature motor failure. Unit war-
12 | 62 | *Motor drive range: 685 to 935 rpm. All other rpms require field- ranty will not be affected.
12 | 63 | supplied drive.
12 | 64 | NOTES:
12 | 65 | 3. Values include losses for filters, unit casing, and wet coils.
12 | 66 | 1. Boldface Out of Drive Package or Motor range .
12 | 67 | 4. Use of a field-supplied motor may affect wire sizing. Contact your
12 | 68 | Carrier representative for details.
12 | 69 | 5. Interpolation is permissible. Do not extrapolate.
12 | 70 | 6. Motor Efficiency: 85%.
12 | 75 | 12
13 | 1 | Performance data (cont)
13 | 2 | FAN PERFORMANCE — HORIZONTAL DISCHARGE UNITS
13 | 3 | 50TJS012 (10 TONS) STANDARD MOTOR (BELT DRIVE)*
13 | 4 | External Static Pressure (in. wg)
13 | 5 | Airflow
13 | 6 | 0.2 0.4 0.6 0.8 1.0 1.2
13 | 7 | (Cfm
13 | 8 | Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts
13 | 9 | 3000 532 0.64 630 605 0.81 763 670 0.97 891 725 1.12 1014 778 1.28 1148 825 1.43 1275
13 | 10 | 3100 544 0.70 677 616 0.86 803 680 1.03 940 735 1.20 1081 787 1.36 1216 835 1.52 1353
13 | 11 | 3200 557 0.75 716 628 0.93 859 690 1.10 998 746 1.28 1148 796 1.44 1284 844 1.61 1430
13 | 12 | 3300 570 0.81 763 639 0.99 907 700 1.18 1064 757 1.36 1216 805 1.52 1353 854 1.70 1508
13 | 13 | 3400 583 0.88 818 651 1.06 965 711 1.25 1123 767 1.44 1284 815 1.61 1430 863 1.79 1587
13 | 14 | 3500 596 0.94 867 663 1.14 1031 721 1.33 1190 777 1.52 1353 826 1.71 1517 871 1.88 1665
13 | 15 | 3600 609 1.01 924 674 1.22 1097 732 1.42 1267 787 1.61 1430 836 1.80 1595 880 1.98 1753
13 | 16 | 3700 622 1.09 989 686 1.30 1165 744 1.50 1335 797 1.70 1508 847 1.91 1691 890 2.09 1849
13 | 17 | 3800 635 1.16 1047 698 1.39 1241 755 1.59 1413 808 1.80 1595 857 2.01 1779 901 2.20 1945
13 | 18 | 3900 649 1.25 1123 713 1.48 1318 767 1.68 1491 818 1.90 1683 867 2.11 1866 912 2.32 2050
13 | 19 | 4000 662 1.33 1190 722 1.57 1396 778 1.78 1578 829 2.01 1779 878 2.22 1962 922 2.44 2203
13 | 20 | 4100 675 1.42 1267 734 1.67 1482 790 1.89 1674 839 2.12 1875 888 2.33 2058 933 2.56 2309
13 | 21 | 4200 689 1.52 1353 746 1.77 1569 801 1.99 1761 851 2.23 1971 898 2.45 2212 943 2.69 2424
13 | 22 | 4300 702 1.61 1430 759 1.88 1665 813 2.11 1866 862 2.34 2067 908 2.58 2326 953 2.81 2533
13 | 23 | 4400 715 1.72 1526 772 1.99 1761 825 2.22 1962 873 2.46 2221 919 2.71 2442 963 2.94 2651
13 | 24 | 4500 729 1.83 1621 785 2.10 1858 837 2.35 2076 885 2.59 2335 929 2.85 2569 973 3.08 2782
13 | 25 | 4600 742 1.94 1718 797 2.22 1962 848 2.48 2238 896 2.72 2451 940 2.98 2688 984 3.22 2914
13 | 26 | 4700 756 2.06 1823 810 2.34 2067 860 2.61 2353 908 2.86 2578 951 3.12 2727 994 3.38 3068
13 | 27 | 4800 770 2.18 1927 823 2.46 2221 872 2.75 2505 919 3.00 2707 963 3.27 2847 1003 3.43 3202
13 | 28 | 4900 783 2.31 2041 836 2.60 2344 884 2.89 2605 931 3.14 2838 974 3.41 2956 1013 3.59 3349
13 | 29 | 5000 797 2.44 2203 849 2.73 2460 897 3.04 2661 943 3.30 2870 984 3.44 3211 1023 3.75 3501
13 | 32 | 50TJS012 (10 TONS) STANDARD MOTOR (BELT DRIVE)* (cont)
13 | 33 | External Static Pressure (in. wg)
13 | 34 | Airflow
13 | 35 | 1.4 1.6 1.8 2.0
13 | 36 | (Cfm)
13 | 37 | Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts
13 | 38 | 3000 874 1.60 1422 926 1.82 1613 974 2.11 1920 1012 2.41 2134
13 | 39 | 3100 880 1.68 1491 933 1.87 1656 983 2.16 1963 1017 2.44 2177
13 | 40 | 3200 888 1.77 1569 934 1.94 1718 988 2.18 1980 1025 2.47 2230
13 | 41 | 3300 897 1.86 1648 940 2.03 1853 989 2.24 2031 1032 2.53 2282
13 | 42 | 3400 907 1.97 1744 947 2.14 1946 991 2.32 2099 1038 2.57 2318
13 | 43 | 3500 916 2.07 1831 956 2.25 2039 997 2.43 2195 1043 2.64 2380
13 | 44 | 3600 926 2.18 1927 966 2.41 2134 1004 2.54 2291 1045 2.74 2478
13 | 45 | 3700 934 2.28 2015 976 2.48 2238 1013 2.66 2397 1051 2.85 2569
13 | 46 | 3800 943 2.41 2160 985 2.60 2334 1023 2.79 2514 1059 2.98 2688
13 | 47 | 3900 952 2.51 2265 994 2.72 2451 1032 2.92 2633 1068 3.12 2819
13 | 48 | 4000 962 2.63 2371 1003 2.84 2560 1042 3.06 2763 1078 3.26 2952
13 | 49 | 4100 973 2.77 2496 1011 2.97 2679 1051 3.20 2895 1087 3.41 3097
13 | 50 | 4200 983 2.91 2624 1021 3.11 2810 1060 3.34 3029 1090 3.51 3276
13 | 51 | 4300 994 3.05 2754 1031 3.25 2943 1068 3.48 3166 1097 3.70 3453
13 | 52 | 4400 1004 3.19 2885 1042 3.41 3097 1080 3.63 3388 1105 3.91 3642
13 | 53 | 4500 1015 3.33 2020 1051 3.45 3218 1090 3.75 3493 1112 4.12 3843
13 | 54 | 4600 1025 3.48 3166 1060 3.61 3369 1100 3.92 3655 1119 4.35 4057
13 | 55 | 4700 1037 3.58 3335 1070 3.84 3325 1111 4.10 3822 1126 4.59 4284
13 | 56 | 4800 1048 3.75 3494 1080 3.95 3686 1121 4.28 3995 1133 4.85 4523
13 | 57 | 4900 1060 3.92 3659 1089 4.13 3854 1132 4.48 4174 1140 5.12 4775
13 | 58 | 5000 1072 4.11 3830 1099 4.32 4027 1144 4.67 4359 — — —
13 | 59 | LEGEND electrical testing on these units ensures that the full range of the
13 | 60 | Bhp — Brake Horsepower Input to Fan motor can be utilized with confidence. Using your fan motors up to
13 | 61 | FIOP — Factory-Installed Option the wattage ratings shown will not result in nuisance tripping or
13 | 62 | Watts — Input Watts to Motor premature motor failure. Unit warranty will not be affected.
13 | 64 | *Standard motor drive range: 685 to 935 rpm.
13 | 65 | 3. Values include losses for filters, unit casings, and wet coils.
13 | 66 | All other rpms require field-supplied drive. 4. Use of a field-supplied motor may affect wire sizing. Contact your
13 | 67 | NOTES: Carrier representative for details.
13 | 68 | 1. Boldface Out of Motor and Drive Package range. 5. Interpolation is permissible. Do not extrapolate.
13 | 69 | 2. Maximum usable watts input is 2120 with standard motor, 6. Motor Efficiency: 85%
13 | 70 | Maximum continuous bhp is 2.90 with standard motor.
13 | 75 | 13
14 | 1 | Performance data (cont)
14 | 2 | FAN PERFORMANCE — HORIZONTAL DISCHARGE UNITS
14 | 3 | 50TJS014 (121 /2 TONS) STANDARD MOTOR (BELT DRIVE)*
14 | 4 | External Static Pressure (in. wg)
14 | 5 | Airflow 0.2 0.4 0.6 0.8 1.0
14 | 6 | (Cfm)
14 | 7 | Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts
14 | 8 | 3700 607 0.97 947 670 1.18 1113 732 1.37 1267 782 1.56 1423 833 1.73 1565
14 | 9 | 3800 621 1.05 1010 681 1.25 1170 742 1.45 1332 795 1.66 1506 842 1.82 1641
14 | 10 | 3900 636 1.13 1073 693 1.32 1226 751 1.53 1398 808 1.76 1590 851 1.92 1725
14 | 11 | 4000 650 1.21 1137 705 1.40 1291 761 1.61 1464 819 1.86 1674 861 2.02 1811
14 | 12 | 4100 665 1.30 1210 717 1.48 1357 772 1.71 1548 830 1.96 1759 871 2.13 1905
14 | 13 | 4200 680 1.39 1283 728 1.57 1431 783 1.81 1632 839 2.05 1836 883 2.25 2009
14 | 14 | 4300 696 1.49 1365 739 1.66 1506 794 1.91 1717 848 2.14 1914 896 2.38 2123
14 | 15 | 4400 711 1.60 1456 750 1.75 1582 805 2.02 1811 857 2.24 2000 908 2.51 2237
14 | 16 | 4500 727 1.70 1540 762 1.85 1666 817 2.12 1897 867 2.35 2096 919 2.63 2343
14 | 17 | 4600 742 1.82 1641 774 1.96 1759 828 2.23 1992 877 2.46 2193 929 2.75 2450
14 | 18 | 4700 758 1.94 1742 786 2.07 1854 840 2.34 2088 888 2.59 2307 938 2.87 2557
14 | 19 | 4800 773 2.06 1845 799 2.18 1948 852 2.46 2193 899 2.72 2423 947 2.98 2656
14 | 20 | 4900 789 2.19 1957 812 2.30 2053 863 2.57 2290 910 2.86 2548 957 3.11 2773
14 | 21 | 5000 805 2.32 2070 826 2.43 2166 875 2.70 2405 921 2.99 2665 966 3.24 2891
14 | 22 | 5100 821 2.47 2202 840 2.57 2290 887 2.83 2521 932 3.13 2792 976 3.38 3019
14 | 23 | 5200 837 2.61 2325 854 2.71 2414 898 2.96 2638 943 3.28 2928 987 3.53 3157
14 | 24 | 5300 853 2.76 2459 868 2.85 2539 909 3.09 2755 955 3.42 3056 998 3.69 3304
14 | 25 | 5400 869 2.92 2602 882 3.01 2683 920 3.24 2891 967 3.57 3193 1009 3.86 3461
14 | 26 | 5500 885 3.09 2755 897 3.17 2828 932 3.38 3019 978 3.72 3331 1029 4.03 3618
14 | 27 | 5600 901 3.26 2910 911 3.33 2973 943 3.54 3166 990 3.87 3470 1031 4.20 3775
14 | 28 | 5700 917 3.44 3074 926 3.50 3129 956 3.70 3313 1002 4.03 3618 1042 4.38 3943
14 | 29 | 5800 933 3.62 3239 941 3.68 3294 968 3.87 3470 1013 4.20 3775 1053 4.56 4111
14 | 30 | 5900 949 3.81 3414 956 3.87 3470 981 4.05 3637 1025 4.37 3934 1065 4.74 4279
14 | 31 | 6000 965 4.01 3600 972 4.06 3646 995 4.23 3804 1037 4.55 4102 1076 4.92 4447
14 | 32 | 6100 981 4.21 3785 987 4.26 3832 1008 4.42 3981 1042 4.73 4270 1088 5.10 4614
14 | 33 | 6200 997 4.42 3981 1002 4.46 4018 1022 4.62 4167 1058 4.91 4437 — — —
14 | 34 | 6300 1014 4.64 4186 1018 4.68 4223 1036 4.83 4363 1070 5.11 4624 — — —
14 | 37 | 50TJS014 (121 /2 TONS) STANDARD MOTOR (BELT DRIVE)* (cont)
14 | 38 | External Static Pressure (in. wg)
14 | 39 | Airflow 1.2 1.4 1.6 1.8 2.0
14 | 40 | (Cfm)
14 | 41 | Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts Rpm Bhp Watts
14 | 42 | 3700 879 1.95 1751 927 2.17 1940 973 2.38 2123 1013 2.57 2290 1046 2.73 2432
14 | 43 | 3800 889 2.03 1819 934 2.26 2018 980 2.48 2210 1022 2.69 2396 1058 2.87 2557
14 | 44 | 3900 898 2.12 1897 942 2.36 2105 987 2.59 2307 1030 2.81 2503 1068 3.01 2683
14 | 45 | 4000 908 2.21 1974 950 2.46 2193 994 2.70 2405 1037 2.92 2602 1077 3.14 2801
14 | 46 | 4100 917 2.32 2070 960 2.55 2272 1001 2.81 2503 1045 3.04 2710 1085 3.21 2919
14 | 47 | 4200 925 2.44 2175 969 2.65 2370 1009 2.92 2602 1051 3.17 2828 1092 3.40 3037
14 | 48 | 4300 935 2.56 2281 979 2.77 2468 1018 3.03 2701 1058 3.29 2937 1100 3.53 3157
14 | 49 | 4400 945 2.68 2387 988 2.89 2575 1028 3.14 2801 1066 3.41 3047 1106 3.67 3285
14 | 50 | 4500 955 2.82 2512 996 3.02 2692 1037 3.25 2901 1074 3.54 3166 1113 3.81 3414
14 | 51 | 4600 967 2.96 2638 1005 3.16 2819 1046 3.38 3019 1084 3.66 3276 1121 3.95 3544
14 | 52 | 4700 980 3.11 2773 1015 3.30 2946 1056 3.52 3147 1093 3.79 3396 1129 4.09 3674
14 | 53 | 4800 992 3.26 2910 1025 3.45 3083 1064 3.67 3285 1103 3.92 3516 1137 4.22 3795
14 | 54 | 4900 1003 3.41 3047 1036 3.61 3230 1073 3.83 3433 1112 4.07 3655 1147 4.36 3925
14 | 55 | 5000 1014 3.56 3184 1049 3.79 3396 1083 4.00 3590 1121 4.23 3804 1157 4.50 4055
14 | 56 | 5100 1024 3.71 3322 1061 3.96 3553 1093 4.17 3748 1129 4.40 3962 1166 4.66 4202
14 | 57 | 5200 1033 3.84 3442 1073 4.14 3720 1103 4.34 3906 1138 4.58 4130 1175 4.82 4354
14 | 58 | 5300 1042 3.98 3572 1084 4.31 3878 1115 4.53 4157 1148 4.76 4326 1184 5.01 4531
14 | 59 | 5400 1051 4.14 3720 1095 4.49 4046 1128 4.74 4279 1158 4.95 4475 1193 5.20 4707
14 | 60 | 5500 1061 4.30 3818 1105 4.66 4204 1140 4.94 4465 1168 5.15 4661 — — —
14 | 61 | 5600 1071 4.46 4018 1114 4.81 4344 1152 5.14 4652 — — — — — —
14 | 62 | 5700 1081 4.64 4186 1123 4.98 4503 — — — — — — — — —
14 | 63 | 5800 1092 4.84 4372 1132 5.15 4661 — — — — — — — — —
14 | 64 | 5900 1103 5.04 4558 — — — — — — — — — — — —
14 | 65 | 6000 1114 5.24 4745 — — — — — — — — — — — —
14 | 66 | 6100 — — — — — — — — — — — — — — —
14 | 67 | 6200 — — — — — — — — — — — — — — —
14 | 68 | 6300 — — — — — — — — — — — — — — —
14 | 69 | LEGEND 2. Maximum usable watts input is 3313 with standard motor.
14 | 70 | Bhp — Brake Horsepower Input to Fan Maximum continuous bhp is 3.70 with standard motor.
14 | 71 | FIOP — Factory-Installed Option Extensive motor and electrical testing on these units ensures that the full
14 | 72 | Watts — Input Watts to Motor range of the motor can be utilized with confidence.
14 | 73 | Using your fan motors up to the wattage ratings shown will not result
14 | 74 | *Standard motor drive range: 860 to 1080 rpm. Alternate motor drive range: in nuisance tripping or premature motor failure. Unit warranty
14 | 75 | 900 to 1260 rpm. All other rpms require field-supplied drive. will not be affected.
14 | 76 | 3. Values include losses for filters, unit casing, and wet coils.
14 | 77 | NOTES:
14 | 78 | 1. Boldface Out of Drive Package or Motor range . 4. Use of a field-supplied motor may affect wire sizing. Contact your Carrier
14 | 79 | representative for details.
14 | 81 | 5. Interpolation is permissible. Do not extrapolate.
14 | 82 | 6. Motor Efficiency: 85%
14 | 83 | 14

## Blower_Airflow_Rows
Model | PDF page | Page line | Airflow CFM | Performance values as printed (RPM / BHP / Watts by static-pressure block)
50LJS007 | 10 | 9 | 1800 | 765 0.45 487 821 0.51 532 923 0.65 638 1019 0.81 843 1099 0.96 883
50LJS007 | 10 | 10 | 1900 | 802 0.45 539 854 0.58 585 953 0.73 700 1046 0.90 835 1126 1.06 965
50LJS007 | 10 | 11 | 2000 | 840 0.60 600 888 0.66 646 984 0.82 771 1073 0.99 907 1154 1.16 1047
50LJS007 | 10 | 12 | 2100 | 878 0.69 669 923 0.75 716 1015 0.91 843 1101 1.08 981 1182 1.27 1140
50LJS007 | 10 | 13 | 2200 | 916 0.78 739 958 0.85 795 1046 1.01 924 1129 1.19 1072 1209 1.39 1241
50LJS007 | 10 | 14 | 2300 | 954 0.89 827 993 0.96 883 1079 1.13 1022 1160 1.31 1173 1237 1.51 1344
50LJS007 | 10 | 15 | 2400 | 993 1.00 916 1029 1.07 973 1112 1.25 1123 1190 1.43 1275 1264 1.63 1447
50LJS007 | 10 | 16 | 2500 | 1031 1.13 1022 1066 1.20 1081 1145 1.39 1241 1220 1.57 1396 1292 1.77 1569
50LJS007 | 10 | 17 | 2600 | 1070 1.26 1131 1103 1.34 1199 1179 1.52 1353 1251 1.71 1517 1322 1.92 1700
50LJS007 | 10 | 18 | 2700 | 1109 1.41 1258 1140 1.48 1318 1212 1.67 1482 1283 1.87 1656 1352 2.09 1849
50LJS007 | 10 | 19 | 2800 | 1148 1.57 1396 1177 1.64 1456 1246 1.83 1621 1316 2.04 1805 1383 2.26 1997
50LJS007 | 10 | 20 | 2900 | 1188 1.74 1543 1215 1.81 1604 1281 2.00 1770 1349 2.22 1962 1413 2.44 2154
50LJS007 | 10 | 21 | 3000 | 1227 1.92 1700 1253 2.00 1770 1316 2.19 1936 1382 2.42 2136 1444 2.63 2317
50LJS007 | 10 | 29 | 1800 | 1178 1.14 1031 1249 1.32 1182 1316 1.52 1353 1382 1.72 1526
50LJS007 | 10 | 30 | 1900 | 1201 1.23 1106 1274 1.43 1275 1338 1.62 1439 1402 1.83 1621
50LJS007 | 10 | 31 | 2000 | 1226 1.33 1990 1297 1.53 1361 1363 1.73 1534 1424 1.94 1718
50LJS007 | 10 | 32 | 2100 | 1252 1.45 1292 1320 1.64 1456 1388 1.85 1639 1448 2.07 1831
50LJS007 | 10 | 33 | 2200 | 1280 1.58 1404 1345 1.77 1569 1410 1.97 1744 1473 2.20 1945
50LJS007 | 10 | 34 | 2300 | 1309 1.71 1517 1372 1.91 1691 1434 2.11 1866 1496 2.34 2067
50LJS007 | 10 | 35 | 2400 | 1336 1.85 1639 1400 2.06 1823 1459 2.26 1997 1519 2.48 2188
50LJS007 | 10 | 36 | 2500 | 1363 2.00 1770 1428 2.22 1962 1486 2.43 2145 1543 2.65 2335
50LJS007 | 10 | 37 | 2600 | 1390 2.15 1901 1456 2.38 2102 1514 2.61 2300 1569 2.83 2487
50LJS007 | 10 | 38 | 2700 | 1418 2.31 2041 1483 2.56 2257 1543 2.80 2462 — — —
50LJS007 | 10 | 39 | 2800 | 1446 2.48 2188 1510 2.73 2403 — — — — — —
50LJS007 | 10 | 40 | 2900 | 1476 2.67 2352 1537 2.92 2562 — — — — — —
50LJS007 | 10 | 41 | 3000 | 1506 2.88 2529 — — — — — — — — —
50TJS008 | 11 | 9 | 2250 | 465 0.43 473 554 0.64 630 630 0.86 803 695 1.09 989 757 1.34 1199
50TJS008 | 11 | 10 | 2300 | 471 0.45 487 559 0.66 646 635 0.89 827 699 1.12 1014 760 1.37 1224
50TJS008 | 11 | 11 | 2400 | 482 0.50 524 569 0.71 684 645 0.95 875 708 1.18 1064 768 1.44 1284
50TJS008 | 11 | 12 | 2500 | 494 0.54 554 581 0.76 723 654 1.01 924 717 1.25 1123 776 1.51 1344
50TJS008 | 11 | 13 | 2550 | 501 0.57 577 587 0.79 747 659 1.05 956 722 1.29 1156 780 1.55 1378
50TJS008 | 11 | 14 | 2660 | 507 0.59 592 592 0.82 771 663 1.08 981 727 1.32 1182 784 1.58 1404
50TJS008 | 11 | 15 | 2700 | 520 0.65 638 604 0.89 827 672 1.14 1031 737 1.40 1250 793 1.66 1473
50TJS008 | 11 | 16 | 2800 | 533 0.71 684 615 0.95 875 683 1.20 1081 747 1.49 1327 802 1.75 1552
50TJS008 | 11 | 17 | 2900 | 546 0.77 731 626 1.02 932 693 1.27 1140 756 1.57 1396 813 1.84 1630
50TJS008 | 11 | 18 | 3000 | 559 0.83 779 637 1.09 989 704 1.35 1207 765 1.66 1473 823 1.94 1718
50TJS008 | 11 | 19 | 3100 | 572 0.90 835 648 1.17 1056 715 1.43 1275 775 1.74 1543 832 2.05 1814
50TJS008 | 11 | 20 | 3200 | 585 0.96 883 660 1.24 1114 727 1.52 1353 785 1.83 1627 841 2.15 1901
50TJS008 | 11 | 21 | 3300 | 598 1.03 940 671 1.32 1182 739 1.62 1439 795 1.91 1691 851 2.26 1997
50TJS008 | 11 | 22 | 3400 | 610 1.10 998 682 1.41 1258 750 1.72 1526 806 2.01 1779 860 2.36 2084
50TJS008 | 11 | 23 | 3500 | 623 1.17 1056 694 1.50 1335 761 1.82 1613 817 2.11 1866 870 2.47 2180
50TJS008 | 11 | 24 | 3600 | 636 1.25 1123 707 1.60 1422 772 1.93 1709 828 2.23 1971 880 2.57 2266
50TJS008 | 11 | 25 | 3700 | 649 1.33 1190 720 1.71 1517 783 2.03 1796 840 2.35 2076 890 2.69 2369
50TJS008 | 11 | 26 | 3750 | 655 1.37 1224 727 1.77 1569 789 2.09 1849 846 2.42 2136 896 2.75 2420
50TJS008 | 11 | 35 | 2250 | 810 1.62 1439 850 1.91 1691 873 2.20 1945 883 2.50 2206 895 2.78 2445
50TJS008 | 11 | 36 | 2300 | 816 1.65 1465 859 1.94 1718 888 2.24 1980 903 2.55 2249 911 2.85 2504
50TJS008 | 11 | 37 | 2400 | 824 1.72 1526 872 2.01 1779 909 2.32 2050 931 2.64 2326 935 2.96 2595
50TJS008 | 11 | 38 | 2500 | 832 1.79 1587 882 2.09 1849 925 2.40 2119 955 2.72 2394 972 3.06 2678
50TJS008 | 11 | 39 | 2550 | 836 1.83 1621 887 2.13 1884 931 2.45 2162 964 2.77 2436 986 3.11 2718
50TJS008 | 11 | 40 | 2660 | 839 1.87 1656 891 2.17 1919 936 2.49 2197 973 2.82 2479 999 3.16 2759
50TJS008 | 11 | 41 | 2700 | 846 1.95 1726 898 2.26 1997 946 2.58 2275 987 2.91 2554 1019 3.26 2839
50TJS008 | 11 | 42 | 2800 | 855 2.04 1805 906 2.35 2076 954 2.67 2352 997 3.01 2637 1034 3.36 2917
50TJS008 | 11 | 43 | 2900 | 863 2.13 1884 913 2.44 2154 961 2.77 2436 1006 3.12 2727 — — —
50TJS008 | 11 | 44 | 3000 | 872 2.22 1962 921 2.54 2240 969 2.88 2529 1014 3.22 2807 — — —
50TJS008 | 11 | 45 | 3100 | 882 2.33 2058 930 2.65 2335 976 2.99 2620 1021 3.34 2902 — — —
50TJS008 | 11 | 46 | 3200 | 892 2.45 2162 939 2.76 2428 984 3.10 2710 — — — — — —
50TJS008 | 11 | 47 | 3300 | 902 2.57 2266 948 2.88 2529 993 3.21 2799 — — — — — —
50TJS008 | 11 | 48 | 3400 | 912 2.69 2369 958 3.01 2637 1002 3.34 2902 — — — — — —
50TJS008 | 11 | 49 | 3500 | 921 2.82 2479 968 3.15 2751 — — — — — — — — —
50TJS008 | 11 | 50 | 3600 | 930 2.95 2587 978 3.29 2862 — — — — — — — — —
50TJS008 | 11 | 51 | 3700 | 940 3.07 2686 — — — — — — — — — — — —
50TJS008 | 11 | 52 | 3750 | 945 3.14 2743 — — — — — — — — — — — —
50TJS009 | 12 | 9 | 2550 | 501 0.57 577 587 0.79 747 659 1.05 956 722 1.29 1156 780 1.55 1378
50TJS009 | 12 | 10 | 2660 | 507 0.59 592 592 0.82 771 663 1.08 981 727 1.32 1182 784 1.58 1404
50TJS009 | 12 | 11 | 2700 | 520 0.65 638 604 0.89 827 672 1.14 1031 737 1.40 1250 793 1.66 1473
50TJS009 | 12 | 12 | 2800 | 533 0.71 684 615 0.95 875 683 1.20 1081 747 1.49 1327 802 1.75 1552
50TJS009 | 12 | 13 | 2900 | 546 0.77 731 626 1.02 932 693 1.27 1140 756 1.57 1396 813 1.84 1630
50TJS009 | 12 | 14 | 3000 | 559 0.83 779 637 1.09 989 704 1.35 1207 765 1.66 1473 823 1.94 1718
50TJS009 | 12 | 15 | 3100 | 572 0.90 835 648 1.17 1056 715 1.43 1275 775 1.74 1543 832 2.05 1814
50TJS009 | 12 | 16 | 3200 | 585 0.96 883 660 1.24 1114 727 1.52 1353 785 1.83 1321 841 2.15 1901
50TJS009 | 12 | 17 | 3300 | 598 1.03 940 671 1.32 1182 739 1.62 1439 795 1.91 1691 851 2.26 1997
50TJS009 | 12 | 18 | 3400 | 610 1.10 998 682 1.41 1258 750 1.72 1526 806 2.01 1779 860 2.36 2084
50TJS009 | 12 | 19 | 3500 | 623 1.17 1056 694 1.50 1335 761 1.82 1613 817 2.11 1866 870 2.47 2180
50TJS009 | 12 | 20 | 3600 | 636 1.25 1123 707 1.60 1422 772 1.93 1709 828 2.23 1971 880 2.57 2266
50TJS009 | 12 | 21 | 3700 | 649 1.33 1190 720 1.71 1517 783 2.03 1796 840 2.35 2076 890 2.69 2369
50TJS009 | 12 | 22 | 3750 | 655 1.37 1224 727 1.77 1569 789 2.09 1849 846 2.42 2136 896 2.75 2420
50TJS009 | 12 | 23 | 3800 | 661 1.41 1258 733 1.82 1613 795 2.15 1901 852 2.48 2188 901 2.80 2462
50TJS009 | 12 | 24 | 3900 | 674 1.49 1327 746 1.93 1709 806 2.26 1997 863 2.61 2300 912 2.93 2571
50TJS009 | 12 | 25 | 4000 | 687 1.57 1396 759 2.05 1814 817 2.38 2102 874 2.75 2420 923 3.08 2694
50TJS009 | 12 | 26 | 4100 | 699 1.60 1473 772 2.17 1919 828 2.50 2206 885 2.88 2529 935 3.23 2815
50TJS009 | 12 | 27 | 4200 | 712 1.75 1552 785 2.30 2032 840 2.64 2326 897 3.03 2653 947 3.39 2940
50TJS009 | 12 | 28 | 4250 | 719 1.80 1595 792 2.37 2093 846 2.71 2386 903 3.10 2710 — — —
50TJS009 | 12 | 37 | 2550 | 836 1.83 1621 887 2.13 1884 931 2.45 2162 964 2.77 2436 986 3.11 2718
50TJS009 | 12 | 38 | 2660 | 839 1.87 1656 891 2.17 1919 936 2.49 2197 973 2.82 2479 999 3.16 2759
50TJS009 | 12 | 39 | 2700 | 846 1.95 1726 898 2.26 1997 946 2.58 2275 987 2.91 2554 1019 3.26 2839
50TJS009 | 12 | 40 | 2800 | 855 2.04 1805 906 2.35 2076 954 2.67 2352 997 3.01 2637 1034 3.36 2917
50TJS009 | 12 | 41 | 2900 | 863 2.13 1884 913 2.44 2154 961 2.77 2436 1006 3.12 2727 — — —
50TJS009 | 12 | 42 | 3000 | 872 2.22 1962 921 2.54 2240 969 2.88 2529 1014 3.22 2807 — — —
50TJS009 | 12 | 43 | 3100 | 882 2.33 2058 930 2.65 2335 976 2.99 2620 1021 3.34 2902 — — —
50TJS009 | 12 | 44 | 3200 | 892 2.45 2162 939 2.76 2428 984 3.10 2710 — — — — — —
50TJS009 | 12 | 45 | 3300 | 902 2.57 2266 948 2.88 2529 993 3.21 2799 — — — — — —
50TJS009 | 12 | 46 | 3400 | 912 2.69 2369 958 3.01 2637 1002 3.34 2902 — — — — — —
50TJS009 | 12 | 47 | 3500 | 921 2.82 2479 968 3.15 2751 — — — — — — — — —
50TJS009 | 12 | 48 | 3600 | 930 2.95 2587 978 3.29 2862 — — — — — — — — —
50TJS009 | 12 | 49 | 3700 | 940 3.07 2686 — — — — — — — — — — — —
50TJS009 | 12 | 50 | 3750 | 945 3.14 2743 — — — — — — — — — — — —
50TJS009 | 12 | 51 | 3800 | 949 3.20 2781 — — — — — — — — — — — —
50TJS009 | 12 | 52 | 3900 | 959 3.33 2894 — — — — — — — — — — — —
50TJS009 | 12 | 53 | 4000 | — — — — — — — — — — — — — — —
50TJS009 | 12 | 54 | 4100 | — — — — — — — — — — — — — — —
50TJS009 | 12 | 55 | 4200 | — — — — — — — — — — — — — — —
50TJS009 | 12 | 56 | 4250 | — — — — — — — — — — — — — — —
50TJS012 | 13 | 9 | 3000 | 532 0.64 630 605 0.81 763 670 0.97 891 725 1.12 1014 778 1.28 1148 825 1.43 1275
50TJS012 | 13 | 10 | 3100 | 544 0.70 677 616 0.86 803 680 1.03 940 735 1.20 1081 787 1.36 1216 835 1.52 1353
50TJS012 | 13 | 11 | 3200 | 557 0.75 716 628 0.93 859 690 1.10 998 746 1.28 1148 796 1.44 1284 844 1.61 1430
50TJS012 | 13 | 12 | 3300 | 570 0.81 763 639 0.99 907 700 1.18 1064 757 1.36 1216 805 1.52 1353 854 1.70 1508
50TJS012 | 13 | 13 | 3400 | 583 0.88 818 651 1.06 965 711 1.25 1123 767 1.44 1284 815 1.61 1430 863 1.79 1587
50TJS012 | 13 | 14 | 3500 | 596 0.94 867 663 1.14 1031 721 1.33 1190 777 1.52 1353 826 1.71 1517 871 1.88 1665
50TJS012 | 13 | 15 | 3600 | 609 1.01 924 674 1.22 1097 732 1.42 1267 787 1.61 1430 836 1.80 1595 880 1.98 1753
50TJS012 | 13 | 16 | 3700 | 622 1.09 989 686 1.30 1165 744 1.50 1335 797 1.70 1508 847 1.91 1691 890 2.09 1849
50TJS012 | 13 | 17 | 3800 | 635 1.16 1047 698 1.39 1241 755 1.59 1413 808 1.80 1595 857 2.01 1779 901 2.20 1945
50TJS012 | 13 | 18 | 3900 | 649 1.25 1123 713 1.48 1318 767 1.68 1491 818 1.90 1683 867 2.11 1866 912 2.32 2050
50TJS012 | 13 | 19 | 4000 | 662 1.33 1190 722 1.57 1396 778 1.78 1578 829 2.01 1779 878 2.22 1962 922 2.44 2203
50TJS012 | 13 | 20 | 4100 | 675 1.42 1267 734 1.67 1482 790 1.89 1674 839 2.12 1875 888 2.33 2058 933 2.56 2309
50TJS012 | 13 | 21 | 4200 | 689 1.52 1353 746 1.77 1569 801 1.99 1761 851 2.23 1971 898 2.45 2212 943 2.69 2424
50TJS012 | 13 | 22 | 4300 | 702 1.61 1430 759 1.88 1665 813 2.11 1866 862 2.34 2067 908 2.58 2326 953 2.81 2533
50TJS012 | 13 | 23 | 4400 | 715 1.72 1526 772 1.99 1761 825 2.22 1962 873 2.46 2221 919 2.71 2442 963 2.94 2651
50TJS012 | 13 | 24 | 4500 | 729 1.83 1621 785 2.10 1858 837 2.35 2076 885 2.59 2335 929 2.85 2569 973 3.08 2782
50TJS012 | 13 | 25 | 4600 | 742 1.94 1718 797 2.22 1962 848 2.48 2238 896 2.72 2451 940 2.98 2688 984 3.22 2914
50TJS012 | 13 | 26 | 4700 | 756 2.06 1823 810 2.34 2067 860 2.61 2353 908 2.86 2578 951 3.12 2727 994 3.38 3068
50TJS012 | 13 | 27 | 4800 | 770 2.18 1927 823 2.46 2221 872 2.75 2505 919 3.00 2707 963 3.27 2847 1003 3.43 3202
50TJS012 | 13 | 28 | 4900 | 783 2.31 2041 836 2.60 2344 884 2.89 2605 931 3.14 2838 974 3.41 2956 1013 3.59 3349
50TJS012 | 13 | 38 | 3000 | 874 1.60 1422 926 1.82 1613 974 2.11 1920 1012 2.41 2134
50TJS012 | 13 | 39 | 3100 | 880 1.68 1491 933 1.87 1656 983 2.16 1963 1017 2.44 2177
50TJS012 | 13 | 40 | 3200 | 888 1.77 1569 934 1.94 1718 988 2.18 1980 1025 2.47 2230
50TJS012 | 13 | 41 | 3300 | 897 1.86 1648 940 2.03 1853 989 2.24 2031 1032 2.53 2282
50TJS012 | 13 | 42 | 3400 | 907 1.97 1744 947 2.14 1946 991 2.32 2099 1038 2.57 2318
50TJS012 | 13 | 43 | 3500 | 916 2.07 1831 956 2.25 2039 997 2.43 2195 1043 2.64 2380
50TJS012 | 13 | 44 | 3600 | 926 2.18 1927 966 2.41 2134 1004 2.54 2291 1045 2.74 2478
50TJS012 | 13 | 45 | 3700 | 934 2.28 2015 976 2.48 2238 1013 2.66 2397 1051 2.85 2569
50TJS012 | 13 | 46 | 3800 | 943 2.41 2160 985 2.60 2334 1023 2.79 2514 1059 2.98 2688
50TJS012 | 13 | 47 | 3900 | 952 2.51 2265 994 2.72 2451 1032 2.92 2633 1068 3.12 2819
50TJS012 | 13 | 48 | 4000 | 962 2.63 2371 1003 2.84 2560 1042 3.06 2763 1078 3.26 2952
50TJS012 | 13 | 49 | 4100 | 973 2.77 2496 1011 2.97 2679 1051 3.20 2895 1087 3.41 3097
50TJS012 | 13 | 50 | 4200 | 983 2.91 2624 1021 3.11 2810 1060 3.34 3029 1090 3.51 3276
50TJS012 | 13 | 51 | 4300 | 994 3.05 2754 1031 3.25 2943 1068 3.48 3166 1097 3.70 3453
50TJS012 | 13 | 52 | 4400 | 1004 3.19 2885 1042 3.41 3097 1080 3.63 3388 1105 3.91 3642
50TJS012 | 13 | 53 | 4500 | 1015 3.33 2020 1051 3.45 3218 1090 3.75 3493 1112 4.12 3843
50TJS012 | 13 | 54 | 4600 | 1025 3.48 3166 1060 3.61 3369 1100 3.92 3655 1119 4.35 4057
50TJS012 | 13 | 55 | 4700 | 1037 3.58 3335 1070 3.84 3325 1111 4.10 3822 1126 4.59 4284
50TJS012 | 13 | 56 | 4800 | 1048 3.75 3494 1080 3.95 3686 1121 4.28 3995 1133 4.85 4523
50TJS012 | 13 | 57 | 4900 | 1060 3.92 3659 1089 4.13 3854 1132 4.48 4174 1140 5.12 4775
50TJS014 | 14 | 8 | 3700 | 607 0.97 947 670 1.18 1113 732 1.37 1267 782 1.56 1423 833 1.73 1565
50TJS014 | 14 | 9 | 3800 | 621 1.05 1010 681 1.25 1170 742 1.45 1332 795 1.66 1506 842 1.82 1641
50TJS014 | 14 | 10 | 3900 | 636 1.13 1073 693 1.32 1226 751 1.53 1398 808 1.76 1590 851 1.92 1725
50TJS014 | 14 | 11 | 4000 | 650 1.21 1137 705 1.40 1291 761 1.61 1464 819 1.86 1674 861 2.02 1811
50TJS014 | 14 | 12 | 4100 | 665 1.30 1210 717 1.48 1357 772 1.71 1548 830 1.96 1759 871 2.13 1905
50TJS014 | 14 | 13 | 4200 | 680 1.39 1283 728 1.57 1431 783 1.81 1632 839 2.05 1836 883 2.25 2009
50TJS014 | 14 | 14 | 4300 | 696 1.49 1365 739 1.66 1506 794 1.91 1717 848 2.14 1914 896 2.38 2123
50TJS014 | 14 | 15 | 4400 | 711 1.60 1456 750 1.75 1582 805 2.02 1811 857 2.24 2000 908 2.51 2237
50TJS014 | 14 | 16 | 4500 | 727 1.70 1540 762 1.85 1666 817 2.12 1897 867 2.35 2096 919 2.63 2343
50TJS014 | 14 | 17 | 4600 | 742 1.82 1641 774 1.96 1759 828 2.23 1992 877 2.46 2193 929 2.75 2450
50TJS014 | 14 | 18 | 4700 | 758 1.94 1742 786 2.07 1854 840 2.34 2088 888 2.59 2307 938 2.87 2557
50TJS014 | 14 | 19 | 4800 | 773 2.06 1845 799 2.18 1948 852 2.46 2193 899 2.72 2423 947 2.98 2656
50TJS014 | 14 | 20 | 4900 | 789 2.19 1957 812 2.30 2053 863 2.57 2290 910 2.86 2548 957 3.11 2773
50TJS014 | 14 | 22 | 5100 | 821 2.47 2202 840 2.57 2290 887 2.83 2521 932 3.13 2792 976 3.38 3019
50TJS014 | 14 | 23 | 5200 | 837 2.61 2325 854 2.71 2414 898 2.96 2638 943 3.28 2928 987 3.53 3157
50TJS014 | 14 | 24 | 5300 | 853 2.76 2459 868 2.85 2539 909 3.09 2755 955 3.42 3056 998 3.69 3304
50TJS014 | 14 | 25 | 5400 | 869 2.92 2602 882 3.01 2683 920 3.24 2891 967 3.57 3193 1009 3.86 3461
50TJS014 | 14 | 26 | 5500 | 885 3.09 2755 897 3.17 2828 932 3.38 3019 978 3.72 3331 1029 4.03 3618
50TJS014 | 14 | 27 | 5600 | 901 3.26 2910 911 3.33 2973 943 3.54 3166 990 3.87 3470 1031 4.20 3775
50TJS014 | 14 | 28 | 5700 | 917 3.44 3074 926 3.50 3129 956 3.70 3313 1002 4.03 3618 1042 4.38 3943
50TJS014 | 14 | 29 | 5800 | 933 3.62 3239 941 3.68 3294 968 3.87 3470 1013 4.20 3775 1053 4.56 4111
50TJS014 | 14 | 30 | 5900 | 949 3.81 3414 956 3.87 3470 981 4.05 3637 1025 4.37 3934 1065 4.74 4279
50TJS014 | 14 | 31 | 6000 | 965 4.01 3600 972 4.06 3646 995 4.23 3804 1037 4.55 4102 1076 4.92 4447
50TJS014 | 14 | 32 | 6100 | 981 4.21 3785 987 4.26 3832 1008 4.42 3981 1042 4.73 4270 1088 5.10 4614
50TJS014 | 14 | 33 | 6200 | 997 4.42 3981 1002 4.46 4018 1022 4.62 4167 1058 4.91 4437 — — —
50TJS014 | 14 | 34 | 6300 | 1014 4.64 4186 1018 4.68 4223 1036 4.83 4363 1070 5.11 4624 — — —
50TJS014 | 14 | 42 | 3700 | 879 1.95 1751 927 2.17 1940 973 2.38 2123 1013 2.57 2290 1046 2.73 2432
50TJS014 | 14 | 43 | 3800 | 889 2.03 1819 934 2.26 2018 980 2.48 2210 1022 2.69 2396 1058 2.87 2557
50TJS014 | 14 | 44 | 3900 | 898 2.12 1897 942 2.36 2105 987 2.59 2307 1030 2.81 2503 1068 3.01 2683
50TJS014 | 14 | 45 | 4000 | 908 2.21 1974 950 2.46 2193 994 2.70 2405 1037 2.92 2602 1077 3.14 2801
50TJS014 | 14 | 46 | 4100 | 917 2.32 2070 960 2.55 2272 1001 2.81 2503 1045 3.04 2710 1085 3.21 2919
50TJS014 | 14 | 47 | 4200 | 925 2.44 2175 969 2.65 2370 1009 2.92 2602 1051 3.17 2828 1092 3.40 3037
50TJS014 | 14 | 48 | 4300 | 935 2.56 2281 979 2.77 2468 1018 3.03 2701 1058 3.29 2937 1100 3.53 3157
50TJS014 | 14 | 49 | 4400 | 945 2.68 2387 988 2.89 2575 1028 3.14 2801 1066 3.41 3047 1106 3.67 3285
50TJS014 | 14 | 50 | 4500 | 955 2.82 2512 996 3.02 2692 1037 3.25 2901 1074 3.54 3166 1113 3.81 3414
50TJS014 | 14 | 51 | 4600 | 967 2.96 2638 1005 3.16 2819 1046 3.38 3019 1084 3.66 3276 1121 3.95 3544
50TJS014 | 14 | 52 | 4700 | 980 3.11 2773 1015 3.30 2946 1056 3.52 3147 1093 3.79 3396 1129 4.09 3674
50TJS014 | 14 | 53 | 4800 | 992 3.26 2910 1025 3.45 3083 1064 3.67 3285 1103 3.92 3516 1137 4.22 3795
50TJS014 | 14 | 54 | 4900 | 1003 3.41 3047 1036 3.61 3230 1073 3.83 3433 1112 4.07 3655 1147 4.36 3925
50TJS014 | 14 | 56 | 5100 | 1024 3.71 3322 1061 3.96 3553 1093 4.17 3748 1129 4.40 3962 1166 4.66 4202
50TJS014 | 14 | 57 | 5200 | 1033 3.84 3442 1073 4.14 3720 1103 4.34 3906 1138 4.58 4130 1175 4.82 4354
50TJS014 | 14 | 58 | 5300 | 1042 3.98 3572 1084 4.31 3878 1115 4.53 4157 1148 4.76 4326 1184 5.01 4531
50TJS014 | 14 | 59 | 5400 | 1051 4.14 3720 1095 4.49 4046 1128 4.74 4279 1158 4.95 4475 1193 5.20 4707
50TJS014 | 14 | 60 | 5500 | 1061 4.30 3818 1105 4.66 4204 1140 4.94 4465 1168 5.15 4661 — — —
50TJS014 | 14 | 61 | 5600 | 1071 4.46 4018 1114 4.81 4344 1152 5.14 4652 — — — — — —
50TJS014 | 14 | 62 | 5700 | 1081 4.64 4186 1123 4.98 4503 — — — — — — — — —
50TJS014 | 14 | 63 | 5800 | 1092 4.84 4372 1132 5.15 4661 — — — — — — — — —
50TJS014 | 14 | 64 | 5900 | 1103 5.04 4558 — — — — — — — — — — — —
50TJS014 | 14 | 65 | 6000 | 1114 5.24 4745 — — — — — — — — — — — —
50TJS014 | 14 | 66 | 6100 | — — — — — — — — — — — — — — —
50TJS014 | 14 | 67 | 6200 | — — — — — — — — — — — — — — —
50TJS014 | 14 | 68 | 6300 | — — — — — — — — — — — — — — —
50TJS014 | 14 | 75 | 900 | to 1260 rpm. All other rpms require field-supplied drive. will not be affected.

## Cooling_Capacity_Raw
PDF page | Page line | Extracted cooling-capacity text
6 | 1 | Performance data
6 | 2 | COOLING CAPACITIES
6 | 3 | 50LJS007 (6 TONS)
6 | 4 | Temp (F) Evaporator Air Quantity — Cfm/BF
6 | 5 | Air Entering 1060/0.04 2200/0.06 2750/0.07
6 | 6 | Condenser Evaporator Air — Ewb (F)
6 | 7 | (Edb) 72 67 62 72 67 62 72 67 62
6 | 8 | TC 77.6 71.0 64.8 81.8 74.6 67.7 85.7 76.1 69.9
6 | 9 | 75 SHC 37.3 46.4 55.1 41.5 53.1 64.3 45.7 58.8 69.8
6 | 10 | kW 4.37 4.35 4.32 4.39 4.36 4.33 4.41 4.37 4.35
6 | 11 | TC 74.7 67.7 60.5 78.6 71.1 63.8 80.8 72.7 67.3
6 | 12 | 85 SHC 36.3 45.1 53.2 40.6 52.0 62.1 44.5 58.0 67.2
6 | 13 | kW 4.77 4.73 4.67 4.81 4.76 4.71 4.83 4.78 4.74
6 | 14 | TC 71.8 64.4 56.2 75.4 67.6 59.9 76.9 69.3 65.6
6 | 15 | 95 SHC 35.3 43.9 51.4 39.7 50.9 59.9 43.3 57.3 64.5
6 | 16 | kW 5.18 5.11 5.02 5.23 5.16 5.08 5.25 5.18 5.13
6 | 17 | TC 68.4 60.3 50.8 71.4 63.8 56.2 73.4 65.4 61.2
6 | 18 | 105 SHC 34.2 42.3 48.8 38.4 49.5 56.2 42.5 56.1 61.1
6 | 19 | kW 5.59 5.48 5.37 5.64 5.55 5.46 5.68 5.59 5.53
6 | 20 | TC 64.7 54.6 45.0 67.7 57.6 52.0 69.4 60.6 57.3
6 | 21 | 115 SHC 32.9 40.1 45.0 37.3 47.3 51.9 41.5 45.2 57.3
6 | 22 | kW 5.99 5.86 5.74 6.06 5.93 5.85 6.10 5.97 5.93
6 | 23 | TC 60.9 48.9 39.3 64.1 51.5 47.7 65.3 55.8 53.4
6 | 24 | 125 SHC 31.7 37.9 39.3 36.1 45.0 47.7 40.4 52.4 53.4
6 | 25 | kW 6.39 6.23 6.12 6.48 6.31 6.24 6.53 6.36 6.32
6 | 28 | 50TJS008 (7.0 TONS)
6 | 29 | Evaporator Air Quantity — Cfm/BF
6 | 30 | Temp (F) Air Entering 2250/0.07 2800/0.09 3000/0.10 3750/0.12
6 | 31 | Condenser (Edb) Evaporator Air — Ewb (F)
6 | 32 | 72 67 62 72 67 62 72 67 62 72 67 62
6 | 33 | TC 99.2 91.5 83.2 102.1 94.8 86.9 102.7 95.5 87.6 107.5 100.0 92.1
6 | 34 | 75 SHC 47.7 59.6 70.6 50.8 65.4 78.7 51.7 67.4 81.1 57.3 76.2 90.8
6 | 35 | kW 7.40 7.07 6.74 7.55 7.24 6.93 7.59 7.30 6.97 7.74 7.45 7.11
6 | 36 | TC 94.8 87.0 78.7 98.2 90.3 82.2 99.0 91.1 83.0 103.0 95.3 88.2
6 | 37 | 85 SHC 46.3 58.1 68.7 49.8 64.1 76.8 51.0 66.2 79.1 55.9 74.8 88.0
6 | 38 | kW 7.94 7.61 7.26 8.11 7.78 7.45 8.15 7.82 7.49 8.28 7.96 7.67
6 | 39 | TC 90.5 82.2 73.9 93.6 85.3 77.2 94.2 85.9 78.4 97.8 89.8 83.9
6 | 40 | 95 SHC 44.8 56.2 66.4 48.4 62.3 74.5 49.6 64.5 76.2 54.7 73.2 83.9
6 | 41 | kW 8.48 8.13 7.76 8.67 8.30 7.92 8.71 8.34 7.98 8.81 8.46 8.21
6 | 42 | TC 85.3 77.0 68.3 87.8 79.9 72.0 88.4 80.5 73.3 92.3 84.1 79.3
6 | 43 | 105 SHC 43.0 54.2 63.7 46.5 60.4 71.6 47.7 62.5 73.0 53.3 71.3 79.3
6 | 44 | kW 9.00 8.61 8.28 9.13 8.77 8.44 9.19 8.81 8.50 9.31 8.96 8.73
6 | 45 | TC 82.8 73.8 66.0 85.2 76.8 69.6 85.6 77.4 71.0 89.4 81.0 77.5
6 | 46 | 115 SHC 42.6 53.8 63.2 46.4 60.4 69.6 47.8 62.6 71.0 53.9 71.8 77.3
6 | 47 | kW 9.50 9.10 8.73 9.64 9.25 8.96 9.69 9.29 9.04 9.83 9.44 9.27
6 | 48 | TC 81.0 71.6 64.4 83.4 74.6 67.9 83.6 75.2 69.4 87.3 78.8 76.2
6 | 49 | 122 SHC 42.3 53.5 62.9 46.3 60.4 68.2 47.9 62.6 69.6 54.2 72.2 75.9
6 | 50 | kW 9.85 9.45 9.05 10.01 9.58 9.32 10.03 9.63 9.42 10.19 9.77 9.65
6 | 54 | 50TJS009 (9.0 TONS)
6 | 55 | Evaporator Air Quantity — Cfm/BF
6 | 56 | Temp (F) Air Entering 2550/0.08 3000/0.10 3400/0.11 4250/0.135
6 | 57 | Condenser (Edb) Evaporator Air — Ewb (F)
6 | 58 | 72 67 62 72 67 62 72 67 62 72 67 62
6 | 59 | TC 121.8 113.3 103.5 124.6 116.3 106.4 125.5 117.9 108.3 130.4 122.4 113.3
6 | 60 | 75 SHC 75.1 64.7 79.3 78.6 68.0 85.1 84.1 71.1 89.5 34.9 78.8 100.6
6 | 61 | kW 7.82 7.62 7.42 7.91 10.74 7.48 7.94 6.76 7.56 8.02 7.85 7.65
6 | 62 | TC 118.4 108.9 98.2 120.9 111.7 101.4 122.5 113.6 103.2 128.0 118.3 108.5
6 | 63 | 85 SHC 56.4 70.7 84.0 58.8 75.8 91.0 60.8 79.8 96.7 67.0 89.7 107.7
6 | 64 | kW 8.51 8.27 8.01 5.57 8.36 8.09 8.65 8.43 8.17 8.77 8.53 8.28
6 | 65 | TC 114.0 103.8 91.2 116.2 106.6 95.5 117.6 108.3 97.9 122.9 112.8 114.5
6 | 66 | 95 SHC 55.0 68.9 80.9 57.5 74.1 88.7 59.7 78.5 94.4 66.3 88.7 103.7
6 | 67 | kW 8.95 9.02 8.73 9.04 9.11 8.84 9.11 9.17 8.91 4.79 9.30 9.05
6 | 68 | TC 107.9 98.2 85.1 110.7 100.6 88.4 112.2 102.1 91.9 116.6 106.5 98.9
6 | 69 | 105 SHC 52.8 56.4 77.9 55.9 72.2 85.1 58.3 76.4 90.5 64.4 86.8 98.9
6 | 70 | kW 9.80 9.49 9.13 9.91 9.60 9.27 9.98 9.66 9.35 10.09 9.78 9.54
6 | 71 | TC 97.7 87.9 75.9 99.9 90.4 78.8 101.3 91.8 82.4 105.0 95.7 90.1
6 | 72 | 115 SHC 48.7 61.7 71.9 51.8 66.9 78.1 54.0 71.2 82.3 59.7 81.0 90.0
6 | 73 | kW 10.33 9.97 9.61 10.46 10.10 9.75 10.54 10.18 9.88 10.61 10.30 10.10
6 | 74 | TC 90.5 80.7 69.5 92.4 83.2 72.1 93.6 84.6 75.8 96.8 88.1 83.9
6 | 75 | 122 SHC 45.8 65.4 67.7 48.9 63.2 73.2 51.0 67.6 76.6 56.4 76.9 83.7
6 | 76 | kW 10.70 10.31 9.94 10.85 10.45 10.09 10.93 10.55 10.25 10.97 10.67 10.49
6 | 81 | 6
7 | 1 | COOLING CAPACITIES (Cont.)
7 | 2 | 50TJS012 (10 TONS)
7 | 3 | Temp (F) Evaporator Air Quantity — Cfm/BF
7 | 4 | Air Entering 3000/0.095 4000/0.125 5000/0.15
7 | 5 | Condenser Evaporator Air — Ewb (F)
7 | 6 | (Edb) 72 67 62 72 67 62 72 67 62
7 | 7 | TC 139.8 128.4 115.3 146.6 134.5 123.3 153.8 140.8 129.8
7 | 8 | 75 SHC 68.7 85.0 100.2 75.3 96.2 116.0 83.7 109.6 129.2
7 | 9 | kW 9.86 9.50 9.19 10.10 9.71 9.36 10.27 9.85 9.50
7 | 10 | TC 133.8 123.1 107.0 140.0 128.8 117.8 147.0 134.2 124.7
7 | 11 | 85 SHC 66.1 82.8 96.5 73.1 94.5 113.4 81.3 106.9 124.6
7 | 12 | kW 10.51 10.17 9.84 10.78 10.38 10.04 10.95 10.51 10.19
7 | 13 | TC 127.7 117.0 99.5 133.3 122.5 110.0 139.4 128.1 119.7
7 | 14 | 95 SHC 64.0 80.7 92.6 71.1 92.5 109.0 78.6 105.1 119.6
7 | 15 | kW 11.24 10.89 10.50 11.49 11.10 10.74 11.64 11.25 10.94
7 | 16 | TC 121.5 107.6 90.4 126.3 115.2 101.4 132.3 120.9 113.3
7 | 17 | 105 SHC 62.1 77.0 87.7 68.8 90.3 101.4 76.7 103.1 113.3
7 | 18 | kW 12.05 11.64 11.21 12.25 11.86 11.52 12.39 12.01 11.77
7 | 19 | TC 111.5 94.9 81.6 116.3 100.7 90.5 121.2 108.5 101.6
7 | 20 | 115 SHC 57.6 70.2 80.8 64.4 82.3 90.5 72.0 95.5 101.6
7 | 21 | kW 12.63 12.17 11.74 12.85 12.42 12.13 12.98 12.57 12.36
7 | 22 | TC 104.5 86.1 75.4 109.3 90.6 82.9 113.5 99.9 93.5
7 | 23 | 122 SHC 54.4 65.4 76.0 61.2 76.6 82.9 68.6 90.1 93.5
7 | 24 | kW 13.03 12.55 12.11 13.28 12.82 12.56 13.39 12.96 12.78
7 | 29 | 50TJS014 (12.5 TONS)
7 | 30 | Evaporator Air Quantity — Cfm/BF
7 | 31 | Temp (F) Air
7 | 32 | 3750/0.10 4500/0.125 5000/0.15 6250/0.15
7 | 33 | Entering
7 | 34 | Condenser (Edb) Evaporator Air — Ewb (F)
7 | 35 | 72 67 62 72 67 62 72 67 62 72 67 62
7 | 36 | TC 166.5 153.9 141.5 171.7 158.8 146.3 173.5 161.5 148.3 181.1 169.0 156.5
7 | 37 | 75 SHC 81.2 101.8 121.5 86.7 110.2 133.1 89.3 115.9 139.0 98.8 130.9 155.5
7 | 38 | kW 9.96 9.68 9.40 10.06 9.78 9.49 10.15 9.87 9.49 10.25 9.96 9.68
7 | 39 | TC 160.6 147.7 133.3 165.2 152.5 139.4 167.8 154.6 142.0 175.6 161.8 150.8
7 | 40 | 85 SHC 79.6 99.4 117.6 85.0 108.0 130.0 87.9 113.6 136.2 97.6 129.1 150.5
7 | 41 | kW 10.81 10.43 10.15 10.90 10.62 10.34 11.00 10.72 10.34 11.19 10.81 10.53
7 | 42 | TC 153.6 141.2 125.2 158.2 145.6 131.9 160.8 147.7 135.4 167.6 154.3 144.8
7 | 43 | 95 SHC 77.2 96.7 113.7 82.6 105.4 126.3 86.0 111.2 133.0 95.1 126.6 144.8
7 | 44 | kW 11.66 11.28 10.90 11.84 11.47 11.09 11.94 11.56 11.19 12.03 11.66 11.37
7 | 45 | TC 146.9 134.0 116.7 150.6 137.9 123.5 152.7 140.0 128.0 159.9 146.3 138.6
7 | 46 | 105 SHC 75.0 94.1 109.5 80.1 102.6 121.5 83.3 108.4 127.9 93.5 123.7 138.5
7 | 47 | kW 12.60 12.13 11.75 12.69 12.31 11.84 12.78 12.41 11.94 12.97 12.50 12.22
7 | 48 | TC 128.7 116.4 99.5 132.4 120.6 107.7 134.0 122.7 112.5 139.3 128.1 122.1
7 | 49 | 115 SHC 67.0 84.2 97.1 71.9 92.6 107.6 74.8 98.2 112.4 83.4 112.2 122.0
7 | 50 | kW 13.87 13.39 12.90 14.07 13.58 13.10 14.07 13.68 13.19 14.16 13.77 13.48
7 | 51 | TC 115.9 104.0 87.5 119.7 108.5 96.7 121.0 110.5 101.7 124.9 115.3 110.5
7 | 52 | 122 SHC 61.5 77.3 88.4 66.2 85.6 97.9 68.9 91.1 101.6 76.3 104.1 110.4
7 | 53 | kW 14.76 14.27 13.71 15.03 14.47 13.97 14.96 14.57 14.07 15.00 14.66 14.37
7 | 56 | LEGEND hIdb = hedb - Total capacity (Btuh)
7 | 57 | 4.5 x cfm
7 | 58 | BF – Bypass factor Where: hewb = Enthalpy of air entering evaporator coil
7 | 59 | Edb – Entering Dry-Bulb 3. The SHC is based on 80 F edb temperature of air entering
7 | 60 | Ewd – Entering Wet-Bulb evaporator coil.
7 | 61 | KW – Compressor Motor Power Input Below 80 F edb, subtract (corr factor x cfm) from SHC.
7 | 62 | Idb – Leaving Dry-Bulb Above 80 F edb, add (corr factor x cfm) to SHC.
7 | 63 | Iwb – Leaving Wet-Bulb ENTERING AIR DRY-BULB TEMP (F)
7 | 64 | SHC – Sensible Heat Capacity (1000 Rtuh) Gross BYPASS
7 | 65 | 79 78 77 76 75 Under 75
7 | 66 | TC – Total Capacity (1000 Btuh) Gross FACTOR
7 | 67 | (BF) 81 82 83 84 85 Over 85
7 | 68 | NOTES: Correction factor
7 | 69 | 1. Direct interpolation is permissible. Do not extrapolate. .05 1.04 2.07 3.11 4.14 5.18
7 | 70 | Use formula
7 | 71 | 2. the following formulas may be used: .10 .98 1.96 2.94 3.92 4.90
7 | 72 | shown
7 | 73 | .20 .87 1.74 2.62 3.49 4.36
7 | 74 | below.
7 | 75 | Sensible capacity (Btuh) .30 .76 1.53 2.29 3.05 3.82
7 | 76 | tIdb = tedb -
7 | 77 | 1.10 x cfm Interpolation is permissible.
7 | 78 | TIwb = Wet-bulb temperature corresponding to enthalpy of Correction factor = 1.10 x (1-BF) x (edb – 80)
7 | 79 | air leaving evaporator coil.
7 | 84 | 7

## Cooling_Ratings
Model | Nominal tons | Standard CFM | Gross cooling capacity Btuh | Net cooling capacity Btuh | Input kW | EER | Sound rating Bels | Source page | Rating basis
50LJS007 | 6 | 2200 | 67600 | 65000 | 6.6 | 9.8 | 8.4 | 3 | ARI 210/240-89 or 360-86 and 270-84
50TJS008 | 7 | 2800 | 85300 | 82200 | 9.8 | 8.4 | 8.6 | 3 | ARI 210/240-89 or 360-86 and 270-84
50TJS009 | 9 | 3000 | 106600 | 103200 | 10.9 | 9.5 | 8.6 | 3 | ARI 210/240-89 or 360-86 and 270-84
50TJS012 | 10 | 4000 | 122500 | 117350 | 13.4 | 8.8 | 8.8 | 3 | ARI 210/240-89 or 360-86 and 270-84
50TJS014 | 12 | 4750 | 146700 | 138050 | 14.1 | 9.8 | 8.8 | 3 | ARI 210/240-89 or 360-86 and 270-84

## Audit_Corrections
Item | Finding / correction | Action taken | Source reference
Electrical_Data / 50LJS007 | Disconnect LRA was represented as 0 in Excel; PDF shows a dash. | Corrected to text value "—" for all 50LJS007 heater rows. | PDF page 16; Electrical_Data
50TJS014 capacity | Cover and page 7 title say 12.5 tons; ARI and Physical Data rate the model at 12 / 12.0 TR. | Kept the technical rating as 12 tons in structured model/rating sheets; 12.5 is documented as the cover/section labeling discrepancy, not overwritten. | PDF pages 1, 3, 4, 7
Blower OCR | Some extracted blower rows contain apparent OCR/transcription anomalies, e.g. 1990 vs 1090 in 50LJS007 at 2000 CFM / ESP 1.0. | Raw extracted text is intentionally unchanged; flagged for visual verification against the PDF image. | PDF page 10; Blower_Performance_Raw
Airflow_Summary / Evaporator coil rows (50TJS008, 50TJS009, 50TJS012) | Evaporator coil rows were 4 for all models; PDF shows 4 only for 50LJS007 and 50TJS014, and 3 rows for TJS008/009/012. | Corrected K3:K5 from 4 to 3. Matches Physical_English (Evaporator rows x fins/in). | PDF pages 4 and 5; Airflow_Summary
Physical_SI P2 and Airflow_Summary D2 / 50LJS007 evaporator airflow L/s | Value was 1.38 L/s (typo carried over from PDF page 5). 2200 CFM x 0.4719 = 1038 L/s, consistent with the TJS models (e.g. 2800 CFM = 1321 L/s). | Corrected 1.38 to 1038 in both sheets. | PDF pages 3, 4, 5; Physical_SI; Airflow_Summary
Electrical_Data / Source page | Source page listed 16-21 by heater row; the whole electrical table is on PDF page 16 only. | Set Source page to 16 for all 30 rows. | PDF page 16; Electrical_Data

## Dimensions_50TJS008_014
Model | Corner A lb | Corner A kg | Corner B lb | Corner B kg | Corner C lb | Corner C kg | Corner D lb | Corner D kg | Dimension H ft-in | Dimension H mm | Dimension J ft-in | Dimension J mm | Dimension K ft-in | Dimension K mm | Source page
50TJS008 | 164 | 74 | 140 | 64 | 208 | 94 | 243 | 110 | 1-2 7/8 | 378 | 3-5 5/16 | 1050 | 2-9 11/16 | 856 | 9
50TJS009 | 165 | 75 | 141 | 64 | 209 | 94 | 245 | 111 | 3-3 7/8 | 1013 | 3-5 5/16 | 1050 | 2-9 11/16 | 856 | 9
50TJS012 | 199 | 90 | 170 | 77 | 252 | 114 | 294 | 134 | 2-5 7/8 | 759 | 4-5 1/16 | 1253 | 3-0 3/8 | 924 | 9
50TJS014 | 202 | 92 | 172 | 78 | 256 | 116 | 300 | 136 | 1-2 7/8 | 378 | 4-5 1/16 | 1253 | 3-0 3/8 | 924 | 9

## Dimension_Callouts_Page9
Callout | Imperial | Metric | View / context
Overall/base plan length | 7-3 3/8 in | 2219 mm | Front plan view
Overall/base plan height | 4-9 3/4 in | 1467 mm | Left-side plan view
Outdoor-air hood width | 2-11 1/2 in | 902 mm | Rear view
Rear offset | 0-3 9/16 in | 90 mm | Rear view
Hood vertical dimension | 1-5 7/8 in | 454 mm | Rear/right-side view
Evaporator coil/fan reference | 1-11 1/4 in | 591 mm | Plan view
Front plan offset | 3-4 1/4 in | 1022 mm | Plan view
Supply-air opening width | 2-4 5/16 in | 719 mm | Right-side view
Supply-air opening height | 1-1 7/8 in | 352 mm | Right-side view
Supply-air lower offset | 0-7 in | 178 mm | Right-side view
Return-air/outdoor-air spacing | 3-1 in | 940 mm | Right-side view
Outdoor-air opening height | 2-2 7/16 in | 671 mm | Right-side view
Condensate drain reference | 1-0 5/8 in | 320 mm | Right-side view
Bottom offset | 0-4 9/16 in | 116 mm | Left-side view
Base rail reference | 0-7 3/8 in | 187 mm | Left-side view
Base rail/front offset | 0-5 3/4 in | 146 mm | Left-side view
Electrical location reference | 2-0 3/8 in | 619 mm | Left-side view
Base rail/forklift reference | 0-2 1/4 in | 57 mm | Front view (typ. 8 places)
Connection sizes (page 9)
Letter | Size | Metric | Description
A | 1-3/8 in diameter | 35 mm | Field power supply hole
B | 2-1/2 in diameter | 64 mm | Power supply knock-out
C | 1-3/4 in diameter | 44 mm | Charging port hole
D | 7/8 in diameter | 22 mm | Field control wiring hole
E | 3/4-14 NPT | — | Standard condensate drain
F | 2 in diameter | 51 mm | Power supply knock-out

## Page9_Visual_Reference
Reference | Details
Source page | PDF page 9: Base unit dimensions — 50TJS008-014
Weight note | Weights are for the unit only (aluminum plate fins) and do not include options or crating.
Dimension note | Dimensions in the drawing are in inches; bracketed values are millimeters.
Model coverage | Corner-weight and H/J/K table covers 50TJS008, 009, 012, and 014.
Visual source | The full page 9 drawing is embedded below for visual verification.

## Dimensions_50LJS007
Model | Standard unit weight lb | Standard unit weight kg | Economizer weight lb | Economizer weight kg | Corner A lb | Corner A kg | Corner B lb | Corner B kg | Corner C lb | Corner C kg | Corner D lb | Corner D kg | Source page
50LJS007 | 520 | 236 | 34 | 15.4 | 108 | 49 | 88 | 40 | 145 | 65.8 | 178 | 80.7 | 8

## Dimension_Callouts_Page8
Callout | Imperial | Metric | View / context
Outdoor-air hood width | 2-0 15/16 in | 633 mm | Rear view
Rear offset | 0-4 1/2 in | 114 mm | Rear view
Hood vertical dimension | 1-4 3/8 in | 416 mm | Rear/right-side view
Condenser section width | 3-3/16 in | 919 mm | Plan view
Overall/base height | 3-9 in | 1144 mm | Plan view
Evaporator coil reference | 1-5 in | 432 mm | Plan view
Front plan offset | 2-9 in | 838 mm | Plan view
Overall/base length | 6-1 11/16 in | 1872 mm | Plan view
Supply-air opening width | 1-5 5/16 in | 440 mm | Right-side view
Supply-air opening height | 0-11 7/8 in | 302 mm | Right-side view
Outdoor-air opening height | 2-1 1/16 in | 652 mm | Right-side view
Return-air opening height | 1-1 1/4 in | 336 mm | Right-side view
Condensate drain reference | 0-7 in | 178 mm | Right-side view
Right-side plan length | 2-1 15/16 in | 659 mm | Right-side view
Right-side return offset | 0-10 13/16 in | 275 mm | Right-side view
Left-side overall height | 2-9 5/16 in | 847 mm | Left-side view
Bottom offset | 0-4 9/16 in | 116 mm | Left-side view
Base rail reference | 0-7 3/8 in | 187 mm | Left-side view
Electrical location reference | 1-4 5/16 in | 415 mm | Left-side view
Electrical lower reference | 1-2 1/4 in | 362 mm | Left-side view
Electrical side offset | 0-3 13/16 in | 97 mm | Left-side view
Forklift slots | 0-2 1/4 in | 57 mm | Front view (typ. 8 places)
Connection sizes (page 8)
Letter | Size | Metric | Description
A | 1-3/8 in diameter | 35 mm | Field power supply hole
B | 2-1/2 in diameter | 64 mm | Power supply knock-out
C | 1-3/4 in diameter | 44 mm | Charging port hole
D | 7/8 in diameter | 22 mm | Field control wiring hole
E | 3/4-14 NPT | — | Standard condensate drain
F | 2 in diameter | 51 mm | Power supply knock-out

## Page8_Visual_Reference
Reference | Details
Source page | PDF page 8: Base unit dimensions — 50LJS007
Weight note | Weights are for the unit only; economizer weight is listed separately. Options and crating are not included.
Dimension note | Dimensions in the drawing are in inches; bracketed values are millimeters.
Model coverage | This page applies to 50LJS007 only.
Connection sizes | The A-F connection sizes are the same connection-size schedule shown on the page.
Visual source | The full page 8 drawing is embedded below for visual verification.

## Pressure_Switches
Device | Setting / function | Model applicability | English value | SI value | Source
High pressure switch | Standard compressor IPRV setting | All models | 400–500 psig | 2758–3448 kPa | Physical data pages 4–5
High pressure switch | Cutout / reset (automatic) | All models | 463–477 / 300–340 psig | 3192–3289 / 2068–2344 kPa | Physical data pages 4–5
Low pressure switch | Cutout / reset (manual) | 50LJS007 | 4–10 / 17–27 psig | 28–69 / 117–186 kPa | Physical data pages 4–5
Low pressure switch | Cutout / reset (manual) | 50TJS008–014 | 14 / 20–30 psig | 97 / 138–207 kPa | Physical data pages 4–5
Freeze-protection switch | Opens / closes | All models | 25–35 / 40–50 °F | −4 to 1.66 / 4.44 to 10 °C | Physical data pages 4–5

## Nomenclature
Code category | Code | Meaning | Source
Prefix | 50 | Cooling only / cooling with optional field-installed electric heat | Page 2
Size family | LJ | Constant volume, size 007 | Page 2
Size family | TJ | Constant volume, size 008–014 | Page 2
Brand/series | S | SAMCO | Page 2
Capacity code | 007 | 6 tons (21 kW) | Page 2
Capacity code | 008 | 7 tons (24.6 kW) | Page 2
Capacity code | 009 | 9 tons (31.7 kW) | Page 2
Capacity code | 012 | 10 tons (35 kW) | Page 2
Capacity code | 014 | 12 tons (44 kW) | Page 2
Packaging | 1 | Standard | Page 2
Packaging | 3 | Export | Page 2
Design series | 3 | Fixed-orifice expansion | Page 2
Voltage code | 9 | 400/420-3-50 | Page 2
Coil fin option | — | Aluminum evaporator and aluminum condenser | Page 2
Coil fin option | P | Pre-coated condenser coil (aluminum fins) | Page 2
Suffix | NE | Standard unit, size 007 | Page 2
Suffix | SR | Standard unit, size 008–024 | Page 2