## README
Carrier Miraco 50UB / 38BB / 40AB — HVAC Selection Database
Purpose: this workbook is a structured database of every model, capacity table and physical/electrical
spec published in the Carrier Miraco Technical Manual (Air Cooled Vertical Packaged / Split, R22, June 2013),
so it can be used to cross-check a Carrier HAP (Hourly Analysis Program) simulation report and select the
correct unit automatically.
How to use it:
1. Open 'Selection Helper' and enter your HAP results (design total cooling load in Btu/hr or kW, the
entering air Wet Bulb/Dry Bulb at the evaporator, the outdoor (condenser entering) design dry bulb,
and the design supply/evaporator airflow in cfm).
2. The sheet automatically searches 'Cooling_Capacity_Data' for the smallest unit size whose capacity
at the nearest tabulated condition meets or exceeds your HAP load, and reports the match.
3. Cross-check the candidate against 'Physical_Condensing', 'Physical_Evaporator' and 'Electrical_Data'
for space, weight and power constraints before finalizing the selection.
Sheets in this workbook:
- Model_List : all model number combinations (Vertical Packaged / Split, Cool-only / Cool-Heat)
- System_Technical_Data : nominal capacity, refrigerant charge, circuits, piping sizes, heating capacity
- Cooling_Capacity_Data : FULL capacity tables (Total capacity, Input power, Sensible capacity) at every
tabulated Evap WB/DB and Condenser entering temperature, for all 7 sizes
- Airflow_Multipliers : correction multipliers when actual evaporator airflow differs from nominal
- Physical_Condensing : 38BB condensing unit physical/mechanical data
- Physical_Evaporator : 40AB evaporator unit physical/mechanical data
- Electrical_Data : full system electrical data (consumption, amps, fuses, wiring)
- General_Specs : narrative specs (materials, safety features, options, standards) for reference
- Selection_Helper : INPUT your HAP data here -> get the recommended model
IMPORTANT — data-entry accuracy note:
A handful of cells in the original PDF's Sensible Capacity tables (pages 14-20) contain values that break
the otherwise smooth/monotonic trend of their row or column (e.g. a sudden large jump). These are almost
certainly print/typesetting errors in the source catalog, NOT transcription errors here. Every such cell has
been reproduced EXACTLY as printed and is highlighted in red fill with a comment in 'Cooling_Capacity_Data'.
Do not use those specific cells for a final selection — cross-check with the neighboring rows/columns or
contact Carrier/Miraco for a corrected table if the design condition falls on one of them.
All units are as printed in the source: R22 refrigerant, capacities in Btu/hr and kW, dimensions in mm,
weights in kg, airflow in m3/hr (physical data tables) or cfm (capacity tables) exactly as tabulated.
═══════════════════════════════════════════════════════════════
CORRECTIONS APPLIED IN v2 (engineering review vs. original build)
═══════════════════════════════════════════════════════════════
A) PHYSICAL DATA CORRECTIONS
38BB-190 Condenser Coil Rows-Tube Diam.: corrected 5-3/8" → 5-5/8"
40AB-250 Evaporator Coil Rows-Tube Diam.: corrected 5-1/2" → 6-1/2"
(Cells highlighted orange in the respective Physical_* sheets.)
Verify against nameplate if the original printed PDF is unclear.
B) MODEL NAMING — 38UB/40UB vs 38BB/40AB
The original PDF's page-1 model-list section uses '38UB' and '40UB' in individual model
numbers, while the rest of the manual and the product cover use '38BB' and '40AB'.
This workbook now uses 38BB/40AB throughout (Model_List corrected in v2).
The Selection_Helper recommendation (Step 4) now looks up the exact model name from
Model_List and shows both Cool/Heat (-E) and Cool Only (-K) variants.
C) COMPLETE LIST OF ANOMALOUS (PINK) CELLS IN Cooling_Capacity_Data
All cells below break the expected monotonic trend of their row or column.
They are highlighted pink in Cooling_Capacity_Data. Do NOT use for final selection.
# Size WB DB Cond Sensible (Btu/hr) Issue
1. 110 15 24 46 94515 Sudden jump vs. Cond43=79265 and prior DB23/Cond46=71345
2. 110 17 21 46 114235 Jump vs. Cond43=53300 (value copied from WB19/DB27/Cond46)
3. 110 21 28 46 72680 ← ADDED v2 Higher than Cond43=70290; identical to DB29/Cond46
4. 145 19 28 35 88135 Drop vs. DB28/Cond30=125630 and DB28/Cond40=118910
5. 145 21 28 46 94515 Drop vs. Cond43=98540
6. 250 21 25 40 96935 Drop vs. Cond35=111235 then slight rise at Cond43=95915
7. 300 19 25 40 167735 Apparent anomaly — but trend is monotonic; mark for review
8. 300 21 25 40 117305 Large drop vs. Cond35=134605; Cond43=116045 only -1260
CORRECTIONS TO EARLIER README NOTES (pre-v2):
- 'Size 145, WB21/DB28, Cond46: sensible=72680' was wrong. Correct is Size 110 (#3 above).
The actual Size 145/WB21/DB28/Cond46 value is 94515 (#5 above).
- 'Size 300, WB19/DB25, Cond40: sensible=117305' was wrong. Correct is WB21/DB25 (#8 above).
The Size 300/WB19/DB25/Cond40 value is 167735 (#7 above — marked for review but may be valid).
D) AIRFLOW CONFLICT FOR SIZE 300 — IMPORTANT
Two different nominal airflow values for Size 300 appear in the same PDF source:
• Cooling_Capacity_Data header: 9500 cfm (printed at top of page 20 capacity table)
• Airflow_Multipliers point-3 (100%): 8752 cfm (printed in the multiplier footnote, page 20)
This internal contradiction exists in the original printed catalog — it is NOT a transcription error.
Impact on Selection_Helper: Step 3 column D shows 9500 cfm for Size 300 (from Cooling_Capacity_Data).
The Airflow_Ratio formula divides by 9500, but the multiplier table treats 8752 as 100%.
Resolution: use 9500 cfm as the nominal when comparing HAP airflow for initial selection;
then apply the Airflow_Multipliers table (with 8752 as its own reference) for capacity correction.
Contact Carrier/Miraco for clarification before final sign-off on a size-300 project.
E) EVAPORATOR DRY BULB (DB) IN SELECTION_HELPER
The 'Evaporator Entering Air — Dry Bulb' (B8) input is NOT used in the Total Capacity lookup.
The catalog Total Capacity table is published at a fixed base DB for each WB; the SUMIFS formula
matches only on WB and Condenser temperature. Sensible capacity does depend on DB, but Sensible
comparison is not automated in this sheet — verify Sensible manually from Cooling_Capacity_Data
if the project is Sensible-load-driven (e.g. server room, lab, very low outside-air fraction).
═══════════════════════════════════════════════════════════════
CORRECTIONS APPLIED IN v3 (verified line-by-line against the source PDF)
═══════════════════════════════════════════════════════════════
F) Cooling_Capacity_Data — footer notes were out of sync with the corrected anomaly list (section C):
- The bullet that said 'Size 145, WB21/DB28, Cond46: 72680' was wrong; corrected to Size 110 (page 16).
- The bullet that said 'Size 300, WB19/DB25, Cond40: 117305' was wrong; that value belongs to WB21/DB25.
Corrected to state the true WB19/DB25/Cond40 value (167735, page 20, flagged for review but may be valid).
- Added the missing bullet for Size 145, WB21/DB28, Cond46 = 94515 (page 17).
All 8 pink-highlighted cells in Cooling_Capacity_Data already matched the corrected list; only the
plain-text summary bullets underneath needed updating.
G) Model_List — column H duplicated column A exactly (both "Nominal Size"). Relabeled to
'Catalog MBH (= Col. A, kept for reference)' and converted to a formula (=A4 etc.) so it can never drift out of sync.
H) Selection_Helper — added a Unit Type Preference input (cell B11: "E" for Cool/Heat or "K" for Cool Only,
defaults to E if left blank). Step 4 recommended-model cells (B33:B35) now return only the selected
variant instead of always showing both "-E / -K" together.
NOTE — one item from an earlier draft review was checked and found NOT supported by the PDF:
a claim that 38BB-190's compressor Power Supply is '380-440V' rather than '380-400V'. Page 9 of the
PDF lists Power Supply as 380-400 V/3Ph/50Hz for ALL sizes, including 190 — this was left unchanged.
(What does vary by size is 'Minimum Volts': 340V for sizes 190/250/300 vs 360V for 55-145, with
'Maximum Volts' at 440V for every size — not currently broken out in Physical_Condensing.)

## Selection_Helper
Selection Helper — Match a HAP Report to the Correct Carrier Miraco Unit
Enter your HAP design results in the yellow cells below. Formulas search the Cooling_Capacity_Data sheet for the closest tabulated condition and the smallest unit size that meets your load.
STEP 1 — Enter HAP Design Results
Required Total Cooling Load | 145000 | Btu/hr
(leave blank if entering kW instead) |  | kW
Evaporator Entering Air — Wet Bulb | 19 | °C
Evaporator Entering Air — Dry Bulb | 24 | °C
Condenser Entering Air Temp (outdoor design DB) | 43 | °C
Design Evaporator Airflow (optional, cfm) |  | cfm
Unit Type Preference (E = Cool/Heat, K = Cool Only) | E | 'E' or 'K'
Effective Required Load (Btu/hr) | 145000 | Btu/hr
STEP 2 — Nearest Tabulated Test Condition (auto-matched)
Nearest catalog Evap. WB (°C) | 19
Nearest catalog Condenser Entering Temp (°C) | 43
Note: array formulas above use LibreOffice/Excel legacy CSE-compatible array constants; if a cell shows an error, select it, retype, and confirm with Ctrl+Shift+Enter (older Excel).
STEP 3 — Capacity of Each Size at the Matched Condition
Unit Size | Total Capacity (Btu/hr) @ matched WB/DB/Cond | Meets Load? | Nominal Airflow (cfm) | Airflow Ratio (Design/Nominal) | Notes
55 | 48520 | no | 2005
90 | 76330 | no | 3010
110 | 96980 | no | 3540
145 | 130000 | no | 6020
190 | 166650 | YES | 6020
250 | 220570 | YES | 7080
300 | 267300 | YES | 9500 |  | NOTE: Size 300 nominal airflow conflict — capacity table uses 9500 cfm but multiplier table treats 8752 cfm as 100%. See README section D.
Note: capacity shown is read directly from the printed table at the nearest tabulated WB/DB/Condenser-temp combination (no interpolation between rows), matching how the catalog itself is meant to be read. If your HAP condition falls between two tabulated points, check both neighboring rows in Cooling_Capacity_Data manually for a conservative selection.
STEP 4 — Recommended Model
Recommended Nominal Size (MBH) | 190
Recommended Vertical Packaged Model | 50UB 180-E
Recommended Condensing Unit Model | 38BB 180-E
Recommended Evaporator Unit Model | 40AB 180-E
Capacity Delivered at This Condition (Btu/hr) | 166650
Safety Margin (%) | 14.93%
IMPORTANT: this automatic match uses the nearest tabulated catalog condition, not true bilinear interpolation, and picks the smallest size with Total Capacity ≥ your load at that single condition — exactly how a manual catalog lookup would be done. For a borderline result (safety margin under ~3%), or if your HAP WB/DB/condenser-temp values fall roughly halfway between two tabulated points, manually check the neighboring rows in Cooling_Capacity_Data, verify against Sensible capacity if the application is sensible-load-driven (e.g. no outside air / high internal loads), and confirm against Physical_Condensing / Physical_Evaporator / Electrical_Data for space, weight and power constraints before finalizing. This sheet narrows the choice quickly; final sign-off should still be a human engineering check.

## Model_List
1. Model Designation and Unit Models
Nominal Size (MBH) | Vertical Packaged Cool/Heat | Vertical Packaged Cool Only | Condensing Unit Cool/Heat | Condensing Unit Cool Only | Evaporator Unit Cool/Heat | Evaporator Unit Cool Only | Catalog MBH (= Col. A, kept for reference)
55 | 50UB 55-E | 50UB 55-K | 38BB 55-E | 38BB 55-K | 40AB 55-E | 40AB 55-K | 55
90 | 50UB 90-E | 50UB 90-K | 38BB 90-E | 38BB 90-K | 40AB 90-E | 40AB 90-K | 90
110 | 50UB 110-E | 50UB 110-K | 38BB 110-E | 38BB 110-K | 40AB 110-E | 40AB 110-K | 110
145 | 50UB 145-E | 50UB 145-K | 38BB 145-E | 38BB 145-K | 40AB 145-E | 40AB 145-K | 145
190 | 50UB 180-E | 50UB 180-K | 38BB 180-E | 38BB 180-K | 40AB 180-E | 40AB 180-K | 190
250 | 50UB 240-E | 50UB 250-K | 38BB 240-E | 38BB 250-K | 40AB 240-E | 40AB 250-K | 250
300 | 50UB 300-E | 50UB 300-K | 38BB 300-E | 38BB 300-K | 40AB 300-E | 40AB 300-K | 300
Source: Carrier Miraco Technical Manual 50UB/38BB/40AB (June 2013), all values as printed in the original PDF.
Note (v2 corrected): catalog model codes use the series prefix directly — 38BB (Condensing) and 40AB (Evaporator). Page 1 of the PDF lists individual models as '38UB xx-E/K' and '40UB xx-E/K' which is a known catalog typo/inconsistency — the correct designations are 38BB and 40AB as shown on the product cover and throughout Section 6/7. For size 190: model number uses '180' (e.g. 50UB 180-E) while nominal capacity is 190 MBH. For size 250: Cool/Heat uses '240' (50UB 240-E / 38BB 240-E / 40AB 240-E) while Cool Only uses '250' (50UB 250-K / 38BB 250-K / 40AB 250-K). Both reproduced exactly as per catalog.

## System_Technical_Data
5. System Technical Data
Size (MBH) | Vertical Packaged Model | Condensing Unit Model | Evaporator Unit Model | Nominal Cooling Capacity (Btu/hr) | Nominal Cooling Capacity (kW) | Refrigerant | Total Charge - Vertical Packaged (kg) | No. of Refrigerant Circuits | Suction Line (Dia-Qty) | Liquid Line (Dia-Qty) | Heating Capacity (kW)
55 | 50UB-55 | 38BB-55 | 40AB-55 | 54500 | 15.97 | R22 | 4.3 | 1 | 7/8"-1 | 1/2"-1 | 6
90 | 50UB-90 | 38BB-90 | 40AB-90 | 85700 | 25.12 | R22 | 4.5 | 1 | 1-1/8"-1 | 1/2"-1 | 15
110 | 50UB-110 | 38BB-110 | 40AB-110 | 109000 | 31.95 | R22 | 2 x 4.3 | 2 | 7/8"-2 | 1/2"-2 | 15
145 | 50UB-145 | 38BB-145 | 40AB-145 | 144000 | 42.2 | R22 | 2 x 5.1 | 2 | 1-1/8"-2 | 1/2"-2 | 18
190 | 50UB-190 | 38BB-190 | 40AB-190 | 186000 | 54.51 | R22 | 2 x 6.5 | 2 | 1-1/8"-2 | 1/2"-2 | 18
250 | 50UB-250 | 38BB-250 | 40AB-250 | 246000 | 72.1 | R22 | 2 x 9.5 | 2 | 1-1/8"-2 | 5/8"-2 | 22.5
300 | 50UB-300 | 38BB-300 | 40AB-300 | 298000 | 87.34 | R22 | 2 x 11 | 2 | 1-3/8"-2 | 7/8"-2 | 24
Source: Carrier Miraco Technical Manual 50UB/38BB/40AB (June 2013), all values as printed in the original PDF.
Refrigerant Control: Expansion Valve (all sizes). Drain Line ID: 3/4" (all sizes).
Cooling capacity basis: 27/19°C DBT/WBT return air to evaporator unit, 100% nominal evaporator air flow, 35°C outdoor ambient temperature.

## Cooling_Capacity_Data
9. Cooling Capacities (full tables, pages 14-20)
One row per (Unit Size, Evap. Entering WB, Evap. Entering DB, Condenser Entering Temp). Sensible capacity DB list differs slightly from the Total-capacity base DB — both captured.
Unit Size | Evap. Air Flow (cfm, nominal) | Evap. Entering WB (°C) | Evap. Entering DB (°C) | Condenser Entering Air Temp (°C) | Total Capacity (Btu/hr) | Total Capacity (kW) | Total Input Power (kW) | Sensible Capacity (Btu/hr) | Sensible Capacity (kW) | Row Type | Notes
55 | 2005 | 15 | 18 | 25 | 53555 | 15.7 | 6.56 |  |  | Total+Input
55 | 2005 | 15 | 18 | 30 | 50555 | 14.82 | 7.09 |  |  | Total+Input
55 | 2005 | 15 | 18 | 35 | 46965 | 13.76 | 7.61 |  |  | Total+Input
55 | 2005 | 15 | 18 | 40 | 43825 | 12.84 | 8.13 |  |  | Total+Input
55 | 2005 | 15 | 18 | 43 | 41715 | 12.23 | 8.44 |  |  | Total+Input
55 | 2005 | 15 | 18 | 46 | 39600 | 11.61 | 8.76 |  |  | Total+Input
55 | 2005 | 15 | 18 | 25 |  |  |  | 30335 | 8.89 | Sensible
55 | 2005 | 15 | 18 | 30 |  |  |  | 28765 | 8.43 | Sensible
55 | 2005 | 15 | 18 | 35 |  |  |  | 27160 | 7.96 | Sensible
55 | 2005 | 15 | 18 | 40 |  |  |  | 25590 | 7.5 | Sensible
55 | 2005 | 15 | 18 | 43 |  |  |  | 23680 | 6.94 | Sensible
55 | 2005 | 15 | 18 | 46 |  |  |  | 21770 | 6.38 | Sensible
55 | 2005 | 15 | 19 | 25 |  |  |  | 33100 | 9.7 | Sensible
55 | 2005 | 15 | 19 | 30 |  |  |  | 31530 | 9.24 | Sensible
55 | 2005 | 15 | 19 | 35 |  |  |  | 29925 | 8.77 | Sensible
55 | 2005 | 15 | 19 | 40 |  |  |  | 28355 | 8.31 | Sensible
55 | 2005 | 15 | 19 | 43 |  |  |  | 26445 | 7.75 | Sensible
55 | 2005 | 15 | 19 | 46 |  |  |  | 24535 | 7.19 | Sensible
55 | 2005 | 15 | 20 | 25 |  |  |  | 35895 | 10.52 | Sensible
55 | 2005 | 15 | 20 | 30 |  |  |  | 34295 | 10.05 | Sensible
55 | 2005 | 15 | 20 | 35 |  |  |  | 32725 | 9.59 | Sensible
55 | 2005 | 15 | 20 | 40 |  |  |  | 31120 | 9.12 | Sensible
55 | 2005 | 15 | 20 | 43 |  |  |  | 29210 | 8.56 | Sensible
55 | 2005 | 15 | 20 | 46 |  |  |  | 27300 | 8 | Sensible
55 | 2005 | 15 | 21 | 25 |  |  |  | 38660 | 11.33 | Sensible
55 | 2005 | 15 | 21 | 30 |  |  |  | 36510 | 10.7 | Sensible
55 | 2005 | 15 | 21 | 35 |  |  |  | 35485 | 10.4 | Sensible
55 | 2005 | 15 | 21 | 40 |  |  |  | 33920 | 9.94 | Sensible
55 | 2005 | 15 | 21 | 43 |  |  |  | 32005 | 9.38 | Sensible
55 | 2005 | 15 | 21 | 46 |  |  |  | 30095 | 8.82 | Sensible
55 | 2005 | 15 | 22 | 25 |  |  |  | 41460 | 12.15 | Sensible
55 | 2005 | 15 | 22 | 30 |  |  |  | 39855 | 11.68 | Sensible
55 | 2005 | 15 | 22 | 35 |  |  |  | 38285 | 11.22 | Sensible
55 | 2005 | 15 | 22 | 40 |  |  |  | 36680 | 10.75 | Sensible
55 | 2005 | 15 | 22 | 43 |  |  |  | 34805 | 10.2 | Sensible
55 | 2005 | 15 | 22 | 46 |  |  |  | 32930 | 9.65 | Sensible
55 | 2005 | 15 | 23 | 25 |  |  |  | 44220 | 12.96 | Sensible
55 | 2005 | 15 | 23 | 30 |  |  |  | 42650 | 12.5 | Sensible
55 | 2005 | 15 | 23 | 35 |  |  |  | 41050 | 12.03 | Sensible
55 | 2005 | 15 | 23 | 40 |  |  |  | 39515 | 11.58 | Sensible
55 | 2005 | 15 | 23 | 43 |  |  |  | 37570 | 11.01 | Sensible
55 | 2005 | 15 | 23 | 46 |  |  |  | 35690 | 10.46 | Sensible
55 | 2005 | 15 | 24 | 25 |  |  |  | 46985 | 13.77 | Sensible
55 | 2005 | 15 | 24 | 30 |  |  |  | 45415 | 13.31 | Sensible
55 | 2005 | 15 | 24 | 35 |  |  |  | 43815 | 12.84 | Sensible
55 | 2005 | 15 | 24 | 40 |  |  |  | 42245 | 12.38 | Sensible
55 | 2005 | 15 | 24 | 43 |  |  |  | 39615 | 11.61 | Sensible
55 | 2005 | 15 | 24 | 46 |  |  |  | 36990 | 10.84 | Sensible
55 | 2005 | 17 | 20 | 25 | 56895 | 16.67 | 6.71 |  |  | Total+Input
55 | 2005 | 17 | 20 | 30 | 54340 | 15.93 | 7.24 |  |  | Total+Input
55 | 2005 | 17 | 20 | 35 | 50750 | 14.87 | 7.76 |  |  | Total+Input
55 | 2005 | 17 | 20 | 40 | 46995 | 13.77 | 8.28 |  |  | Total+Input
55 | 2005 | 17 | 20 | 43 | 44985 | 13.18 | 8.59 |  |  | Total+Input
55 | 2005 | 17 | 20 | 46 | 42975 | 12.6 | 8.91 |  |  | Total+Input
55 | 2005 | 17 | 20 | 25 |  |  |  | 30540 | 8.95 | Sensible
55 | 2005 | 17 | 20 | 30 |  |  |  | 28935 | 8.48 | Sensible
55 | 2005 | 17 | 20 | 35 |  |  |  | 27365 | 8.02 | Sensible
55 | 2005 | 17 | 20 | 40 |  |  |  | 25765 | 7.55 | Sensible
55 | 2005 | 17 | 20 | 43 |  |  |  | 23885 | 7 | Sensible
55 | 2005 | 17 | 20 | 46 |  |  |  | 22010 | 6.45 | Sensible
55 | 2005 | 17 | 21 | 25 |  |  |  | 33305 | 9.76 | Sensible
55 | 2005 | 17 | 21 | 30 |  |  |  | 31735 | 9.3 | Sensible
55 | 2005 | 17 | 21 | 35 |  |  |  | 30130 | 8.83 | Sensible
55 | 2005 | 17 | 21 | 40 |  |  |  | 28560 | 8.37 | Sensible
55 | 2005 | 17 | 21 | 43 |  |  |  | 26650 | 7.81 | Sensible
55 | 2005 | 17 | 21 | 46 |  |  |  | 24740 | 7.25 | Sensible
55 | 2005 | 17 | 22 | 25 |  |  |  | 36100 | 10.58 | Sensible
55 | 2005 | 17 | 22 | 30 |  |  |  | 34500 | 10.11 | Sensible
55 | 2005 | 17 | 22 | 35 |  |  |  | 32930 | 9.65 | Sensible
55 | 2005 | 17 | 22 | 40 |  |  |  | 31395 | 9.2 | Sensible
55 | 2005 | 17 | 22 | 43 |  |  |  | 29415 | 8.62 | Sensible
55 | 2005 | 17 | 22 | 46 |  |  |  | 27435 | 8.04 | Sensible
55 | 2005 | 17 | 23 | 25 |  |  |  | 38900 | 11.4 | Sensible
55 | 2005 | 17 | 23 | 30 |  |  |  | 37295 | 10.93 | Sensible
55 | 2005 | 17 | 23 | 35 |  |  |  | 35690 | 10.46 | Sensible
55 | 2005 | 17 | 23 | 40 |  |  |  | 34120 | 10 | Sensible
55 | 2005 | 17 | 23 | 43 |  |  |  | 32210 | 9.44 | Sensible
55 | 2005 | 17 | 23 | 46 |  |  |  | 30300 | 8.88 | Sensible
55 | 2005 | 17 | 24 | 25 |  |  |  | 41630 | 12.2 | Sensible
55 | 2005 | 17 | 24 | 30 |  |  |  | 40060 | 11.74 | Sensible
55 | 2005 | 17 | 24 | 35 |  |  |  | 38455 | 11.27 | Sensible
55 | 2005 | 17 | 24 | 40 |  |  |  | 36885 | 10.81 | Sensible
55 | 2005 | 17 | 24 | 43 |  |  |  | 34975 | 10.25 | Sensible
55 | 2005 | 17 | 24 | 46 |  |  |  | 33065 | 9.69 | Sensible
55 | 2005 | 17 | 25 | 25 |  |  |  | 44425 | 13.02 | Sensible
55 | 2005 | 17 | 25 | 30 |  |  |  | 42825 | 12.55 | Sensible
55 | 2005 | 17 | 25 | 35 |  |  |  | 41255 | 12.09 | Sensible
55 | 2005 | 17 | 25 | 40 |  |  |  | 39650 | 11.62 | Sensible
55 | 2005 | 17 | 25 | 43 |  |  |  | 37740 | 11.06 | Sensible
55 | 2005 | 17 | 25 | 46 |  |  |  | 35830 | 10.5 | Sensible
55 | 2005 | 17 | 26 | 25 |  |  |  | 47190 | 13.83 | Sensible
55 | 2005 | 17 | 26 | 30 |  |  |  | 45620 | 13.37 | Sensible
55 | 2005 | 17 | 26 | 35 |  |  |  | 44015 | 12.9 | Sensible
55 | 2005 | 17 | 26 | 40 |  |  |  | 42450 | 12.44 | Sensible
55 | 2005 | 17 | 26 | 43 |  |  |  | 40535 | 11.88 | Sensible
55 | 2005 | 17 | 26 | 46 |  |  |  | 38625 | 11.32 | Sensible
55 | 2005 | 19 | 22 | 25 | 60270 | 17.66 | 6.86 |  |  | Total+Input
55 | 2005 | 19 | 22 | 30 | 57680 | 16.91 | 7.39 |  |  | Total+Input
55 | 2005 | 19 | 22 | 35 | 54500 | 15.97 | 7.91 |  |  | Total+Input
55 | 2005 | 19 | 22 | 40 | 50780 | 14.88 | 8.43 |  |  | Total+Input
55 | 2005 | 19 | 22 | 43 | 48520 | 14.22 | 8.74 |  |  | Total+Input
55 | 2005 | 19 | 22 | 46 | 46250 | 13.56 | 9.06 |  |  | Total+Input
55 | 2005 | 19 | 22 | 25 |  |  |  | 30745 | 9.01 | Sensible
55 | 2005 | 19 | 22 | 30 |  |  |  | 29140 | 8.54 | Sensible
55 | 2005 | 19 | 22 | 35 |  |  |  | 27570 | 8.08 | Sensible
55 | 2005 | 19 | 22 | 40 |  |  |  | 25970 | 7.61 | Sensible
55 | 2005 | 19 | 22 | 43 |  |  |  | 24055 | 7.05 | Sensible
55 | 2005 | 19 | 22 | 46 |  |  |  | 22145 | 6.49 | Sensible
55 | 2005 | 19 | 23 | 25 |  |  |  | 33510 | 9.82 | Sensible
55 | 2005 | 19 | 23 | 30 |  |  |  | 31770 | 9.31 | Sensible
55 | 2005 | 19 | 23 | 35 |  |  |  | 30370 | 8.9 | Sensible
55 | 2005 | 19 | 23 | 40 |  |  |  | 28730 | 8.42 | Sensible
55 | 2005 | 19 | 23 | 43 |  |  |  | 26855 | 7.87 | Sensible
55 | 2005 | 19 | 23 | 46 |  |  |  | 24980 | 7.32 | Sensible
55 | 2005 | 19 | 24 | 25 |  |  |  | 36340 | 10.65 | Sensible
55 | 2005 | 19 | 24 | 30 |  |  |  | 34705 | 10.17 | Sensible
55 | 2005 | 19 | 24 | 35 |  |  |  | 33100 | 9.7 | Sensible
55 | 2005 | 19 | 24 | 40 |  |  |  | 31495 | 9.23 | Sensible
55 | 2005 | 19 | 24 | 43 |  |  |  | 29620 | 8.68 | Sensible
55 | 2005 | 19 | 24 | 46 |  |  |  | 27740 | 8.13 | Sensible
55 | 2005 | 19 | 25 | 25 |  |  |  | 39070 | 11.45 | Sensible
55 | 2005 | 19 | 25 | 30 |  |  |  | 37465 | 10.98 | Sensible
55 | 2005 | 19 | 25 | 35 |  |  |  | 35865 | 10.51 | Sensible
55 | 2005 | 19 | 25 | 40 |  |  |  | 34260 | 10.04 | Sensible
55 | 2005 | 19 | 25 | 43 |  |  |  | 32380 | 9.49 | Sensible
55 | 2005 | 19 | 25 | 46 |  |  |  | 30505 | 8.94 | Sensible
55 | 2005 | 19 | 26 | 25 |  |  |  | 41835 | 12.26 | Sensible
55 | 2005 | 19 | 26 | 30 |  |  |  | 40265 | 11.8 | Sensible
55 | 2005 | 19 | 26 | 35 |  |  |  | 38625 | 11.32 | Sensible
55 | 2005 | 19 | 26 | 40 |  |  |  | 37025 | 10.85 | Sensible
55 | 2005 | 19 | 26 | 43 |  |  |  | 35145 | 10.3 | Sensible
55 | 2005 | 19 | 26 | 46 |  |  |  | 33270 | 9.75 | Sensible
55 | 2005 | 19 | 27 | 25 |  |  |  | 44630 | 13.08 | Sensible
55 | 2005 | 19 | 27 | 30 |  |  |  | 43030 | 12.61 | Sensible
55 | 2005 | 19 | 27 | 35 |  |  |  | 41390 | 12.13 | Sensible
55 | 2005 | 19 | 27 | 40 |  |  |  | 39785 | 11.66 | Sensible
55 | 2005 | 19 | 27 | 43 |  |  |  | 37910 | 11.11 | Sensible
55 | 2005 | 19 | 27 | 46 |  |  |  | 36035 | 10.56 | Sensible
55 | 2005 | 19 | 28 | 25 |  |  |  | 47395 | 13.89 | Sensible
55 | 2005 | 19 | 28 | 30 |  |  |  | 45825 | 13.43 | Sensible
55 | 2005 | 19 | 28 | 35 |  |  |  | 44155 | 12.94 | Sensible
55 | 2005 | 19 | 28 | 40 |  |  |  | 42585 | 12.48 | Sensible
55 | 2005 | 19 | 28 | 43 |  |  |  | 40675 | 11.92 | Sensible
55 | 2005 | 19 | 28 | 46 |  |  |  | 38765 | 11.36 | Sensible
55 | 2005 | 21 | 24 | 25 | 63285 | 18.55 | 7.01 |  |  | Total+Input
55 | 2005 | 21 | 24 | 30 | 60480 | 17.73 | 7.54 |  |  | Total+Input
55 | 2005 | 21 | 24 | 35 | 57505 | 16.85 | 8.06 |  |  | Total+Input
55 | 2005 | 21 | 24 | 40 | 53750 | 15.75 | 8.58 |  |  | Total+Input
55 | 2005 | 21 | 24 | 43 | 51685 | 15.15 | 8.89 |  |  | Total+Input
55 | 2005 | 21 | 24 | 46 | 49620 | 14.54 | 9.21 |  |  | Total+Input
55 | 2005 | 21 | 24 | 25 |  |  |  | 30915 | 9.06 | Sensible
55 | 2005 | 21 | 24 | 30 |  |  |  | 29345 | 8.6 | Sensible
55 | 2005 | 21 | 24 | 35 |  |  |  | 27740 | 8.13 | Sensible
55 | 2005 | 21 | 24 | 40 |  |  |  | 26175 | 7.67 | Sensible
55 | 2005 | 21 | 24 | 43 |  |  |  | 24260 | 7.11 | Sensible
55 | 2005 | 21 | 24 | 46 |  |  |  | 22350 | 6.55 | Sensible
55 | 2005 | 21 | 25 | 25 |  |  |  | 33715 | 9.88 | Sensible
55 | 2005 | 21 | 25 | 30 |  |  |  | 32110 | 9.41 | Sensible
55 | 2005 | 21 | 25 | 35 |  |  |  | 30505 | 8.94 | Sensible
55 | 2005 | 21 | 25 | 40 |  |  |  | 28935 | 8.48 | Sensible
55 | 2005 | 21 | 25 | 43 |  |  |  | 26820 | 7.86 | Sensible
55 | 2005 | 21 | 25 | 46 |  |  |  | 24705 | 7.24 | Sensible
55 | 2005 | 21 | 26 | 25 |  |  |  | 36510 | 10.7 | Sensible
55 | 2005 | 21 | 26 | 30 |  |  |  | 34905 | 10.23 | Sensible
55 | 2005 | 21 | 26 | 35 |  |  |  | 33270 | 9.75 | Sensible
55 | 2005 | 21 | 26 | 40 |  |  |  | 31700 | 9.29 | Sensible
55 | 2005 | 21 | 26 | 43 |  |  |  | 29585 | 8.67 | Sensible
55 | 2005 | 21 | 26 | 46 |  |  |  | 27470 | 8.05 | Sensible
55 | 2005 | 21 | 27 | 25 |  |  |  | 39275 | 11.51 | Sensible
55 | 2005 | 21 | 27 | 30 |  |  |  | 37670 | 11.04 | Sensible
55 | 2005 | 21 | 27 | 35 |  |  |  | 36035 | 10.56 | Sensible
55 | 2005 | 21 | 27 | 40 |  |  |  | 34465 | 10.1 | Sensible
55 | 2005 | 21 | 27 | 43 |  |  |  | 32350 | 9.48 | Sensible
55 | 2005 | 21 | 27 | 46 |  |  |  | 30235 | 8.86 | Sensible
55 | 2005 | 21 | 28 | 25 |  |  |  | 42040 | 12.32 | Sensible
55 | 2005 | 21 | 28 | 30 |  |  |  | 40470 | 11.86 | Sensible
55 | 2005 | 21 | 28 | 35 |  |  |  | 38795 | 11.37 | Sensible
55 | 2005 | 21 | 28 | 40 |  |  |  | 37260 | 10.92 | Sensible
55 | 2005 | 21 | 28 | 43 |  |  |  | 35215 | 10.32 | Sensible
55 | 2005 | 21 | 28 | 46 |  |  |  | 33165 | 9.72 | Sensible
55 | 2005 | 21 | 29 | 25 |  |  |  | 44800 | 13.13 | Sensible
55 | 2005 | 21 | 29 | 30 |  |  |  | 43235 | 12.67 | Sensible
55 | 2005 | 21 | 29 | 35 |  |  |  | 41560 | 12.18 | Sensible
55 | 2005 | 21 | 29 | 40 |  |  |  | 39990 | 11.72 | Sensible
55 | 2005 | 21 | 29 | 43 |  |  |  | 38150 | 11.18 | Sensible
55 | 2005 | 21 | 29 | 46 |  |  |  | 36305 | 10.64 | Sensible
55 | 2005 | 21 | 30 | 25 |  |  |  | 47600 | 13.95 | Sensible
55 | 2005 | 21 | 30 | 30 |  |  |  | 45415 | 13.31 | Sensible
55 | 2005 | 21 | 30 | 35 |  |  |  | 44325 | 12.99 | Sensible
55 | 2005 | 21 | 30 | 40 |  |  |  | 42755 | 12.53 | Sensible
55 | 2005 | 21 | 30 | 43 |  |  |  | 40945 | 12 | Sensible
55 | 2005 | 21 | 30 | 46 |  |  |  | 39140 | 11.47 | Sensible
90 | 3010 | 15 | 18 | 25 | 87250 | 25.57 | 9.66 |  |  | Total+Input
90 | 3010 | 15 | 18 | 30 | 80520 | 23.6 | 10.3 |  |  | Total+Input
90 | 3010 | 15 | 18 | 35 | 74240 | 21.76 | 10.79 |  |  | Total+Input
90 | 3010 | 15 | 18 | 40 | 67770 | 19.86 | 11.56 |  |  | Total+Input
90 | 3010 | 15 | 18 | 43 | 63880 | 18.72 | 11.86 |  |  | Total+Input
90 | 3010 | 15 | 18 | 46 | 59985 | 17.58 | 12.16 |  |  | Total+Input
90 | 3010 | 15 | 18 | 25 |  |  |  | 53775 | 15.76 | Sensible
90 | 3010 | 15 | 18 | 30 |  |  |  | 49885 | 14.62 | Sensible
90 | 3010 | 15 | 18 | 35 |  |  |  | 45995 | 13.48 | Sensible
90 | 3010 | 15 | 18 | 40 |  |  |  | 42105 | 12.34 | Sensible
90 | 3010 | 15 | 18 | 43 |  |  |  | 37430 | 10.97 | Sensible
90 | 3010 | 15 | 18 | 46 |  |  |  | 32760 | 9.6 | Sensible
90 | 3010 | 15 | 19 | 25 |  |  |  | 58380 | 17.11 | Sensible
90 | 3010 | 15 | 19 | 30 |  |  |  | 54490 | 15.97 | Sensible
90 | 3010 | 15 | 19 | 35 |  |  |  | 50600 | 14.83 | Sensible
90 | 3010 | 15 | 19 | 40 |  |  |  | 46715 | 13.69 | Sensible
90 | 3010 | 15 | 19 | 43 |  |  |  | 42040 | 12.32 | Sensible
90 | 3010 | 15 | 19 | 46 |  |  |  | 37365 | 10.95 | Sensible
90 | 3010 | 15 | 20 | 25 |  |  |  | 62990 | 18.46 | Sensible
90 | 3010 | 15 | 20 | 30 |  |  |  | 59100 | 17.32 | Sensible
90 | 3010 | 15 | 20 | 35 |  |  |  | 55210 | 16.18 | Sensible
90 | 3010 | 15 | 20 | 40 |  |  |  | 51320 | 15.04 | Sensible
90 | 3010 | 15 | 20 | 43 |  |  |  | 46645 | 13.67 | Sensible
90 | 3010 | 15 | 20 | 46 |  |  |  | 41970 | 12.3 | Sensible
90 | 3010 | 15 | 21 | 25 |  |  |  | 67595 | 19.81 | Sensible
90 | 3010 | 15 | 21 | 30 |  |  |  | 63705 | 18.67 | Sensible
90 | 3010 | 15 | 21 | 35 |  |  |  | 59815 | 17.53 | Sensible
90 | 3010 | 15 | 21 | 40 |  |  |  | 55925 | 16.39 | Sensible
90 | 3010 | 15 | 21 | 43 |  |  |  | 51250 | 15.02 | Sensible
90 | 3010 | 15 | 21 | 46 |  |  |  | 46575 | 13.65 | Sensible
90 | 3010 | 15 | 22 | 25 |  |  |  | 72200 | 21.16 | Sensible
90 | 3010 | 15 | 22 | 30 |  |  |  | 68310 | 20.02 | Sensible
90 | 3010 | 15 | 22 | 35 |  |  |  | 64420 | 18.88 | Sensible
90 | 3010 | 15 | 22 | 40 |  |  |  | 60530 | 17.74 | Sensible
90 | 3010 | 15 | 22 | 43 |  |  |  | 55855 | 16.37 | Sensible
90 | 3010 | 15 | 22 | 46 |  |  |  | 51180 | 15 | Sensible
90 | 3010 | 15 | 23 | 25 |  |  |  | 76805 | 22.51 | Sensible
90 | 3010 | 15 | 23 | 30 |  |  |  | 72915 | 21.37 | Sensible
90 | 3010 | 15 | 23 | 35 |  |  |  | 69025 | 20.23 | Sensible
90 | 3010 | 15 | 23 | 40 |  |  |  | 65140 | 19.09 | Sensible
90 | 3010 | 15 | 23 | 43 |  |  |  | 60465 | 17.72 | Sensible
90 | 3010 | 15 | 23 | 46 |  |  |  | 55790 | 16.35 | Sensible
90 | 3010 | 15 | 24 | 25 |  |  |  | 81415 | 23.86 | Sensible
90 | 3010 | 15 | 24 | 30 |  |  |  | 77525 | 22.72 | Sensible
90 | 3010 | 15 | 24 | 35 |  |  |  | 73635 | 21.58 | Sensible
90 | 3010 | 15 | 24 | 40 |  |  |  | 69745 | 20.44 | Sensible
90 | 3010 | 15 | 24 | 43 |  |  |  | 65070 | 19.07 | Sensible
90 | 3010 | 15 | 24 | 46 |  |  |  | 60395 | 17.7 | Sensible
90 | 3010 | 17 | 20 | 25 | 92335 | 27.06 | 9.87 |  |  | Total+Input
90 | 3010 | 17 | 20 | 30 | 86145 | 25.25 | 10.5 |  |  | Total+Input
90 | 3010 | 17 | 20 | 35 | 79970 | 23.44 | 10.99 |  |  | Total+Input
90 | 3010 | 17 | 20 | 40 | 73810 | 21.63 | 11.77 |  |  | Total+Input
90 | 3010 | 17 | 20 | 43 | 70105 | 20.55 | 12.11 |  |  | Total+Input
90 | 3010 | 17 | 20 | 46 | 66395 | 19.46 | 12.46 |  |  | Total+Input
90 | 3010 | 17 | 20 | 25 |  |  |  | 53400 | 15.65 | Sensible
90 | 3010 | 17 | 20 | 30 |  |  |  | 49510 | 14.51 | Sensible
90 | 3010 | 17 | 20 | 35 |  |  |  | 45620 | 13.37 | Sensible
90 | 3010 | 17 | 20 | 40 |  |  |  | 41730 | 12.23 | Sensible
90 | 3010 | 17 | 20 | 43 |  |  |  | 37055 | 10.86 | Sensible
90 | 3010 | 17 | 20 | 46 |  |  |  | 32380 | 9.49 | Sensible
90 | 3010 | 17 | 21 | 25 |  |  |  | 58005 | 17 | Sensible
90 | 3010 | 17 | 21 | 30 |  |  |  | 54115 | 15.86 | Sensible
90 | 3010 | 17 | 21 | 35 |  |  |  | 50225 | 14.72 | Sensible
90 | 3010 | 17 | 21 | 40 |  |  |  | 46335 | 13.58 | Sensible
90 | 3010 | 17 | 21 | 43 |  |  |  | 41665 | 12.21 | Sensible
90 | 3010 | 17 | 21 | 46 |  |  |  | 36990 | 10.84 | Sensible
90 | 3010 | 17 | 22 | 25 |  |  |  | 62615 | 18.35 | Sensible
90 | 3010 | 17 | 22 | 30 |  |  |  | 58725 | 17.21 | Sensible
90 | 3010 | 17 | 22 | 35 |  |  |  | 54835 | 16.07 | Sensible
90 | 3010 | 17 | 22 | 40 |  |  |  | 50945 | 14.93 | Sensible
90 | 3010 | 17 | 22 | 43 |  |  |  | 46270 | 13.56 | Sensible
90 | 3010 | 17 | 22 | 46 |  |  |  | 41595 | 12.19 | Sensible
90 | 3010 | 17 | 23 | 25 |  |  |  | 67220 | 19.7 | Sensible
90 | 3010 | 17 | 23 | 30 |  |  |  | 63330 | 18.56 | Sensible
90 | 3010 | 17 | 23 | 35 |  |  |  | 59440 | 17.42 | Sensible
90 | 3010 | 17 | 23 | 40 |  |  |  | 55550 | 16.28 | Sensible
90 | 3010 | 17 | 23 | 43 |  |  |  | 50875 | 14.91 | Sensible
90 | 3010 | 17 | 23 | 46 |  |  |  | 46200 | 13.54 | Sensible
90 | 3010 | 17 | 24 | 25 |  |  |  | 71825 | 21.05 | Sensible
90 | 3010 | 17 | 24 | 30 |  |  |  | 67935 | 19.91 | Sensible
90 | 3010 | 17 | 24 | 35 |  |  |  | 64045 | 18.77 | Sensible
90 | 3010 | 17 | 24 | 40 |  |  |  | 60155 | 17.63 | Sensible
90 | 3010 | 17 | 24 | 43 |  |  |  | 55480 | 16.26 | Sensible
90 | 3010 | 17 | 24 | 46 |  |  |  | 50805 | 14.89 | Sensible
90 | 3010 | 17 | 25 | 25 |  |  |  | 76430 | 22.4 | Sensible
90 | 3010 | 17 | 25 | 30 |  |  |  | 72540 | 21.26 | Sensible
90 | 3010 | 17 | 25 | 35 |  |  |  | 68650 | 20.12 | Sensible
90 | 3010 | 17 | 25 | 40 |  |  |  | 64760 | 18.98 | Sensible
90 | 3010 | 17 | 25 | 43 |  |  |  | 60090 | 17.61 | Sensible
90 | 3010 | 17 | 25 | 46 |  |  |  | 55415 | 16.24 | Sensible
90 | 3010 | 17 | 26 | 25 |  |  |  | 81035 | 23.75 | Sensible
90 | 3010 | 17 | 26 | 30 |  |  |  | 77150 | 22.61 | Sensible
90 | 3010 | 17 | 26 | 35 |  |  |  | 73260 | 21.47 | Sensible
90 | 3010 | 17 | 26 | 40 |  |  |  | 69370 | 20.33 | Sensible
90 | 3010 | 17 | 26 | 43 |  |  |  | 64695 | 18.96 | Sensible
90 | 3010 | 17 | 26 | 46 |  |  |  | 60020 | 17.59 | Sensible
90 | 3010 | 19 | 22 | 25 | 97450 | 28.56 | 10.08 |  |  | Total+Input
90 | 3010 | 19 | 22 | 30 | 91570 | 26.84 | 10.71 |  |  | Total+Input
90 | 3010 | 19 | 22 | 35 | 85700 | 25.12 | 11.28 |  |  | Total+Input
90 | 3010 | 19 | 22 | 40 | 79850 | 23.4 | 11.98 |  |  | Total+Input
90 | 3010 | 19 | 22 | 43 | 76330 | 22.37 | 12.37 |  |  | Total+Input
90 | 3010 | 19 | 22 | 46 | 72810 | 21.34 | 12.76 |  |  | Total+Input
90 | 3010 | 19 | 22 | 25 |  |  |  | 53025 | 15.54 | Sensible
90 | 3010 | 19 | 22 | 30 |  |  |  | 49135 | 14.4 | Sensible
90 | 3010 | 19 | 22 | 35 |  |  |  | 45245 | 13.26 | Sensible
90 | 3010 | 19 | 22 | 40 |  |  |  | 41355 | 12.12 | Sensible
90 | 3010 | 19 | 22 | 43 |  |  |  | 36680 | 10.75 | Sensible
90 | 3010 | 19 | 22 | 46 |  |  |  | 32005 | 9.38 | Sensible
90 | 3010 | 19 | 23 | 25 |  |  |  | 57630 | 16.89 | Sensible
90 | 3010 | 19 | 23 | 30 |  |  |  | 53740 | 15.75 | Sensible
90 | 3010 | 19 | 23 | 35 |  |  |  | 49850 | 14.61 | Sensible
90 | 3010 | 19 | 23 | 40 |  |  |  | 45960 | 13.47 | Sensible
90 | 3010 | 19 | 23 | 43 |  |  |  | 41290 | 12.1 | Sensible
90 | 3010 | 19 | 23 | 46 |  |  |  | 36615 | 10.73 | Sensible
90 | 3010 | 19 | 24 | 25 |  |  |  | 62235 | 18.24 | Sensible
90 | 3010 | 19 | 24 | 30 |  |  |  | 58350 | 17.1 | Sensible
90 | 3010 | 19 | 24 | 35 |  |  |  | 54460 | 15.96 | Sensible
90 | 3010 | 19 | 24 | 40 |  |  |  | 50570 | 14.82 | Sensible
90 | 3010 | 19 | 24 | 43 |  |  |  | 45895 | 13.45 | Sensible
90 | 3010 | 19 | 24 | 46 |  |  |  | 41220 | 12.08 | Sensible
90 | 3010 | 19 | 25 | 25 |  |  |  | 66845 | 19.59 | Sensible
90 | 3010 | 19 | 25 | 30 |  |  |  | 62955 | 18.45 | Sensible
90 | 3010 | 19 | 25 | 35 |  |  |  | 59065 | 17.31 | Sensible
90 | 3010 | 19 | 25 | 40 |  |  |  | 55175 | 16.17 | Sensible
90 | 3010 | 19 | 25 | 43 |  |  |  | 50500 | 14.8 | Sensible
90 | 3010 | 19 | 25 | 46 |  |  |  | 45825 | 13.43 | Sensible
90 | 3010 | 19 | 26 | 25 |  |  |  | 71450 | 20.94 | Sensible
90 | 3010 | 19 | 26 | 30 |  |  |  | 67560 | 19.8 | Sensible
90 | 3010 | 19 | 26 | 35 |  |  |  | 63670 | 18.66 | Sensible
90 | 3010 | 19 | 26 | 40 |  |  |  | 59780 | 17.52 | Sensible
90 | 3010 | 19 | 26 | 43 |  |  |  | 55105 | 16.15 | Sensible
90 | 3010 | 19 | 26 | 46 |  |  |  | 50430 | 14.78 | Sensible
90 | 3010 | 19 | 27 | 25 |  |  |  | 76055 | 22.29 | Sensible
90 | 3010 | 19 | 27 | 30 |  |  |  | 72165 | 21.15 | Sensible
90 | 3010 | 19 | 27 | 35 |  |  |  | 68275 | 20.01 | Sensible
90 | 3010 | 19 | 27 | 40 |  |  |  | 64385 | 18.87 | Sensible
90 | 3010 | 19 | 27 | 43 |  |  |  | 59710 | 17.5 | Sensible
90 | 3010 | 19 | 27 | 46 |  |  |  | 55040 | 16.13 | Sensible
90 | 3010 | 19 | 28 | 25 |  |  |  | 80660 | 23.64 | Sensible
90 | 3010 | 19 | 28 | 30 |  |  |  | 76770 | 22.5 | Sensible
90 | 3010 | 19 | 28 | 35 |  |  |  | 72885 | 21.36 | Sensible
90 | 3010 | 19 | 28 | 40 |  |  |  | 68995 | 20.22 | Sensible
90 | 3010 | 19 | 28 | 43 |  |  |  | 64320 | 18.85 | Sensible
90 | 3010 | 19 | 28 | 46 |  |  |  | 59645 | 17.48 | Sensible
90 | 3010 | 21 | 24 | 25 | 102570 | 30.06 | 10.31 |  |  | Total+Input
90 | 3010 | 21 | 24 | 30 | 96995 | 28.43 | 10.92 |  |  | Total+Input
90 | 3010 | 21 | 24 | 35 | 91440 | 26.8 | 11.49 |  |  | Total+Input
90 | 3010 | 21 | 24 | 40 | 85890 | 25.17 | 12.21 |  |  | Total+Input
90 | 3010 | 21 | 24 | 43 | 82560 | 24.2 | 12.63 |  |  | Total+Input
90 | 3010 | 21 | 24 | 46 | 79225 | 23.22 | 13.06 |  |  | Total+Input
90 | 3010 | 21 | 24 | 25 |  |  |  | 52650 | 15.43 | Sensible
90 | 3010 | 21 | 24 | 30 |  |  |  | 48760 | 14.29 | Sensible
90 | 3010 | 21 | 24 | 35 |  |  |  | 44870 | 13.15 | Sensible
90 | 3010 | 21 | 24 | 40 |  |  |  | 40980 | 12.01 | Sensible
90 | 3010 | 21 | 24 | 43 |  |  |  | 36305 | 10.64 | Sensible
90 | 3010 | 21 | 24 | 46 |  |  |  | 31630 | 9.27 | Sensible
90 | 3010 | 21 | 25 | 25 |  |  |  | 57255 | 16.78 | Sensible
90 | 3010 | 21 | 25 | 30 |  |  |  | 53365 | 15.64 | Sensible
90 | 3010 | 21 | 25 | 35 |  |  |  | 49475 | 14.5 | Sensible
90 | 3010 | 21 | 25 | 40 |  |  |  | 45585 | 13.36 | Sensible
90 | 3010 | 21 | 25 | 43 |  |  |  | 40910 | 11.99 | Sensible
90 | 3010 | 21 | 25 | 46 |  |  |  | 36240 | 10.62 | Sensible
90 | 3010 | 21 | 26 | 25 |  |  |  | 61860 | 18.13 | Sensible
90 | 3010 | 21 | 26 | 30 |  |  |  | 57970 | 16.99 | Sensible
90 | 3010 | 21 | 26 | 35 |  |  |  | 54085 | 15.85 | Sensible
90 | 3010 | 21 | 26 | 40 |  |  |  | 50195 | 14.71 | Sensible
90 | 3010 | 21 | 26 | 43 |  |  |  | 45520 | 13.34 | Sensible
90 | 3010 | 21 | 26 | 46 |  |  |  | 40845 | 11.97 | Sensible
90 | 3010 | 21 | 27 | 25 |  |  |  | 66470 | 19.48 | Sensible
90 | 3010 | 21 | 27 | 30 |  |  |  | 62580 | 18.34 | Sensible
90 | 3010 | 21 | 27 | 35 |  |  |  | 58690 | 17.2 | Sensible
90 | 3010 | 21 | 27 | 40 |  |  |  | 54800 | 16.06 | Sensible
90 | 3010 | 21 | 27 | 43 |  |  |  | 50125 | 14.69 | Sensible
90 | 3010 | 21 | 27 | 46 |  |  |  | 45450 | 13.32 | Sensible
90 | 3010 | 21 | 28 | 25 |  |  |  | 71075 | 20.83 | Sensible
90 | 3010 | 21 | 28 | 30 |  |  |  | 67185 | 19.69 | Sensible
90 | 3010 | 21 | 28 | 35 |  |  |  | 63295 | 18.55 | Sensible
90 | 3010 | 21 | 28 | 40 |  |  |  | 59405 | 17.41 | Sensible
90 | 3010 | 21 | 28 | 43 |  |  |  | 54730 | 16.04 | Sensible
90 | 3010 | 21 | 28 | 46 |  |  |  | 50055 | 14.67 | Sensible
90 | 3010 | 21 | 29 | 25 |  |  |  | 75680 | 22.18 | Sensible
90 | 3010 | 21 | 29 | 30 |  |  |  | 71790 | 21.04 | Sensible
90 | 3010 | 21 | 29 | 35 |  |  |  | 67900 | 19.9 | Sensible
90 | 3010 | 21 | 29 | 40 |  |  |  | 64010 | 18.76 | Sensible
90 | 3010 | 21 | 29 | 43 |  |  |  | 59335 | 17.39 | Sensible
90 | 3010 | 21 | 29 | 46 |  |  |  | 54665 | 16.02 | Sensible
90 | 3010 | 21 | 30 | 25 |  |  |  | 80285 | 23.53 | Sensible
90 | 3010 | 21 | 30 | 30 |  |  |  | 76395 | 22.39 | Sensible
90 | 3010 | 21 | 30 | 35 |  |  |  | 72505 | 21.25 | Sensible
90 | 3010 | 21 | 30 | 40 |  |  |  | 68620 | 20.11 | Sensible
90 | 3010 | 21 | 30 | 43 |  |  |  | 63945 | 18.74 | Sensible
90 | 3010 | 21 | 30 | 46 |  |  |  | 59270 | 17.37 | Sensible
110 | 3540 | 15 | 18 | 25 | 107035 | 31.37 | 14.06 |  |  | Total+Input
110 | 3540 | 15 | 18 | 30 | 101100 | 29.63 | 14.17 |  |  | Total+Input
110 | 3540 | 15 | 18 | 35 | 93930 | 27.53 | 15.22 |  |  | Total+Input
110 | 3540 | 15 | 18 | 40 | 87625 | 25.68 | 16.26 |  |  | Total+Input
110 | 3540 | 15 | 18 | 43 | 83340 | 24.43 | 16.89 |  |  | Total+Input
110 | 3540 | 15 | 18 | 46 | 79050 | 23.17 | 17.52 |  |  | Total+Input
110 | 3540 | 15 | 18 | 25 |  |  |  | 60700 | 17.79 | Sensible
110 | 3540 | 15 | 18 | 30 |  |  |  | 57530 | 16.86 | Sensible
110 | 3540 | 15 | 18 | 35 |  |  |  | 54355 | 15.93 | Sensible
110 | 3540 | 15 | 18 | 40 |  |  |  | 51180 | 15 | Sensible
110 | 3540 | 15 | 18 | 43 |  |  |  | 47360 | 13.88 | Sensible
110 | 3540 | 15 | 18 | 46 |  |  |  | 43540 | 12.76 | Sensible
110 | 3540 | 15 | 19 | 25 |  |  |  | 66230 | 19.41 | Sensible
110 | 3540 | 15 | 19 | 30 |  |  |  | 63055 | 18.48 | Sensible
110 | 3540 | 15 | 19 | 35 |  |  |  | 59885 | 17.55 | Sensible
110 | 3540 | 15 | 19 | 40 |  |  |  | 56710 | 16.62 | Sensible
110 | 3540 | 15 | 19 | 43 |  |  |  | 52925 | 15.51 | Sensible
110 | 3540 | 15 | 19 | 46 |  |  |  | 49135 | 14.4 | Sensible
110 | 3540 | 15 | 20 | 25 |  |  |  | 71790 | 21.04 | Sensible
110 | 3540 | 15 | 20 | 30 |  |  |  | 68620 | 20.11 | Sensible
110 | 3540 | 15 | 20 | 35 |  |  |  | 65445 | 19.18 | Sensible
110 | 3540 | 15 | 20 | 40 |  |  |  | 62270 | 18.25 | Sensible
110 | 3540 | 15 | 20 | 43 |  |  |  | 58450 | 17.13 | Sensible
110 | 3540 | 15 | 20 | 46 |  |  |  | 54630 | 16.01 | Sensible
110 | 3540 | 15 | 21 | 25 |  |  |  | 77355 | 22.67 | Sensible
110 | 3540 | 15 | 21 | 30 |  |  |  | 74180 | 21.74 | Sensible
110 | 3540 | 15 | 21 | 35 |  |  |  | 71005 | 20.81 | Sensible
110 | 3540 | 15 | 21 | 40 |  |  |  | 67835 | 19.88 | Sensible
110 | 3540 | 15 | 21 | 43 |  |  |  | 64010 | 18.76 | Sensible
110 | 3540 | 15 | 21 | 46 |  |  |  | 60190 | 17.64 | Sensible
110 | 3540 | 15 | 22 | 25 |  |  |  | 82915 | 24.3 | Sensible
110 | 3540 | 15 | 22 | 30 |  |  |  | 79740 | 23.37 | Sensible
110 | 3540 | 15 | 22 | 35 |  |  |  | 76570 | 22.44 | Sensible
110 | 3540 | 15 | 22 | 40 |  |  |  | 73395 | 21.51 | Sensible
110 | 3540 | 15 | 22 | 43 |  |  |  | 69575 | 20.39 | Sensible
110 | 3540 | 15 | 22 | 46 |  |  |  | 66980 | 19.63 | Sensible
110 | 3540 | 15 | 23 | 25 |  |  |  | 88475 | 25.93 | Sensible
110 | 3540 | 15 | 23 | 30 |  |  |  | 85300 | 25 | Sensible
110 | 3540 | 15 | 23 | 35 |  |  |  | 82095 | 24.06 | Sensible
110 | 3540 | 15 | 23 | 40 |  |  |  | 78920 | 23.13 | Sensible
110 | 3540 | 15 | 23 | 43 |  |  |  | 75135 | 22.02 | Sensible
110 | 3540 | 15 | 23 | 46 |  |  |  | 71345 | 20.91 | Sensible
110 | 3540 | 15 | 24 | 25 |  |  |  | 94005 | 27.55 | Sensible
110 | 3540 | 15 | 24 | 30 |  |  |  | 90830 | 26.62 | Sensible
110 | 3540 | 15 | 24 | 35 |  |  |  | 87655 | 25.69 | Sensible
110 | 3540 | 15 | 24 | 40 |  |  |  | 84485 | 24.76 | Sensible
110 | 3540 | 15 | 24 | 43 |  |  |  | 79265 | 23.23 | Sensible
110 | 3540 | 15 | 24 | 46 |  |  |  | 94515 | 27.7 | Sensible
110 | 3540 | 17 | 20 | 25 | 113785 | 33.35 | 14.38 |  |  | Total+Input
110 | 3540 | 17 | 20 | 30 | 108635 | 31.84 | 14.47 |  |  | Total+Input
110 | 3540 | 17 | 20 | 35 | 101465 | 29.74 | 15.52 |  |  | Total+Input
110 | 3540 | 17 | 20 | 40 | 93965 | 27.54 | 16.56 |  |  | Total+Input
110 | 3540 | 17 | 20 | 43 | 89920 | 26.35 | 17.19 |  |  | Total+Input
110 | 3540 | 17 | 20 | 46 | 85870 | 25.17 | 17.82 |  |  | Total+Input
110 | 3540 | 17 | 20 | 25 |  |  |  | 61075 | 17.9 | Sensible
110 | 3540 | 17 | 20 | 30 |  |  |  | 57905 | 16.97 | Sensible
110 | 3540 | 17 | 20 | 35 |  |  |  | 54730 | 16.04 | Sensible
110 | 3540 | 17 | 20 | 40 |  |  |  | 51560 | 15.11 | Sensible
110 | 3540 | 17 | 20 | 43 |  |  |  | 47770 | 14 | Sensible
110 | 3540 | 17 | 20 | 46 |  |  |  | 43985 | 12.89 | Sensible
110 | 3540 | 17 | 21 | 25 |  |  |  | 66640 | 19.53 | Sensible
110 | 3540 | 17 | 21 | 30 |  |  |  | 63465 | 18.6 | Sensible
110 | 3540 | 17 | 21 | 35 |  |  |  | 60295 | 17.67 | Sensible
110 | 3540 | 17 | 21 | 40 |  |  |  | 57120 | 16.74 | Sensible
110 | 3540 | 17 | 21 | 43 |  |  |  | 53300 | 15.62 | Sensible
110 | 3540 | 17 | 21 | 46 |  |  |  | 114235 | 33.48 | Sensible
110 | 3540 | 17 | 22 | 25 |  |  |  | 72200 | 21.16 | Sensible
110 | 3540 | 17 | 22 | 30 |  |  |  | 69025 | 20.23 | Sensible
110 | 3540 | 17 | 22 | 35 |  |  |  | 65855 | 19.3 | Sensible
110 | 3540 | 17 | 22 | 40 |  |  |  | 62680 | 18.37 | Sensible
110 | 3540 | 17 | 22 | 43 |  |  |  | 58860 | 17.25 | Sensible
110 | 3540 | 17 | 22 | 46 |  |  |  | 55040 | 16.13 | Sensible
110 | 3540 | 17 | 23 | 25 |  |  |  | 77760 | 22.79 | Sensible
110 | 3540 | 17 | 23 | 30 |  |  |  | 74590 | 21.86 | Sensible
110 | 3540 | 17 | 23 | 35 |  |  |  | 71415 | 20.93 | Sensible
110 | 3540 | 17 | 23 | 40 |  |  |  | 68240 | 20 | Sensible
110 | 3540 | 17 | 23 | 43 |  |  |  | 64420 | 18.88 | Sensible
110 | 3540 | 17 | 23 | 46 |  |  |  | 60600 | 17.76 | Sensible
110 | 3540 | 17 | 24 | 25 |  |  |  | 83290 | 24.41 | Sensible
110 | 3540 | 17 | 24 | 30 |  |  |  | 80115 | 23.48 | Sensible
110 | 3540 | 17 | 24 | 35 |  |  |  | 76945 | 22.55 | Sensible
110 | 3540 | 17 | 24 | 40 |  |  |  | 73770 | 21.62 | Sensible
110 | 3540 | 17 | 24 | 43 |  |  |  | 69985 | 20.51 | Sensible
110 | 3540 | 17 | 24 | 46 |  |  |  | 66195 | 19.4 | Sensible
110 | 3540 | 17 | 25 | 25 |  |  |  | 88850 | 26.04 | Sensible
110 | 3540 | 17 | 25 | 30 |  |  |  | 85680 | 25.11 | Sensible
110 | 3540 | 17 | 25 | 35 |  |  |  | 82505 | 24.18 | Sensible
110 | 3540 | 17 | 25 | 40 |  |  |  | 79330 | 23.25 | Sensible
110 | 3540 | 17 | 25 | 43 |  |  |  | 75510 | 22.13 | Sensible
110 | 3540 | 17 | 25 | 46 |  |  |  | 71690 | 21.01 | Sensible
110 | 3540 | 17 | 26 | 25 |  |  |  | 94415 | 27.67 | Sensible
110 | 3540 | 17 | 26 | 30 |  |  |  | 91240 | 26.74 | Sensible
110 | 3540 | 17 | 26 | 35 |  |  |  | 88065 | 25.81 | Sensible
110 | 3540 | 17 | 26 | 40 |  |  |  | 84895 | 24.88 | Sensible
110 | 3540 | 17 | 26 | 43 |  |  |  | 81070 | 23.76 | Sensible
110 | 3540 | 17 | 26 | 46 |  |  |  | 77250 | 22.64 | Sensible
110 | 3540 | 19 | 22 | 25 | 120500 | 35.32 | 14.7 |  |  | Total+Input
110 | 3540 | 19 | 22 | 30 | 115350 | 33.81 | 14.77 |  |  | Total+Input
110 | 3540 | 19 | 22 | 35 | 109000 | 31.95 | 15.82 |  |  | Total+Input
110 | 3540 | 19 | 22 | 40 | 101500 | 29.75 | 16.86 |  |  | Total+Input
110 | 3540 | 19 | 22 | 43 | 96980 | 28.42 | 17.49 |  |  | Total+Input
110 | 3540 | 19 | 22 | 46 | 92450 | 27.1 | 18.12 |  |  | Total+Input
110 | 3540 | 19 | 22 | 25 |  |  |  | 61485 | 18.02 | Sensible
110 | 3540 | 19 | 22 | 30 |  |  |  | 58315 | 17.09 | Sensible
110 | 3540 | 19 | 22 | 35 |  |  |  | 55140 | 16.16 | Sensible
110 | 3540 | 19 | 22 | 40 |  |  |  | 51965 | 15.23 | Sensible
110 | 3540 | 19 | 22 | 43 |  |  |  | 48145 | 14.11 | Sensible
110 | 3540 | 19 | 22 | 46 |  |  |  | 44325 | 12.99 | Sensible
110 | 3540 | 19 | 23 | 25 |  |  |  | 67050 | 19.65 | Sensible
110 | 3540 | 19 | 23 | 30 |  |  |  | 63875 | 18.72 | Sensible
110 | 3540 | 19 | 23 | 35 |  |  |  | 60700 | 17.79 | Sensible
110 | 3540 | 19 | 23 | 40 |  |  |  | 57495 | 16.85 | Sensible
110 | 3540 | 19 | 23 | 43 |  |  |  | 53705 | 15.74 | Sensible
110 | 3540 | 19 | 23 | 46 |  |  |  | 49920 | 14.63 | Sensible
110 | 3540 | 19 | 24 | 25 |  |  |  | 72575 | 21.27 | Sensible
110 | 3540 | 19 | 24 | 30 |  |  |  | 69405 | 20.34 | Sensible
110 | 3540 | 19 | 24 | 35 |  |  |  | 66195 | 19.4 | Sensible
110 | 3540 | 19 | 24 | 40 |  |  |  | 63020 | 18.47 | Sensible
110 | 3540 | 19 | 24 | 43 |  |  |  | 59235 | 17.36 | Sensible
110 | 3540 | 19 | 24 | 46 |  |  |  | 55445 | 16.25 | Sensible
110 | 3540 | 19 | 25 | 25 |  |  |  | 78135 | 22.9 | Sensible
110 | 3540 | 19 | 25 | 30 |  |  |  | 74965 | 21.97 | Sensible
110 | 3540 | 19 | 25 | 35 |  |  |  | 71755 | 21.03 | Sensible
110 | 3540 | 19 | 25 | 40 |  |  |  | 68550 | 20.09 | Sensible
110 | 3540 | 19 | 25 | 43 |  |  |  | 64760 | 18.98 | Sensible
110 | 3540 | 19 | 25 | 46 |  |  |  | 60975 | 17.87 | Sensible
110 | 3540 | 19 | 26 | 25 |  |  |  | 83700 | 24.53 | Sensible
110 | 3540 | 19 | 26 | 30 |  |  |  | 80525 | 23.6 | Sensible
110 | 3540 | 19 | 26 | 35 |  |  |  | 77250 | 22.64 | Sensible
110 | 3540 | 19 | 26 | 40 |  |  |  | 74075 | 21.71 | Sensible
110 | 3540 | 19 | 26 | 43 |  |  |  | 70290 | 20.6 | Sensible
110 | 3540 | 19 | 26 | 46 |  |  |  | 66500 | 19.49 | Sensible
110 | 3540 | 19 | 27 | 25 |  |  |  | 89260 | 26.16 | Sensible
110 | 3540 | 19 | 27 | 30 |  |  |  | 86085 | 25.23 | Sensible
110 | 3540 | 19 | 27 | 35 |  |  |  | 84075 | 24.64 | Sensible
110 | 3540 | 19 | 27 | 40 |  |  |  | 79265 | 23.23 | Sensible
110 | 3540 | 19 | 27 | 43 |  |  |  | 75815 | 22.22 | Sensible
110 | 3540 | 19 | 27 | 46 |  |  |  | 72370 | 21.21 | Sensible
110 | 3540 | 19 | 28 | 25 |  |  |  | 94820 | 27.79 | Sensible
110 | 3540 | 19 | 28 | 30 |  |  |  | 91650 | 26.86 | Sensible
110 | 3540 | 19 | 28 | 35 |  |  |  | 88305 | 25.88 | Sensible
110 | 3540 | 19 | 28 | 40 |  |  |  | 85130 | 24.95 | Sensible
110 | 3540 | 19 | 28 | 43 |  |  |  | 81345 | 23.84 | Sensible
110 | 3540 | 19 | 28 | 46 |  |  |  | 77555 | 22.73 | Sensible
110 | 3540 | 21 | 24 | 25 | 123265 | 36.13 | 15.02 |  |  | Total+Input
110 | 3540 | 21 | 24 | 30 | 120910 | 35.44 | 15.07 |  |  | Total+Input
110 | 3540 | 21 | 24 | 35 | 114970 | 33.7 | 16.12 |  |  | Total+Input
110 | 3540 | 21 | 24 | 40 | 107470 | 31.5 | 17.16 |  |  | Total+Input
110 | 3540 | 21 | 24 | 43 | 102945 | 30.17 | 17.79 |  |  | Total+Input
110 | 3540 | 21 | 24 | 46 | 98420 | 28.85 | 18.42 |  |  | Total+Input
110 | 3540 | 21 | 24 | 25 |  |  |  | 61860 | 18.13 | Sensible
110 | 3540 | 21 | 24 | 30 |  |  |  | 58690 | 17.2 | Sensible
110 | 3540 | 21 | 24 | 35 |  |  |  | 55515 | 16.27 | Sensible
110 | 3540 | 21 | 24 | 40 |  |  |  | 52345 | 15.34 | Sensible
110 | 3540 | 21 | 24 | 43 |  |  |  | 48555 | 14.23 | Sensible
110 | 3540 | 21 | 24 | 46 |  |  |  | 44770 | 13.12 | Sensible
110 | 3540 | 21 | 25 | 25 |  |  |  | 67425 | 19.76 | Sensible
110 | 3540 | 21 | 25 | 30 |  |  |  | 64250 | 18.83 | Sensible
110 | 3540 | 21 | 25 | 35 |  |  |  | 61045 | 17.89 | Sensible
110 | 3540 | 21 | 25 | 40 |  |  |  | 57870 | 16.96 | Sensible
110 | 3540 | 21 | 25 | 43 |  |  |  | 53640 | 15.72 | Sensible
110 | 3540 | 21 | 25 | 46 |  |  |  | 49410 | 14.48 | Sensible
110 | 3540 | 21 | 26 | 25 |  |  |  | 72985 | 21.39 | Sensible
110 | 3540 | 21 | 26 | 30 |  |  |  | 69810 | 20.46 | Sensible
110 | 3540 | 21 | 26 | 35 |  |  |  | 66570 | 19.51 | Sensible
110 | 3540 | 21 | 26 | 40 |  |  |  | 63395 | 18.58 | Sensible
110 | 3540 | 21 | 26 | 43 |  |  |  | 59165 | 17.34 | Sensible
110 | 3540 | 21 | 26 | 46 |  |  |  | 54935 | 16.1 | Sensible
110 | 3540 | 21 | 27 | 25 |  |  |  | 78545 | 23.02 | Sensible
110 | 3540 | 21 | 27 | 30 |  |  |  | 75375 | 22.09 | Sensible
110 | 3540 | 21 | 27 | 35 |  |  |  | 72100 | 21.13 | Sensible
110 | 3540 | 21 | 27 | 40 |  |  |  | 68925 | 20.2 | Sensible
110 | 3540 | 21 | 27 | 43 |  |  |  | 64730 | 18.97 | Sensible
110 | 3540 | 21 | 27 | 46 |  |  |  | 60530 | 17.74 | Sensible
110 | 3540 | 21 | 28 | 25 |  |  |  | 84110 | 24.65 | Sensible
110 | 3540 | 21 | 28 | 30 |  |  |  | 80935 | 23.72 | Sensible
110 | 3540 | 21 | 28 | 35 |  |  |  | 77625 | 22.75 | Sensible
110 | 3540 | 21 | 28 | 40 |  |  |  | 74450 | 21.82 | Sensible
110 | 3540 | 21 | 28 | 43 |  |  |  | 70290 | 20.6 | Sensible
110 | 3540 | 21 | 28 | 46 |  |  |  | 72680 | 21.3 | Sensible
110 | 3540 | 21 | 29 | 25 |  |  |  | 89635 | 26.27 | Sensible
110 | 3540 | 21 | 29 | 30 |  |  |  | 86465 | 25.34 | Sensible
110 | 3540 | 21 | 29 | 35 |  |  |  | 83155 | 24.37 | Sensible
110 | 3540 | 21 | 29 | 40 |  |  |  | 79980 | 23.44 | Sensible
110 | 3540 | 21 | 29 | 43 |  |  |  | 76330 | 22.37 | Sensible
110 | 3540 | 21 | 29 | 46 |  |  |  | 72680 | 21.3 | Sensible
110 | 3540 | 21 | 30 | 25 |  |  |  | 95195 | 27.9 | Sensible
110 | 3540 | 21 | 30 | 30 |  |  |  | 90830 | 26.62 | Sensible
110 | 3540 | 21 | 30 | 35 |  |  |  | 88680 | 25.99 | Sensible
110 | 3540 | 21 | 30 | 40 |  |  |  | 85505 | 25.06 | Sensible
110 | 3540 | 21 | 30 | 43 |  |  |  | 81890 | 24 | Sensible
110 | 3540 | 21 | 30 | 46 |  |  |  | 78275 | 22.94 | Sensible
145 | 6020 | 15 | 18 | 25 | 144790 | 42.44 | 15.7 |  |  | Total+Input
145 | 6020 | 15 | 18 | 30 | 138030 | 40.45 | 17.21 |  |  | Total+Input
145 | 6020 | 15 | 18 | 35 | 129665 | 38 | 18.64 |  |  | Total+Input
145 | 6020 | 15 | 18 | 40 | 120915 | 35.44 | 20.07 |  |  | Total+Input
145 | 6020 | 15 | 18 | 43 | 115665 | 33.9 | 20.81 |  |  | Total+Input
145 | 6020 | 15 | 18 | 46 | 110415 | 32.36 | 21.55 |  |  | Total+Input
145 | 6020 | 15 | 18 | 25 |  |  |  | 82505 | 24.18 | Sensible
145 | 6020 | 15 | 18 | 30 |  |  |  | 79125 | 23.19 | Sensible
145 | 6020 | 15 | 18 | 35 |  |  |  | 75750 | 22.2 | Sensible
145 | 6020 | 15 | 18 | 40 |  |  |  | 72335 | 21.2 | Sensible
145 | 6020 | 15 | 18 | 43 |  |  |  | 68345 | 20.03 | Sensible
145 | 6020 | 15 | 18 | 46 |  |  |  | 64355 | 18.86 | Sensible
145 | 6020 | 15 | 19 | 25 |  |  |  | 90420 | 26.5 | Sensible
145 | 6020 | 15 | 19 | 30 |  |  |  | 87045 | 25.51 | Sensible
145 | 6020 | 15 | 19 | 35 |  |  |  | 83665 | 24.52 | Sensible
145 | 6020 | 15 | 19 | 40 |  |  |  | 80320 | 23.54 | Sensible
145 | 6020 | 15 | 19 | 43 |  |  |  | 76260 | 22.35 | Sensible
145 | 6020 | 15 | 19 | 46 |  |  |  | 72200 | 21.16 | Sensible
145 | 6020 | 15 | 20 | 25 |  |  |  | 98335 | 28.82 | Sensible
145 | 6020 | 15 | 20 | 30 |  |  |  | 94960 | 27.83 | Sensible
145 | 6020 | 15 | 20 | 35 |  |  |  | 91580 | 26.84 | Sensible
145 | 6020 | 15 | 20 | 40 |  |  |  | 88235 | 25.86 | Sensible
145 | 6020 | 15 | 20 | 43 |  |  |  | 84175 | 24.67 | Sensible
145 | 6020 | 15 | 20 | 46 |  |  |  | 80115 | 23.48 | Sensible
145 | 6020 | 15 | 21 | 25 |  |  |  | 106250 | 31.14 | Sensible
145 | 6020 | 15 | 21 | 30 |  |  |  | 102875 | 30.15 | Sensible
145 | 6020 | 15 | 21 | 35 |  |  |  | 99495 | 29.16 | Sensible
145 | 6020 | 15 | 21 | 40 |  |  |  | 96155 | 28.18 | Sensible
145 | 6020 | 15 | 21 | 43 |  |  |  | 92090 | 26.99 | Sensible
145 | 6020 | 15 | 21 | 46 |  |  |  | 88030 | 25.8 | Sensible
145 | 6020 | 15 | 22 | 25 |  |  |  | 114170 | 33.46 | Sensible
145 | 6020 | 15 | 22 | 30 |  |  |  | 110790 | 32.47 | Sensible
145 | 6020 | 15 | 22 | 35 |  |  |  | 107410 | 31.48 | Sensible
145 | 6020 | 15 | 22 | 40 |  |  |  | 104070 | 30.5 | Sensible
145 | 6020 | 15 | 22 | 43 |  |  |  | 100010 | 29.31 | Sensible
145 | 6020 | 15 | 22 | 46 |  |  |  | 97485 | 28.57 | Sensible
145 | 6020 | 15 | 23 | 25 |  |  |  | 122085 | 35.78 | Sensible
145 | 6020 | 15 | 23 | 30 |  |  |  | 118705 | 34.79 | Sensible
145 | 6020 | 15 | 23 | 35 |  |  |  | 115330 | 33.8 | Sensible
145 | 6020 | 15 | 23 | 40 |  |  |  | 111985 | 32.82 | Sensible
145 | 6020 | 15 | 23 | 43 |  |  |  | 107925 | 31.63 | Sensible
145 | 6020 | 15 | 23 | 46 |  |  |  | 103865 | 30.44 | Sensible
145 | 6020 | 15 | 24 | 25 |  |  |  | 130000 | 38.1 | Sensible
145 | 6020 | 15 | 24 | 30 |  |  |  | 126620 | 37.11 | Sensible
145 | 6020 | 15 | 24 | 35 |  |  |  | 123245 | 36.12 | Sensible
145 | 6020 | 15 | 24 | 40 |  |  |  | 119900 | 35.14 | Sensible
145 | 6020 | 15 | 24 | 43 |  |  |  | 115840 | 33.95 | Sensible
145 | 6020 | 15 | 24 | 46 |  |  |  | 111780 | 32.76 | Sensible
145 | 6020 | 17 | 20 | 25 | 150740 | 44.18 | 16.11 |  |  | Total+Input
145 | 6020 | 17 | 20 | 30 | 144390 | 42.32 | 17.62 |  |  | Total+Input
145 | 6020 | 17 | 20 | 35 | 136850 | 40.11 | 19.05 |  |  | Total+Input
145 | 6020 | 17 | 20 | 40 | 128100 | 37.54 | 20.48 |  |  | Total+Input
145 | 6020 | 17 | 20 | 43 | 122850 | 36.01 | 21.22 |  |  | Total+Input
145 | 6020 | 17 | 20 | 46 | 117600 | 34.47 | 21.96 |  |  | Total+Input
145 | 6020 | 17 | 20 | 25 |  |  |  | 82025 | 24.04 | Sensible
145 | 6020 | 17 | 20 | 30 |  |  |  | 78650 | 23.05 | Sensible
145 | 6020 | 17 | 20 | 35 |  |  |  | 75270 | 22.06 | Sensible
145 | 6020 | 17 | 20 | 40 |  |  |  | 71895 | 21.07 | Sensible
145 | 6020 | 17 | 20 | 43 |  |  |  | 67835 | 19.88 | Sensible
145 | 6020 | 17 | 20 | 46 |  |  |  | 63775 | 18.69 | Sensible
145 | 6020 | 17 | 21 | 25 |  |  |  | 89945 | 26.36 | Sensible
145 | 6020 | 17 | 21 | 30 |  |  |  | 86565 | 25.37 | Sensible
145 | 6020 | 17 | 21 | 35 |  |  |  | 83185 | 24.38 | Sensible
145 | 6020 | 17 | 21 | 40 |  |  |  | 79810 | 23.39 | Sensible
145 | 6020 | 17 | 21 | 43 |  |  |  | 75750 | 22.2 | Sensible
145 | 6020 | 17 | 21 | 46 |  |  |  | 68275 | 20.01 | Sensible
145 | 6020 | 17 | 22 | 25 |  |  |  | 97860 | 28.68 | Sensible
145 | 6020 | 17 | 22 | 30 |  |  |  | 94480 | 27.69 | Sensible
145 | 6020 | 17 | 22 | 35 |  |  |  | 91105 | 26.7 | Sensible
145 | 6020 | 17 | 22 | 40 |  |  |  | 87725 | 25.71 | Sensible
145 | 6020 | 17 | 22 | 43 |  |  |  | 83665 | 24.52 | Sensible
145 | 6020 | 17 | 22 | 46 |  |  |  | 79605 | 23.33 | Sensible
145 | 6020 | 17 | 23 | 25 |  |  |  | 105775 | 31 | Sensible
145 | 6020 | 17 | 23 | 30 |  |  |  | 102395 | 30.01 | Sensible
145 | 6020 | 17 | 23 | 35 |  |  |  | 99020 | 29.02 | Sensible
145 | 6020 | 17 | 23 | 40 |  |  |  | 95640 | 28.03 | Sensible
145 | 6020 | 17 | 23 | 43 |  |  |  | 91580 | 26.84 | Sensible
145 | 6020 | 17 | 23 | 46 |  |  |  | 87520 | 25.65 | Sensible
145 | 6020 | 17 | 24 | 25 |  |  |  | 113690 | 33.32 | Sensible
145 | 6020 | 17 | 24 | 30 |  |  |  | 110310 | 32.33 | Sensible
145 | 6020 | 17 | 24 | 35 |  |  |  | 106935 | 31.34 | Sensible
145 | 6020 | 17 | 24 | 40 |  |  |  | 103555 | 30.35 | Sensible
145 | 6020 | 17 | 24 | 43 |  |  |  | 99495 | 29.16 | Sensible
145 | 6020 | 17 | 24 | 46 |  |  |  | 95435 | 27.97 | Sensible
145 | 6020 | 17 | 25 | 25 |  |  |  | 121605 | 35.64 | Sensible
145 | 6020 | 17 | 25 | 30 |  |  |  | 118230 | 34.65 | Sensible
145 | 6020 | 17 | 25 | 35 |  |  |  | 114850 | 33.66 | Sensible
145 | 6020 | 17 | 25 | 40 |  |  |  | 111475 | 32.67 | Sensible
145 | 6020 | 17 | 25 | 43 |  |  |  | 107410 | 31.48 | Sensible
145 | 6020 | 17 | 25 | 46 |  |  |  | 103350 | 30.29 | Sensible
145 | 6020 | 17 | 26 | 25 |  |  |  | 129520 | 37.96 | Sensible
145 | 6020 | 17 | 26 | 30 |  |  |  | 126145 | 36.97 | Sensible
145 | 6020 | 17 | 26 | 35 |  |  |  | 122765 | 35.98 | Sensible
145 | 6020 | 17 | 26 | 40 |  |  |  | 119390 | 34.99 | Sensible
145 | 6020 | 17 | 26 | 43 |  |  |  | 115330 | 33.8 | Sensible
145 | 6020 | 17 | 26 | 46 |  |  |  | 111270 | 32.61 | Sensible
145 | 6020 | 19 | 22 | 25 | 155940 | 45.7 | 16.52 |  |  | Total+Input
145 | 6020 | 19 | 22 | 30 | 150750 | 44.18 | 18.03 |  |  | Total+Input
145 | 6020 | 19 | 22 | 35 | 144000 | 42.2 | 19.46 |  |  | Total+Input
145 | 6020 | 19 | 22 | 40 | 135250 | 39.64 | 20.89 |  |  | Total+Input
145 | 6020 | 19 | 22 | 43 | 130000 | 38.1 | 21.63 |  |  | Total+Input
145 | 6020 | 19 | 22 | 46 | 124750 | 36.56 | 22.37 |  |  | Total+Input
145 | 6020 | 19 | 22 | 25 |  |  |  | 81515 | 23.89 | Sensible
145 | 6020 | 19 | 22 | 30 |  |  |  | 78135 | 22.9 | Sensible
145 | 6020 | 19 | 22 | 35 |  |  |  | 74760 | 21.91 | Sensible
145 | 6020 | 19 | 22 | 40 |  |  |  | 71415 | 20.93 | Sensible
145 | 6020 | 19 | 22 | 43 |  |  |  | 67355 | 19.74 | Sensible
145 | 6020 | 19 | 22 | 46 |  |  |  | 63295 | 18.55 | Sensible
145 | 6020 | 19 | 23 | 25 |  |  |  | 89430 | 26.21 | Sensible
145 | 6020 | 19 | 23 | 30 |  |  |  | 86055 | 25.22 | Sensible
145 | 6020 | 19 | 23 | 35 |  |  |  | 82675 | 24.23 | Sensible
145 | 6020 | 19 | 23 | 40 |  |  |  | 79330 | 23.25 | Sensible
145 | 6020 | 19 | 23 | 43 |  |  |  | 75270 | 22.06 | Sensible
145 | 6020 | 19 | 23 | 46 |  |  |  | 71210 | 20.87 | Sensible
145 | 6020 | 19 | 24 | 25 |  |  |  | 97345 | 28.53 | Sensible
145 | 6020 | 19 | 24 | 30 |  |  |  | 93970 | 27.54 | Sensible
145 | 6020 | 19 | 24 | 35 |  |  |  | 90590 | 26.55 | Sensible
145 | 6020 | 19 | 24 | 40 |  |  |  | 87245 | 25.57 | Sensible
145 | 6020 | 19 | 24 | 43 |  |  |  | 83185 | 24.38 | Sensible
145 | 6020 | 19 | 24 | 46 |  |  |  | 79125 | 23.19 | Sensible
145 | 6020 | 19 | 25 | 25 |  |  |  | 105265 | 30.85 | Sensible
145 | 6020 | 19 | 25 | 30 |  |  |  | 101885 | 29.86 | Sensible
145 | 6020 | 19 | 25 | 35 |  |  |  | 98505 | 28.87 | Sensible
145 | 6020 | 19 | 25 | 40 |  |  |  | 95165 | 27.89 | Sensible
145 | 6020 | 19 | 25 | 43 |  |  |  | 91105 | 26.7 | Sensible
145 | 6020 | 19 | 25 | 46 |  |  |  | 87045 | 25.51 | Sensible
145 | 6020 | 19 | 26 | 25 |  |  |  | 113180 | 33.17 | Sensible
145 | 6020 | 19 | 26 | 30 |  |  |  | 109800 | 32.18 | Sensible
145 | 6020 | 19 | 26 | 35 |  |  |  | 106425 | 31.19 | Sensible
145 | 6020 | 19 | 26 | 40 |  |  |  | 103080 | 30.21 | Sensible
145 | 6020 | 19 | 26 | 43 |  |  |  | 99020 | 29.02 | Sensible
145 | 6020 | 19 | 26 | 46 |  |  |  | 94960 | 27.83 | Sensible
145 | 6020 | 19 | 27 | 25 |  |  |  | 121095 | 35.49 | Sensible
145 | 6020 | 19 | 27 | 30 |  |  |  | 117715 | 34.5 | Sensible
145 | 6020 | 19 | 27 | 35 |  |  |  | 114340 | 33.51 | Sensible
145 | 6020 | 19 | 27 | 40 |  |  |  | 110995 | 32.53 | Sensible
145 | 6020 | 19 | 27 | 43 |  |  |  | 106935 | 31.34 | Sensible
145 | 6020 | 19 | 27 | 46 |  |  |  | 102875 | 30.15 | Sensible
145 | 6020 | 19 | 28 | 25 |  |  |  | 129010 | 37.81 | Sensible
145 | 6020 | 19 | 28 | 30 |  |  |  | 125630 | 36.82 | Sensible
145 | 6020 | 19 | 28 | 35 |  |  |  | 88135 | 25.83 | Sensible
145 | 6020 | 19 | 28 | 40 |  |  |  | 118910 | 34.85 | Sensible
145 | 6020 | 19 | 28 | 43 |  |  |  | 114850 | 33.66 | Sensible
145 | 6020 | 19 | 28 | 46 |  |  |  | 110790 | 32.47 | Sensible
145 | 6020 | 21 | 24 | 25 | 161895 | 47.45 | 16.93 |  |  | Total+Input
145 | 6020 | 21 | 24 | 30 | 157935 | 46.29 | 18.43 |  |  | Total+Input
145 | 6020 | 21 | 24 | 35 | 151150 | 44.3 | 19.8 |  |  | Total+Input
145 | 6020 | 21 | 24 | 40 | 142400 | 41.74 | 21.3 |  |  | Total+Input
145 | 6020 | 21 | 24 | 43 | 137155 | 40.2 | 22.04 |  |  | Total+Input
145 | 6020 | 21 | 24 | 46 | 131905 | 38.66 | 22.78 |  |  | Total+Input
145 | 6020 | 21 | 24 | 25 |  |  |  | 81035 | 23.75 | Sensible
145 | 6020 | 21 | 24 | 30 |  |  |  | 77660 | 22.76 | Sensible
145 | 6020 | 21 | 24 | 35 |  |  |  | 74280 | 21.77 | Sensible
145 | 6020 | 21 | 24 | 40 |  |  |  | 70905 | 20.78 | Sensible
145 | 6020 | 21 | 24 | 43 |  |  |  | 66880 | 19.6 | Sensible
145 | 6020 | 21 | 24 | 46 |  |  |  | 62850 | 18.42 | Sensible
145 | 6020 | 21 | 25 | 25 |  |  |  | 88955 | 26.07 | Sensible
145 | 6020 | 21 | 25 | 30 |  |  |  | 85575 | 25.08 | Sensible
145 | 6020 | 21 | 25 | 35 |  |  |  | 82200 | 24.09 | Sensible
145 | 6020 | 21 | 25 | 40 |  |  |  | 78820 | 23.1 | Sensible
145 | 6020 | 21 | 25 | 43 |  |  |  | 74795 | 21.92 | Sensible
145 | 6020 | 21 | 25 | 46 |  |  |  | 70765 | 20.74 | Sensible
145 | 6020 | 21 | 26 | 25 |  |  |  | 96870 | 28.39 | Sensible
145 | 6020 | 21 | 26 | 30 |  |  |  | 93490 | 27.4 | Sensible
145 | 6020 | 21 | 26 | 35 |  |  |  | 90115 | 26.41 | Sensible
145 | 6020 | 21 | 26 | 40 |  |  |  | 86735 | 25.42 | Sensible
145 | 6020 | 21 | 26 | 43 |  |  |  | 82710 | 24.24 | Sensible
145 | 6020 | 21 | 26 | 46 |  |  |  | 78685 | 23.06 | Sensible
145 | 6020 | 21 | 27 | 25 |  |  |  | 104785 | 30.71 | Sensible
145 | 6020 | 21 | 27 | 30 |  |  |  | 101405 | 29.72 | Sensible
145 | 6020 | 21 | 27 | 35 |  |  |  | 98030 | 28.73 | Sensible
145 | 6020 | 21 | 27 | 40 |  |  |  | 94650 | 27.74 | Sensible
145 | 6020 | 21 | 27 | 43 |  |  |  | 90625 | 26.56 | Sensible
145 | 6020 | 21 | 27 | 46 |  |  |  | 86600 | 25.38 | Sensible
145 | 6020 | 21 | 28 | 25 |  |  |  | 112700 | 33.03 | Sensible
145 | 6020 | 21 | 28 | 30 |  |  |  | 109325 | 32.04 | Sensible
145 | 6020 | 21 | 28 | 35 |  |  |  | 105945 | 31.05 | Sensible
145 | 6020 | 21 | 28 | 40 |  |  |  | 102565 | 30.06 | Sensible
145 | 6020 | 21 | 28 | 43 |  |  |  | 98540 | 28.88 | Sensible
145 | 6020 | 21 | 28 | 46 |  |  |  | 94515 | 27.7 | Sensible
145 | 6020 | 21 | 29 | 25 |  |  |  | 120615 | 35.35 | Sensible
145 | 6020 | 21 | 29 | 30 |  |  |  | 117240 | 34.36 | Sensible
145 | 6020 | 21 | 29 | 35 |  |  |  | 113860 | 33.37 | Sensible
145 | 6020 | 21 | 29 | 40 |  |  |  | 110485 | 32.38 | Sensible
145 | 6020 | 21 | 29 | 43 |  |  |  | 106455 | 31.2 | Sensible
145 | 6020 | 21 | 29 | 46 |  |  |  | 102770 | 30.12 | Sensible
145 | 6020 | 21 | 30 | 25 |  |  |  | 128535 | 37.67 | Sensible
145 | 6020 | 21 | 30 | 30 |  |  |  | 125155 | 36.68 | Sensible
145 | 6020 | 21 | 30 | 35 |  |  |  | 121775 | 35.69 | Sensible
145 | 6020 | 21 | 30 | 40 |  |  |  | 118400 | 34.7 | Sensible
145 | 6020 | 21 | 30 | 43 |  |  |  | 114375 | 33.52 | Sensible
145 | 6020 | 21 | 30 | 46 |  |  |  | 110345 | 32.34 | Sensible
190 | 6020 | 15 | 18 | 25 | 198855 | 58.28 | 19.94 |  |  | Total+Input
190 | 6020 | 15 | 18 | 30 | 183860 | 53.89 | 21.09 |  |  | Total+Input
190 | 6020 | 15 | 18 | 35 | 170195 | 49.88 | 22.2 |  |  | Total+Input
190 | 6020 | 15 | 18 | 40 | 157250 | 46.09 | 23.78 |  |  | Total+Input
190 | 6020 | 15 | 18 | 43 | 150600 | 44.14 | 24.84 |  |  | Total+Input
190 | 6020 | 15 | 18 | 46 | 143950 | 42.19 | 25.9 |  |  | Total+Input
190 | 6020 | 15 | 18 | 25 |  |  |  | 116865 | 34.25 | Sensible
190 | 6020 | 15 | 18 | 30 |  |  |  | 108025 | 31.66 | Sensible
190 | 6020 | 15 | 18 | 35 |  |  |  | 99190 | 29.07 | Sensible
190 | 6020 | 15 | 18 | 40 |  |  |  | 90350 | 26.48 | Sensible
190 | 6020 | 15 | 18 | 43 |  |  |  | 79775 | 23.38 | Sensible
190 | 6020 | 15 | 18 | 46 |  |  |  | 68515 | 20.08 | Sensible
190 | 6020 | 15 | 19 | 25 |  |  |  | 125460 | 36.77 | Sensible
190 | 6020 | 15 | 19 | 30 |  |  |  | 116625 | 34.18 | Sensible
190 | 6020 | 15 | 19 | 35 |  |  |  | 107820 | 31.6 | Sensible
190 | 6020 | 15 | 19 | 40 |  |  |  | 98985 | 29.01 | Sensible
190 | 6020 | 15 | 19 | 43 |  |  |  | 88030 | 25.8 | Sensible
190 | 6020 | 15 | 19 | 46 |  |  |  | 77795 | 22.8 | Sensible
190 | 6020 | 15 | 20 | 25 |  |  |  | 134095 | 39.3 | Sensible
190 | 6020 | 15 | 20 | 30 |  |  |  | 125255 | 36.71 | Sensible
190 | 6020 | 15 | 20 | 35 |  |  |  | 116420 | 34.12 | Sensible
190 | 6020 | 15 | 20 | 40 |  |  |  | 107585 | 31.53 | Sensible
190 | 6020 | 15 | 20 | 43 |  |  |  | 104445 | 30.61 | Sensible
190 | 6020 | 15 | 20 | 46 |  |  |  | 86430 | 25.33 | Sensible
190 | 6020 | 15 | 21 | 25 |  |  |  | 142690 | 41.82 | Sensible
190 | 6020 | 15 | 21 | 30 |  |  |  | 133855 | 39.23 | Sensible
190 | 6020 | 15 | 21 | 35 |  |  |  | 125020 | 36.64 | Sensible
190 | 6020 | 15 | 21 | 40 |  |  |  | 116180 | 34.05 | Sensible
190 | 6020 | 15 | 21 | 43 |  |  |  | 105605 | 30.95 | Sensible
190 | 6020 | 15 | 21 | 46 |  |  |  | 95025 | 27.85 | Sensible
190 | 6020 | 15 | 22 | 25 |  |  |  | 151325 | 44.35 | Sensible
190 | 6020 | 15 | 22 | 30 |  |  |  | 142490 | 41.76 | Sensible
190 | 6020 | 15 | 22 | 35 |  |  |  | 133650 | 39.17 | Sensible
190 | 6020 | 15 | 22 | 40 |  |  |  | 124815 | 36.58 | Sensible
190 | 6020 | 15 | 22 | 43 |  |  |  | 114235 | 33.48 | Sensible
190 | 6020 | 15 | 22 | 46 |  |  |  | 103660 | 30.38 | Sensible
190 | 6020 | 15 | 23 | 25 |  |  |  | 159925 | 46.87 | Sensible
190 | 6020 | 15 | 23 | 30 |  |  |  | 151085 | 44.28 | Sensible
190 | 6020 | 15 | 23 | 35 |  |  |  | 142250 | 41.69 | Sensible
190 | 6020 | 15 | 23 | 40 |  |  |  | 133410 | 39.1 | Sensible
190 | 6020 | 15 | 23 | 43 |  |  |  | 122835 | 36 | Sensible
190 | 6020 | 15 | 23 | 46 |  |  |  | 112255 | 32.9 | Sensible
190 | 6020 | 15 | 24 | 25 |  |  |  | 168555 | 49.4 | Sensible
190 | 6020 | 15 | 24 | 30 |  |  |  | 159720 | 46.81 | Sensible
190 | 6020 | 15 | 24 | 35 |  |  |  | 150880 | 44.22 | Sensible
190 | 6020 | 15 | 24 | 40 |  |  |  | 142045 | 41.63 | Sensible
190 | 6020 | 15 | 24 | 43 |  |  |  | 131465 | 38.53 | Sensible
190 | 6020 | 15 | 24 | 46 |  |  |  | 120890 | 35.43 | Sensible
190 | 6020 | 17 | 20 | 25 | 205310 | 60.17 | 20.41 |  |  | Total+Input
190 | 6020 | 17 | 20 | 30 | 190760 | 55.91 | 21.56 |  |  | Total+Input
190 | 6020 | 17 | 20 | 35 | 177985 | 52.16 | 22.67 |  |  | Total+Input
190 | 6020 | 17 | 20 | 40 | 166045 | 48.67 | 24.25 |  |  | Total+Input
190 | 6020 | 17 | 20 | 43 | 158895 | 46.57 | 25.17 |  |  | Total+Input
190 | 6020 | 17 | 20 | 46 | 151745 | 44.47 | 26.1 |  |  | Total+Input
190 | 6020 | 17 | 20 | 25 |  |  |  | 116350 | 34.1 | Sensible
190 | 6020 | 17 | 20 | 30 |  |  |  | 107515 | 31.51 | Sensible
190 | 6020 | 17 | 20 | 35 |  |  |  | 98680 | 28.92 | Sensible
190 | 6020 | 17 | 20 | 40 |  |  |  | 89840 | 26.33 | Sensible
190 | 6020 | 17 | 20 | 43 |  |  |  | 79265 | 23.23 | Sensible
190 | 6020 | 17 | 20 | 46 |  |  |  | 68685 | 20.13 | Sensible
190 | 6020 | 17 | 21 | 25 |  |  |  | 124950 | 36.62 | Sensible
190 | 6020 | 17 | 21 | 30 |  |  |  | 116115 | 34.03 | Sensible
190 | 6020 | 17 | 21 | 35 |  |  |  | 107275 | 31.44 | Sensible
190 | 6020 | 17 | 21 | 40 |  |  |  | 98440 | 28.85 | Sensible
190 | 6020 | 17 | 21 | 43 |  |  |  | 87860 | 25.75 | Sensible
190 | 6020 | 17 | 21 | 46 |  |  |  | 77285 | 22.65 | Sensible
190 | 6020 | 17 | 22 | 25 |  |  |  | 133580 | 39.15 | Sensible
190 | 6020 | 17 | 22 | 30 |  |  |  | 124745 | 36.56 | Sensible
190 | 6020 | 17 | 22 | 35 |  |  |  | 115910 | 33.97 | Sensible
190 | 6020 | 17 | 22 | 40 |  |  |  | 107070 | 31.38 | Sensible
190 | 6020 | 17 | 22 | 43 |  |  |  | 96495 | 28.28 | Sensible
190 | 6020 | 17 | 22 | 46 |  |  |  | 85915 | 25.18 | Sensible
190 | 6020 | 17 | 23 | 25 |  |  |  | 142180 | 41.67 | Sensible
190 | 6020 | 17 | 23 | 30 |  |  |  | 133345 | 39.08 | Sensible
190 | 6020 | 17 | 23 | 35 |  |  |  | 124505 | 36.49 | Sensible
190 | 6020 | 17 | 23 | 40 |  |  |  | 115670 | 33.9 | Sensible
190 | 6020 | 17 | 23 | 43 |  |  |  | 105090 | 30.8 | Sensible
190 | 6020 | 17 | 23 | 46 |  |  |  | 94515 | 27.7 | Sensible
190 | 6020 | 17 | 24 | 25 |  |  |  | 150780 | 44.19 | Sensible
190 | 6020 | 17 | 24 | 30 |  |  |  | 141975 | 41.61 | Sensible
190 | 6020 | 17 | 24 | 35 |  |  |  | 132390 | 38.8 | Sensible
190 | 6020 | 17 | 24 | 40 |  |  |  | 124300 | 36.43 | Sensible
190 | 6020 | 17 | 24 | 43 |  |  |  | 113725 | 33.33 | Sensible
190 | 6020 | 17 | 24 | 46 |  |  |  | 101305 | 29.69 | Sensible
190 | 6020 | 17 | 25 | 25 |  |  |  | 159410 | 46.72 | Sensible
190 | 6020 | 17 | 25 | 30 |  |  |  | 150575 | 44.13 | Sensible
190 | 6020 | 17 | 25 | 35 |  |  |  | 141735 | 41.54 | Sensible
190 | 6020 | 17 | 25 | 40 |  |  |  | 132900 | 38.95 | Sensible
190 | 6020 | 17 | 25 | 43 |  |  |  | 122325 | 35.85 | Sensible
190 | 6020 | 17 | 25 | 46 |  |  |  | 111745 | 32.75 | Sensible
190 | 6020 | 17 | 26 | 25 |  |  |  | 168010 | 49.24 | Sensible
190 | 6020 | 17 | 26 | 30 |  |  |  | 159170 | 46.65 | Sensible
190 | 6020 | 17 | 26 | 35 |  |  |  | 150335 | 44.06 | Sensible
190 | 6020 | 17 | 26 | 40 |  |  |  | 141500 | 41.47 | Sensible
190 | 6020 | 17 | 26 | 43 |  |  |  | 130920 | 38.37 | Sensible
190 | 6020 | 17 | 26 | 46 |  |  |  | 120345 | 35.27 | Sensible
190 | 6020 | 19 | 22 | 25 | 210950 | 61.83 | 20.88 |  |  | Total+Input
190 | 6020 | 19 | 22 | 30 | 197660 | 57.93 | 22.03 |  |  | Total+Input
190 | 6020 | 19 | 22 | 35 | 186000 | 54.51 | 23.14 |  |  | Total+Input
190 | 6020 | 19 | 22 | 40 | 173800 | 50.94 | 24.72 |  |  | Total+Input
190 | 6020 | 19 | 22 | 43 | 166650 | 48.84 | 25.51 |  |  | Total+Input
190 | 6020 | 19 | 22 | 46 | 159500 | 46.75 | 26.3 |  |  | Total+Input
190 | 6020 | 19 | 22 | 25 |  |  |  | 115840 | 33.95 | Sensible
190 | 6020 | 19 | 22 | 30 |  |  |  | 107005 | 31.36 | Sensible
190 | 6020 | 19 | 22 | 35 |  |  |  | 98165 | 28.77 | Sensible
190 | 6020 | 19 | 22 | 40 |  |  |  | 89330 | 26.18 | Sensible
190 | 6020 | 19 | 22 | 43 |  |  |  | 78750 | 23.08 | Sensible
190 | 6020 | 19 | 22 | 46 |  |  |  | 68175 | 19.98 | Sensible
190 | 6020 | 19 | 23 | 25 |  |  |  | 124440 | 36.47 | Sensible
190 | 6020 | 19 | 23 | 30 |  |  |  | 115600 | 33.88 | Sensible
190 | 6020 | 19 | 23 | 35 |  |  |  | 106765 | 31.29 | Sensible
190 | 6020 | 19 | 23 | 40 |  |  |  | 97925 | 28.7 | Sensible
190 | 6020 | 19 | 23 | 43 |  |  |  | 87350 | 25.6 | Sensible
190 | 6020 | 19 | 23 | 46 |  |  |  | 76770 | 22.5 | Sensible
190 | 6020 | 19 | 24 | 25 |  |  |  | 133035 | 38.99 | Sensible
190 | 6020 | 19 | 24 | 30 |  |  |  | 124300 | 36.43 | Sensible
190 | 6020 | 19 | 24 | 35 |  |  |  | 115395 | 33.82 | Sensible
190 | 6020 | 19 | 24 | 40 |  |  |  | 106560 | 31.23 | Sensible
190 | 6020 | 19 | 24 | 43 |  |  |  | 95950 | 28.12 | Sensible
190 | 6020 | 19 | 24 | 46 |  |  |  | 85370 | 25.02 | Sensible
190 | 6020 | 19 | 25 | 25 |  |  |  | 141670 | 41.52 | Sensible
190 | 6020 | 19 | 25 | 30 |  |  |  | 132830 | 38.93 | Sensible
190 | 6020 | 19 | 25 | 35 |  |  |  | 123995 | 36.34 | Sensible
190 | 6020 | 19 | 25 | 40 |  |  |  | 115155 | 33.75 | Sensible
190 | 6020 | 19 | 25 | 43 |  |  |  | 104580 | 30.65 | Sensible
190 | 6020 | 19 | 25 | 46 |  |  |  | 94005 | 27.55 | Sensible
190 | 6020 | 19 | 26 | 25 |  |  |  | 150265 | 44.04 | Sensible
190 | 6020 | 19 | 26 | 30 |  |  |  | 141430 | 41.45 | Sensible
190 | 6020 | 19 | 26 | 35 |  |  |  | 132595 | 38.86 | Sensible
190 | 6020 | 19 | 26 | 40 |  |  |  | 123755 | 36.27 | Sensible
190 | 6020 | 19 | 26 | 43 |  |  |  | 113180 | 33.17 | Sensible
190 | 6020 | 19 | 26 | 46 |  |  |  | 102600 | 30.07 | Sensible
190 | 6020 | 19 | 27 | 25 |  |  |  | 158900 | 46.57 | Sensible
190 | 6020 | 19 | 27 | 30 |  |  |  | 150060 | 43.98 | Sensible
190 | 6020 | 19 | 27 | 35 |  |  |  | 141225 | 41.39 | Sensible
190 | 6020 | 19 | 27 | 40 |  |  |  | 132390 | 38.8 | Sensible
190 | 6020 | 19 | 27 | 43 |  |  |  | 121810 | 35.7 | Sensible
190 | 6020 | 19 | 27 | 46 |  |  |  | 111235 | 32.6 | Sensible
190 | 6020 | 19 | 28 | 25 |  |  |  | 167500 | 49.09 | Sensible
190 | 6020 | 19 | 28 | 30 |  |  |  | 158660 | 46.5 | Sensible
190 | 6020 | 19 | 28 | 35 |  |  |  | 149825 | 43.91 | Sensible
190 | 6020 | 19 | 28 | 40 |  |  |  | 140985 | 41.32 | Sensible
190 | 6020 | 19 | 28 | 43 |  |  |  | 130410 | 38.22 | Sensible
190 | 6020 | 19 | 28 | 46 |  |  |  | 119830 | 35.12 | Sensible
190 | 6020 | 21 | 24 | 25 | 217410 | 63.72 | 21.35 |  |  | Total+Input
190 | 6020 | 21 | 24 | 30 | 205455 | 60.22 | 22.5 |  |  | Total+Input
190 | 6020 | 21 | 24 | 35 | 193500 | 56.71 | 23.61 |  |  | Total+Input
190 | 6020 | 21 | 24 | 40 | 181560 | 53.21 | 25.19 |  |  | Total+Input
190 | 6020 | 21 | 24 | 43 | 174410 | 51.12 | 26.14 |  |  | Total+Input
190 | 6020 | 21 | 24 | 46 | 167260 | 49.02 | 27.09 |  |  | Total+Input
190 | 6020 | 21 | 24 | 25 |  |  |  | 115295 | 33.79 | Sensible
190 | 6020 | 21 | 24 | 30 |  |  |  | 106455 | 31.2 | Sensible
190 | 6020 | 21 | 24 | 35 |  |  |  | 97620 | 28.61 | Sensible
190 | 6020 | 21 | 24 | 40 |  |  |  | 88785 | 26.02 | Sensible
190 | 6020 | 21 | 24 | 43 |  |  |  | 78205 | 22.92 | Sensible
190 | 6020 | 21 | 24 | 46 |  |  |  | 67630 | 19.82 | Sensible
190 | 6020 | 21 | 25 | 25 |  |  |  | 123925 | 36.32 | Sensible
190 | 6020 | 21 | 25 | 30 |  |  |  | 115090 | 33.73 | Sensible
190 | 6020 | 21 | 25 | 35 |  |  |  | 106250 | 31.14 | Sensible
190 | 6020 | 21 | 25 | 40 |  |  |  | 97415 | 28.55 | Sensible
190 | 6020 | 21 | 25 | 43 |  |  |  | 86840 | 25.45 | Sensible
190 | 6020 | 21 | 25 | 46 |  |  |  | 76260 | 22.35 | Sensible
190 | 6020 | 21 | 26 | 25 |  |  |  | 132525 | 38.84 | Sensible
190 | 6020 | 21 | 26 | 30 |  |  |  | 123685 | 36.25 | Sensible
190 | 6020 | 21 | 26 | 35 |  |  |  | 114850 | 33.66 | Sensible
190 | 6020 | 21 | 26 | 40 |  |  |  | 106015 | 31.07 | Sensible
190 | 6020 | 21 | 26 | 43 |  |  |  | 95435 | 27.97 | Sensible
190 | 6020 | 21 | 26 | 46 |  |  |  | 84860 | 24.87 | Sensible
190 | 6020 | 21 | 27 | 25 |  |  |  | 141155 | 41.37 | Sensible
190 | 6020 | 21 | 27 | 30 |  |  |  | 132320 | 38.78 | Sensible
190 | 6020 | 21 | 27 | 35 |  |  |  | 123485 | 36.19 | Sensible
190 | 6020 | 21 | 27 | 40 |  |  |  | 114645 | 33.6 | Sensible
190 | 6020 | 21 | 27 | 43 |  |  |  | 104070 | 30.5 | Sensible
190 | 6020 | 21 | 27 | 46 |  |  |  | 93490 | 27.4 | Sensible
190 | 6020 | 21 | 28 | 25 |  |  |  | 149755 | 43.89 | Sensible
190 | 6020 | 21 | 28 | 30 |  |  |  | 140920 | 41.3 | Sensible
190 | 6020 | 21 | 28 | 35 |  |  |  | 132080 | 38.71 | Sensible
190 | 6020 | 21 | 28 | 40 |  |  |  | 123245 | 36.12 | Sensible
190 | 6020 | 21 | 28 | 43 |  |  |  | 112665 | 33.02 | Sensible
190 | 6020 | 21 | 28 | 46 |  |  |  | 102090 | 29.92 | Sensible
190 | 6020 | 21 | 29 | 25 |  |  |  | 158355 | 46.41 | Sensible
190 | 6020 | 21 | 29 | 30 |  |  |  | 149515 | 43.82 | Sensible
190 | 6020 | 21 | 29 | 35 |  |  |  | 140715 | 41.24 | Sensible
190 | 6020 | 21 | 29 | 40 |  |  |  | 131875 | 38.65 | Sensible
190 | 6020 | 21 | 29 | 43 |  |  |  | 121265 | 35.54 | Sensible
190 | 6020 | 21 | 29 | 46 |  |  |  | 110690 | 32.44 | Sensible
190 | 6020 | 21 | 30 | 25 |  |  |  | 166985 | 48.94 | Sensible
190 | 6020 | 21 | 30 | 30 |  |  |  | 158150 | 46.35 | Sensible
190 | 6020 | 21 | 30 | 35 |  |  |  | 149310 | 43.76 | Sensible
190 | 6020 | 21 | 30 | 40 |  |  |  | 140475 | 41.17 | Sensible
190 | 6020 | 21 | 30 | 43 |  |  |  | 129895 | 38.07 | Sensible
190 | 6020 | 21 | 30 | 46 |  |  |  | 119320 | 34.97 | Sensible
250 | 7080 | 15 | 18 | 25 | 259675 | 76.11 | 25.62 |  |  | Total+Input
250 | 7080 | 15 | 18 | 30 | 245230 | 71.87 | 27.4 |  |  | Total+Input
250 | 7080 | 15 | 18 | 35 | 230820 | 67.65 | 29.3 |  |  | Total+Input
250 | 7080 | 15 | 18 | 40 | 216410 | 63.43 | 31.32 |  |  | Total+Input
250 | 7080 | 15 | 18 | 43 | 207800 | 60.9 | 32.62 |  |  | Total+Input
250 | 7080 | 15 | 18 | 46 | 199190 | 58.38 | 33.93 |  |  | Total+Input
250 | 7080 | 15 | 18 | 25 |  |  |  | 107345 | 31.46 | Sensible
250 | 7080 | 15 | 18 | 30 |  |  |  | 100315 | 29.4 | Sensible
250 | 7080 | 15 | 18 | 35 |  |  |  | 93285 | 27.34 | Sensible
250 | 7080 | 15 | 18 | 40 |  |  |  | 86225 | 25.27 | Sensible
250 | 7080 | 15 | 18 | 43 |  |  |  | 77935 | 22.84 | Sensible
250 | 7080 | 15 | 18 | 46 |  |  |  | 69675 | 20.42 | Sensible
250 | 7080 | 15 | 19 | 25 |  |  |  | 124575 | 36.51 | Sensible
250 | 7080 | 15 | 19 | 30 |  |  |  | 117545 | 34.45 | Sensible
250 | 7080 | 15 | 19 | 35 |  |  |  | 110620 | 32.42 | Sensible
250 | 7080 | 15 | 19 | 40 |  |  |  | 103590 | 30.36 | Sensible
250 | 7080 | 15 | 19 | 43 |  |  |  | 95300 | 27.93 | Sensible
250 | 7080 | 15 | 19 | 46 |  |  |  | 87010 | 25.5 | Sensible
250 | 7080 | 15 | 20 | 25 |  |  |  | 141910 | 41.59 | Sensible
250 | 7080 | 15 | 20 | 30 |  |  |  | 131260 | 38.47 | Sensible
250 | 7080 | 15 | 20 | 35 |  |  |  | 127850 | 37.47 | Sensible
250 | 7080 | 15 | 20 | 40 |  |  |  | 120855 | 35.42 | Sensible
250 | 7080 | 15 | 20 | 43 |  |  |  | 112530 | 32.98 | Sensible
250 | 7080 | 15 | 20 | 46 |  |  |  | 104205 | 30.54 | Sensible
250 | 7080 | 15 | 21 | 25 |  |  |  | 159170 | 46.65 | Sensible
250 | 7080 | 15 | 21 | 30 |  |  |  | 152180 | 44.6 | Sensible
250 | 7080 | 15 | 21 | 35 |  |  |  | 145215 | 42.56 | Sensible
250 | 7080 | 15 | 21 | 40 |  |  |  | 138190 | 40.5 | Sensible
250 | 7080 | 15 | 21 | 43 |  |  |  | 129895 | 38.07 | Sensible
250 | 7080 | 15 | 21 | 46 |  |  |  | 121605 | 35.64 | Sensible
250 | 7080 | 15 | 22 | 25 |  |  |  | 176505 | 51.73 | Sensible
250 | 7080 | 15 | 22 | 30 |  |  |  | 169475 | 49.67 | Sensible
250 | 7080 | 15 | 22 | 35 |  |  |  | 162380 | 47.59 | Sensible
250 | 7080 | 15 | 22 | 40 |  |  |  | 155455 | 45.56 | Sensible
250 | 7080 | 15 | 22 | 43 |  |  |  | 147130 | 43.12 | Sensible
250 | 7080 | 15 | 22 | 46 |  |  |  | 138805 | 40.68 | Sensible
250 | 7080 | 15 | 23 | 25 |  |  |  | 193735 | 56.78 | Sensible
250 | 7080 | 15 | 23 | 30 |  |  |  | 186740 | 54.73 | Sensible
250 | 7080 | 15 | 23 | 35 |  |  |  | 179815 | 52.7 | Sensible
250 | 7080 | 15 | 23 | 40 |  |  |  | 172750 | 50.63 | Sensible
250 | 7080 | 15 | 23 | 43 |  |  |  | 164495 | 48.21 | Sensible
250 | 7080 | 15 | 23 | 46 |  |  |  | 156270 | 45.8 | Sensible
250 | 7080 | 15 | 24 | 25 |  |  |  | 211105 | 61.87 | Sensible
250 | 7080 | 15 | 24 | 30 |  |  |  | 204075 | 59.81 | Sensible
250 | 7080 | 15 | 24 | 35 |  |  |  | 197080 | 57.76 | Sensible
250 | 7080 | 15 | 24 | 40 |  |  |  | 190155 | 55.73 | Sensible
250 | 7080 | 15 | 24 | 43 |  |  |  | 181830 | 53.29 | Sensible
250 | 7080 | 15 | 24 | 46 |  |  |  | 173505 | 50.85 | Sensible
250 | 7080 | 17 | 20 | 25 | 265255 | 77.74 | 26.57 |  |  | Total+Input
250 | 7080 | 17 | 20 | 30 | 251650 | 73.75 | 28.35 |  |  | Total+Input
250 | 7080 | 17 | 20 | 35 | 237205 | 69.52 | 30.25 |  |  | Total+Input
250 | 7080 | 17 | 20 | 40 | 222830 | 65.31 | 32.27 |  |  | Total+Input
250 | 7080 | 17 | 20 | 43 | 212360 | 62.24 | 33.57 |  |  | Total+Input
250 | 7080 | 17 | 20 | 46 | 201890 | 59.17 | 34.88 |  |  | Total+Input
250 | 7080 | 17 | 20 | 25 |  |  |  | 107550 | 31.52 | Sensible
250 | 7080 | 17 | 20 | 30 |  |  |  | 100485 | 29.45 | Sensible
250 | 7080 | 17 | 20 | 35 |  |  |  | 93455 | 27.39 | Sensible
250 | 7080 | 17 | 20 | 40 |  |  |  | 86530 | 25.36 | Sensible
250 | 7080 | 17 | 20 | 43 |  |  |  | 78205 | 22.92 | Sensible
250 | 7080 | 17 | 20 | 46 |  |  |  | 69880 | 20.48 | Sensible
250 | 7080 | 17 | 21 | 25 |  |  |  | 124780 | 36.57 | Sensible
250 | 7080 | 17 | 21 | 30 |  |  |  | 117855 | 34.54 | Sensible
250 | 7080 | 17 | 21 | 35 |  |  |  | 110790 | 32.47 | Sensible
250 | 7080 | 17 | 21 | 40 |  |  |  | 103760 | 30.41 | Sensible
250 | 7080 | 17 | 21 | 43 |  |  |  | 95470 | 27.98 | Sensible
250 | 7080 | 17 | 21 | 46 |  |  |  | 87180 | 25.55 | Sensible
250 | 7080 | 17 | 22 | 25 |  |  |  | 142080 | 41.64 | Sensible
250 | 7080 | 17 | 22 | 30 |  |  |  | 135085 | 39.59 | Sensible
250 | 7080 | 17 | 22 | 35 |  |  |  | 128090 | 37.54 | Sensible
250 | 7080 | 17 | 22 | 40 |  |  |  | 121130 | 35.5 | Sensible
250 | 7080 | 17 | 22 | 43 |  |  |  | 112805 | 33.06 | Sensible
250 | 7080 | 17 | 22 | 46 |  |  |  | 104480 | 30.62 | Sensible
250 | 7080 | 17 | 23 | 25 |  |  |  | 159375 | 46.71 | Sensible
250 | 7080 | 17 | 23 | 30 |  |  |  | 152415 | 44.67 | Sensible
250 | 7080 | 17 | 23 | 35 |  |  |  | 145390 | 42.61 | Sensible
250 | 7080 | 17 | 23 | 40 |  |  |  | 138360 | 40.55 | Sensible
250 | 7080 | 17 | 23 | 43 |  |  |  | 130035 | 38.11 | Sensible
250 | 7080 | 17 | 23 | 46 |  |  |  | 121710 | 35.67 | Sensible
250 | 7080 | 17 | 24 | 25 |  |  |  | 176710 | 51.79 | Sensible
250 | 7080 | 17 | 24 | 30 |  |  |  | 169680 | 49.73 | Sensible
250 | 7080 | 17 | 24 | 35 |  |  |  | 162755 | 47.7 | Sensible
250 | 7080 | 17 | 24 | 40 |  |  |  | 155725 | 45.64 | Sensible
250 | 7080 | 17 | 24 | 43 |  |  |  | 147400 | 43.2 | Sensible
250 | 7080 | 17 | 24 | 46 |  |  |  | 139075 | 40.76 | Sensible
250 | 7080 | 17 | 25 | 25 |  |  |  | 194045 | 56.87 | Sensible
250 | 7080 | 17 | 25 | 30 |  |  |  | 187015 | 54.81 | Sensible
250 | 7080 | 17 | 25 | 35 |  |  |  | 179985 | 52.75 | Sensible
250 | 7080 | 17 | 25 | 40 |  |  |  | 172955 | 50.69 | Sensible
250 | 7080 | 17 | 25 | 43 |  |  |  | 164665 | 48.26 | Sensible
250 | 7080 | 17 | 25 | 46 |  |  |  | 156375 | 45.83 | Sensible
250 | 7080 | 17 | 26 | 25 |  |  |  | 211310 | 61.93 | Sensible
250 | 7080 | 17 | 26 | 30 |  |  |  | 204280 | 59.87 | Sensible
250 | 7080 | 17 | 26 | 35 |  |  |  | 197320 | 57.83 | Sensible
250 | 7080 | 17 | 26 | 40 |  |  |  | 190290 | 55.77 | Sensible
250 | 7080 | 17 | 26 | 43 |  |  |  | 182000 | 53.34 | Sensible
250 | 7080 | 17 | 26 | 46 |  |  |  | 173705 | 50.91 | Sensible
250 | 7080 | 19 | 22 | 25 | 269050 | 78.85 | 27.52 |  |  | Total+Input
250 | 7080 | 19 | 22 | 30 | 258000 | 75.62 | 29.3 |  |  | Total+Input
250 | 7080 | 19 | 22 | 35 | 246000 | 72.1 | 31.2 |  |  | Total+Input
250 | 7080 | 19 | 22 | 40 | 229180 | 67.17 | 33.22 |  |  | Total+Input
250 | 7080 | 19 | 22 | 43 | 220570 | 64.65 | 34.52 |  |  | Total+Input
250 | 7080 | 19 | 22 | 46 | 211960 | 62.12 | 35.83 |  |  | Total+Input
250 | 7080 | 19 | 22 | 25 |  |  |  | 107720 | 31.57 | Sensible
250 | 7080 | 19 | 22 | 30 |  |  |  | 100690 | 29.51 | Sensible
250 | 7080 | 19 | 22 | 35 |  |  |  | 93730 | 27.47 | Sensible
250 | 7080 | 19 | 22 | 40 |  |  |  | 86700 | 25.41 | Sensible
250 | 7080 | 19 | 22 | 43 |  |  |  | 78375 | 22.97 | Sensible
250 | 7080 | 19 | 22 | 46 |  |  |  | 70050 | 20.53 | Sensible
250 | 7080 | 19 | 23 | 25 |  |  |  | 125050 | 36.65 | Sensible
250 | 7080 | 19 | 23 | 30 |  |  |  | 117990 | 34.58 | Sensible
250 | 7080 | 19 | 23 | 35 |  |  |  | 110995 | 32.53 | Sensible
250 | 7080 | 19 | 23 | 40 |  |  |  | 104070 | 30.5 | Sensible
250 | 7080 | 19 | 23 | 43 |  |  |  | 95745 | 28.06 | Sensible
250 | 7080 | 19 | 23 | 46 |  |  |  | 87420 | 25.62 | Sensible
250 | 7080 | 19 | 24 | 25 |  |  |  | 142315 | 41.71 | Sensible
250 | 7080 | 19 | 24 | 30 |  |  |  | 135390 | 39.68 | Sensible
250 | 7080 | 19 | 24 | 35 |  |  |  | 128330 | 37.61 | Sensible
250 | 7080 | 19 | 24 | 40 |  |  |  | 121300 | 35.55 | Sensible
250 | 7080 | 19 | 24 | 43 |  |  |  | 113010 | 33.12 | Sensible
250 | 7080 | 19 | 24 | 46 |  |  |  | 104715 | 30.69 | Sensible
250 | 7080 | 19 | 25 | 25 |  |  |  | 159615 | 46.78 | Sensible
250 | 7080 | 19 | 25 | 30 |  |  |  | 152620 | 44.73 | Sensible
250 | 7080 | 19 | 25 | 35 |  |  |  | 145560 | 42.66 | Sensible
250 | 7080 | 19 | 25 | 40 |  |  |  | 138630 | 40.63 | Sensible
250 | 7080 | 19 | 25 | 43 |  |  |  | 130340 | 38.2 | Sensible
250 | 7080 | 19 | 25 | 46 |  |  |  | 122050 | 35.77 | Sensible
250 | 7080 | 19 | 26 | 25 |  |  |  | 176880 | 51.84 | Sensible
250 | 7080 | 19 | 26 | 30 |  |  |  | 169955 | 49.81 | Sensible
250 | 7080 | 19 | 26 | 35 |  |  |  | 162890 | 47.74 | Sensible
250 | 7080 | 19 | 26 | 40 |  |  |  | 155895 | 45.69 | Sensible
250 | 7080 | 19 | 26 | 43 |  |  |  | 147570 | 43.25 | Sensible
250 | 7080 | 19 | 26 | 46 |  |  |  | 139245 | 40.81 | Sensible
250 | 7080 | 19 | 27 | 25 |  |  |  | 194215 | 56.92 | Sensible
250 | 7080 | 19 | 27 | 30 |  |  |  | 187220 | 54.87 | Sensible
250 | 7080 | 19 | 27 | 35 |  |  |  | 180155 | 52.8 | Sensible
250 | 7080 | 19 | 27 | 40 |  |  |  | 173230 | 50.77 | Sensible
250 | 7080 | 19 | 27 | 43 |  |  |  | 164905 | 48.33 | Sensible
250 | 7080 | 19 | 27 | 46 |  |  |  | 156580 | 45.89 | Sensible
250 | 7080 | 19 | 28 | 25 |  |  |  | 211445 | 61.97 | Sensible
250 | 7080 | 19 | 28 | 30 |  |  |  | 204520 | 59.94 | Sensible
250 | 7080 | 19 | 28 | 35 |  |  |  | 197525 | 57.89 | Sensible
250 | 7080 | 19 | 28 | 40 |  |  |  | 190460 | 55.82 | Sensible
250 | 7080 | 19 | 28 | 43 |  |  |  | 182170 | 53.39 | Sensible
250 | 7080 | 19 | 28 | 46 |  |  |  | 173880 | 50.96 | Sensible
250 | 7080 | 21 | 24 | 25 | 272920 | 79.99 | 28.47 |  |  | Total+Input
250 | 7080 | 21 | 24 | 30 | 264390 | 77.49 | 30.25 |  |  | Total+Input
250 | 7080 | 21 | 24 | 35 | 249980 | 73.26 | 32.15 |  |  | Total+Input
250 | 7080 | 21 | 24 | 40 | 235460 | 69.01 | 34.17 |  |  | Total+Input
250 | 7080 | 21 | 24 | 43 | 226850 | 66.49 | 35.41 |  |  | Total+Input
250 | 7080 | 21 | 24 | 46 | 218240 | 63.96 | 36.66 |  |  | Total+Input
250 | 7080 | 21 | 24 | 25 |  |  |  | 107990 | 31.65 | Sensible
250 | 7080 | 21 | 24 | 30 |  |  |  | 100590 | 29.48 | Sensible
250 | 7080 | 21 | 24 | 35 |  |  |  | 93900 | 27.52 | Sensible
250 | 7080 | 21 | 24 | 40 |  |  |  | 86905 | 25.47 | Sensible
250 | 7080 | 21 | 24 | 43 |  |  |  | 78580 | 23.03 | Sensible
250 | 7080 | 21 | 24 | 46 |  |  |  | 70255 | 20.59 | Sensible
250 | 7080 | 21 | 25 | 25 |  |  |  | 125225 | 36.7 | Sensible
250 | 7080 | 21 | 25 | 30 |  |  |  | 118230 | 34.65 | Sensible
250 | 7080 | 21 | 25 | 35 |  |  |  | 111235 | 32.6 | Sensible
250 | 7080 | 21 | 25 | 40 |  |  |  | 96935 | 28.41 | Sensible
250 | 7080 | 21 | 25 | 43 |  |  |  | 95915 | 28.11 | Sensible
250 | 7080 | 21 | 25 | 46 |  |  |  | 87590 | 25.67 | Sensible
250 | 7080 | 21 | 26 | 25 |  |  |  | 142590 | 41.79 | Sensible
250 | 7080 | 21 | 26 | 30 |  |  |  | 135525 | 39.72 | Sensible
250 | 7080 | 21 | 26 | 35 |  |  |  | 128500 | 37.66 | Sensible
250 | 7080 | 21 | 26 | 40 |  |  |  | 121470 | 35.6 | Sensible
250 | 7080 | 21 | 26 | 43 |  |  |  | 113180 | 33.17 | Sensible
250 | 7080 | 21 | 26 | 46 |  |  |  | 104885 | 30.74 | Sensible
250 | 7080 | 21 | 27 | 25 |  |  |  | 159820 | 46.84 | Sensible
250 | 7080 | 21 | 27 | 30 |  |  |  | 152790 | 44.78 | Sensible
250 | 7080 | 21 | 27 | 35 |  |  |  | 145865 | 42.75 | Sensible
250 | 7080 | 21 | 27 | 40 |  |  |  | 138805 | 40.68 | Sensible
250 | 7080 | 21 | 27 | 43 |  |  |  | 130510 | 38.25 | Sensible
250 | 7080 | 21 | 27 | 46 |  |  |  | 122220 | 35.82 | Sensible
250 | 7080 | 21 | 28 | 25 |  |  |  | 177155 | 51.92 | Sensible
250 | 7080 | 21 | 28 | 30 |  |  |  | 170125 | 49.86 | Sensible
250 | 7080 | 21 | 28 | 35 |  |  |  | 163095 | 47.8 | Sensible
250 | 7080 | 21 | 28 | 40 |  |  |  | 156065 | 45.74 | Sensible
250 | 7080 | 21 | 28 | 43 |  |  |  | 147740 | 43.3 | Sensible
250 | 7080 | 21 | 28 | 46 |  |  |  | 139415 | 40.86 | Sensible
250 | 7080 | 21 | 29 | 25 |  |  |  | 194830 | 57.1 | Sensible
250 | 7080 | 21 | 29 | 30 |  |  |  | 187460 | 54.94 | Sensible
250 | 7080 | 21 | 29 | 35 |  |  |  | 180430 | 52.88 | Sensible
250 | 7080 | 21 | 29 | 40 |  |  |  | 173435 | 50.83 | Sensible
250 | 7080 | 21 | 29 | 43 |  |  |  | 165110 | 48.39 | Sensible
250 | 7080 | 21 | 29 | 46 |  |  |  | 156785 | 45.95 | Sensible
250 | 7080 | 21 | 30 | 25 |  |  |  | 211750 | 62.06 | Sensible
250 | 7080 | 21 | 30 | 30 |  |  |  | 204755 | 60.01 | Sensible
250 | 7080 | 21 | 30 | 35 |  |  |  | 197695 | 57.94 | Sensible
250 | 7080 | 21 | 30 | 40 |  |  |  | 190665 | 55.88 | Sensible
250 | 7080 | 21 | 30 | 43 |  |  |  | 182375 | 53.45 | Sensible
250 | 7080 | 21 | 30 | 46 |  |  |  | 174085 | 51.02 | Sensible
300 | 9500 | 15 | 18 | 25 | 314595 | 92.2 | 41.25 |  |  | Total+Input
300 | 9500 | 15 | 18 | 30 | 297135 | 87.09 | 44.12 |  |  | Total+Input
300 | 9500 | 15 | 18 | 35 | 279610 | 81.95 | 47.18 |  |  | Total+Input
300 | 9500 | 15 | 18 | 40 | 262185 | 76.84 | 50.43 |  |  | Total+Input
300 | 9500 | 15 | 18 | 43 | 251760 | 73.79 | 52.53 |  |  | Total+Input
300 | 9500 | 15 | 18 | 46 | 241330 | 70.73 | 54.63 |  |  | Total+Input
300 | 9500 | 15 | 18 | 25 |  |  |  | 129895 | 38.07 | Sensible
300 | 9500 | 15 | 18 | 30 |  |  |  | 121365 | 35.57 | Sensible
300 | 9500 | 15 | 18 | 35 |  |  |  | 112870 | 33.08 | Sensible
300 | 9500 | 15 | 18 | 40 |  |  |  | 104340 | 30.58 | Sensible
300 | 9500 | 15 | 18 | 43 |  |  |  | 94310 | 27.64 | Sensible
300 | 9500 | 15 | 18 | 46 |  |  |  | 84315 | 24.71 | Sensible
300 | 9500 | 15 | 19 | 25 |  |  |  | 150745 | 44.18 | Sensible
300 | 9500 | 15 | 19 | 30 |  |  |  | 142215 | 41.68 | Sensible
300 | 9500 | 15 | 19 | 35 |  |  |  | 133855 | 39.23 | Sensible
300 | 9500 | 15 | 19 | 40 |  |  |  | 125360 | 36.74 | Sensible
300 | 9500 | 15 | 19 | 43 |  |  |  | 115330 | 33.8 | Sensible
300 | 9500 | 15 | 19 | 46 |  |  |  | 105295 | 30.86 | Sensible
300 | 9500 | 15 | 20 | 25 |  |  |  | 171695 | 50.32 | Sensible
300 | 9500 | 15 | 20 | 30 |  |  |  | 158830 | 46.55 | Sensible
300 | 9500 | 15 | 20 | 35 |  |  |  | 154705 | 45.34 | Sensible
300 | 9500 | 15 | 20 | 40 |  |  |  | 146240 | 42.86 | Sensible
300 | 9500 | 15 | 20 | 43 |  |  |  | 136175 | 39.91 | Sensible
300 | 9500 | 15 | 20 | 46 |  |  |  | 126075 | 36.95 | Sensible
300 | 9500 | 15 | 21 | 25 |  |  |  | 192610 | 56.45 | Sensible
300 | 9500 | 15 | 21 | 30 |  |  |  | 184150 | 53.97 | Sensible
300 | 9500 | 15 | 21 | 35 |  |  |  | 175720 | 51.5 | Sensible
300 | 9500 | 15 | 21 | 40 |  |  |  | 167225 | 49.01 | Sensible
300 | 9500 | 15 | 21 | 43 |  |  |  | 157160 | 46.06 | Sensible
300 | 9500 | 15 | 21 | 46 |  |  |  | 147130 | 43.12 | Sensible
300 | 9500 | 15 | 22 | 25 |  |  |  | 213560 | 62.59 | Sensible
300 | 9500 | 15 | 22 | 30 |  |  |  | 205065 | 60.1 | Sensible
300 | 9500 | 15 | 22 | 35 |  |  |  | 196465 | 57.58 | Sensible
300 | 9500 | 15 | 22 | 40 |  |  |  | 188105 | 55.13 | Sensible
300 | 9500 | 15 | 22 | 43 |  |  |  | 178040 | 52.18 | Sensible
300 | 9500 | 15 | 22 | 46 |  |  |  | 167940 | 49.22 | Sensible
300 | 9500 | 15 | 23 | 25 |  |  |  | 234405 | 68.7 | Sensible
300 | 9500 | 15 | 23 | 30 |  |  |  | 225945 | 66.22 | Sensible
300 | 9500 | 15 | 23 | 35 |  |  |  | 217585 | 63.77 | Sensible
300 | 9500 | 15 | 23 | 40 |  |  |  | 209020 | 61.26 | Sensible
300 | 9500 | 15 | 23 | 43 |  |  |  | 199025 | 58.33 | Sensible
300 | 9500 | 15 | 23 | 46 |  |  |  | 189095 | 55.42 | Sensible
300 | 9500 | 15 | 24 | 25 |  |  |  | 255425 | 74.86 | Sensible
300 | 9500 | 15 | 24 | 30 |  |  |  | 246930 | 72.37 | Sensible
300 | 9500 | 15 | 24 | 35 |  |  |  | 238465 | 69.89 | Sensible
300 | 9500 | 15 | 24 | 40 |  |  |  | 230075 | 67.43 | Sensible
300 | 9500 | 15 | 24 | 43 |  |  |  | 220010 | 64.48 | Sensible
300 | 9500 | 15 | 24 | 46 |  |  |  | 209945 | 61.53 | Sensible
300 | 9500 | 17 | 20 | 25 | 321355 | 94.18 | 42.78 |  |  | Total+Input
300 | 9500 | 17 | 20 | 30 | 304910 | 89.36 | 45.65 |  |  | Total+Input
300 | 9500 | 17 | 20 | 35 | 287345 | 84.22 | 48.71 |  |  | Total+Input
300 | 9500 | 17 | 20 | 40 | 269960 | 79.12 | 51.96 |  |  | Total+Input
300 | 9500 | 17 | 20 | 43 | 257280 | 75.4 | 54.06 |  |  | Total+Input
300 | 9500 | 17 | 20 | 46 | 244600 | 71.69 | 56.16 |  |  | Total+Input
300 | 9500 | 17 | 20 | 25 |  |  |  | 130135 | 38.14 | Sensible
300 | 9500 | 17 | 20 | 30 |  |  |  | 121570 | 35.63 | Sensible
300 | 9500 | 17 | 20 | 35 |  |  |  | 113075 | 33.14 | Sensible
300 | 9500 | 17 | 20 | 40 |  |  |  | 104715 | 30.69 | Sensible
300 | 9500 | 17 | 20 | 43 |  |  |  | 94615 | 27.73 | Sensible
300 | 9500 | 17 | 20 | 46 |  |  |  | 84550 | 24.78 | Sensible
300 | 9500 | 17 | 21 | 25 |  |  |  | 150985 | 44.25 | Sensible
300 | 9500 | 17 | 21 | 30 |  |  |  | 142590 | 41.79 | Sensible
300 | 9500 | 17 | 21 | 35 |  |  |  | 134060 | 39.29 | Sensible
300 | 9500 | 17 | 21 | 40 |  |  |  | 125565 | 36.8 | Sensible
300 | 9500 | 17 | 21 | 43 |  |  |  | 115535 | 33.86 | Sensible
300 | 9500 | 17 | 21 | 46 |  |  |  | 105500 | 30.92 | Sensible
300 | 9500 | 17 | 22 | 25 |  |  |  | 171900 | 50.38 | Sensible
300 | 9500 | 17 | 22 | 30 |  |  |  | 163435 | 47.9 | Sensible
300 | 9500 | 17 | 22 | 35 |  |  |  | 154975 | 45.42 | Sensible
300 | 9500 | 17 | 22 | 40 |  |  |  | 146580 | 42.96 | Sensible
300 | 9500 | 17 | 22 | 43 |  |  |  | 136480 | 40 | Sensible
300 | 9500 | 17 | 22 | 46 |  |  |  | 126415 | 37.05 | Sensible
300 | 9500 | 17 | 23 | 25 |  |  |  | 192850 | 56.52 | Sensible
300 | 9500 | 17 | 23 | 30 |  |  |  | 184420 | 54.05 | Sensible
300 | 9500 | 17 | 23 | 35 |  |  |  | 175925 | 51.56 | Sensible
300 | 9500 | 17 | 23 | 40 |  |  |  | 167430 | 49.07 | Sensible
300 | 9500 | 17 | 23 | 43 |  |  |  | 157330 | 46.11 | Sensible
300 | 9500 | 17 | 23 | 46 |  |  |  | 147265 | 43.16 | Sensible
300 | 9500 | 17 | 24 | 25 |  |  |  | 213835 | 62.67 | Sensible
300 | 9500 | 17 | 24 | 30 |  |  |  | 205305 | 60.17 | Sensible
300 | 9500 | 17 | 24 | 35 |  |  |  | 196945 | 57.72 | Sensible
300 | 9500 | 17 | 24 | 40 |  |  |  | 188415 | 55.22 | Sensible
300 | 9500 | 17 | 24 | 43 |  |  |  | 178350 | 52.27 | Sensible
300 | 9500 | 17 | 24 | 46 |  |  |  | 168280 | 49.32 | Sensible
300 | 9500 | 17 | 25 | 25 |  |  |  | 234780 | 68.81 | Sensible
300 | 9500 | 17 | 25 | 30 |  |  |  | 226285 | 66.32 | Sensible
300 | 9500 | 17 | 25 | 35 |  |  |  | 217790 | 63.83 | Sensible
300 | 9500 | 17 | 25 | 40 |  |  |  | 209260 | 61.33 | Sensible
300 | 9500 | 17 | 25 | 43 |  |  |  | 199230 | 58.39 | Sensible
300 | 9500 | 17 | 25 | 46 |  |  |  | 189200 | 55.45 | Sensible
300 | 9500 | 17 | 26 | 25 |  |  |  | 255700 | 74.94 | Sensible
300 | 9500 | 17 | 26 | 30 |  |  |  | 247170 | 72.44 | Sensible
300 | 9500 | 17 | 26 | 35 |  |  |  | 238740 | 69.97 | Sensible
300 | 9500 | 17 | 26 | 40 |  |  |  | 230245 | 67.48 | Sensible
300 | 9500 | 17 | 26 | 43 |  |  |  | 220215 | 64.54 | Sensible
300 | 9500 | 17 | 26 | 46 |  |  |  | 210180 | 61.6 | Sensible
300 | 9500 | 19 | 22 | 25 | 325950 | 95.53 | 44.31 |  |  | Total+Input
300 | 9500 | 19 | 22 | 30 | 312600 | 91.62 | 47.18 |  |  | Total+Input
300 | 9500 | 19 | 22 | 35 | 298000 | 87.34 | 50.24 |  |  | Total+Input
300 | 9500 | 19 | 22 | 40 | 277650 | 81.37 | 53.49 |  |  | Total+Input
300 | 9500 | 19 | 22 | 43 | 267300 | 78.34 | 55.59 |  |  | Total+Input
300 | 9500 | 19 | 22 | 46 | 256800 | 75.26 | 57.69 |  |  | Total+Input
300 | 9500 | 19 | 22 | 25 |  |  |  | 130340 | 38.2 | Sensible
300 | 9500 | 19 | 22 | 30 |  |  |  | 121845 | 35.71 | Sensible
300 | 9500 | 19 | 22 | 35 |  |  |  | 113415 | 33.24 | Sensible
300 | 9500 | 19 | 22 | 40 |  |  |  | 104920 | 30.75 | Sensible
300 | 9500 | 19 | 22 | 43 |  |  |  | 94820 | 27.79 | Sensible
300 | 9500 | 19 | 22 | 46 |  |  |  | 84755 | 24.84 | Sensible
300 | 9500 | 19 | 23 | 25 |  |  |  | 151325 | 44.35 | Sensible
300 | 9500 | 19 | 23 | 30 |  |  |  | 142760 | 41.84 | Sensible
300 | 9500 | 19 | 23 | 35 |  |  |  | 134300 | 39.36 | Sensible
300 | 9500 | 19 | 23 | 40 |  |  |  | 125940 | 36.91 | Sensible
300 | 9500 | 19 | 23 | 43 |  |  |  | 115840 | 33.95 | Sensible
300 | 9500 | 19 | 23 | 46 |  |  |  | 105775 | 31 | Sensible
300 | 9500 | 19 | 24 | 25 |  |  |  | 172205 | 50.47 | Sensible
300 | 9500 | 19 | 24 | 30 |  |  |  | 163815 | 48.01 | Sensible
300 | 9500 | 19 | 24 | 35 |  |  |  | 155285 | 45.51 | Sensible
300 | 9500 | 19 | 24 | 40 |  |  |  | 146785 | 43.02 | Sensible
300 | 9500 | 19 | 24 | 43 |  |  |  | 136755 | 40.08 | Sensible
300 | 9500 | 19 | 24 | 46 |  |  |  | 126690 | 37.13 | Sensible
300 | 9500 | 19 | 25 | 25 |  |  |  | 193120 | 56.6 | Sensible
300 | 9500 | 19 | 25 | 30 |  |  |  | 184660 | 54.12 | Sensible
300 | 9500 | 19 | 25 | 35 |  |  |  | 176130 | 51.62 | Sensible
300 | 9500 | 19 | 25 | 40 |  |  |  | 167735 | 49.16 | Sensible
300 | 9500 | 19 | 25 | 43 |  |  |  | 157705 | 46.22 | Sensible
300 | 9500 | 19 | 25 | 46 |  |  |  | 147675 | 43.28 | Sensible
300 | 9500 | 19 | 26 | 25 |  |  |  | 214035 | 62.73 | Sensible
300 | 9500 | 19 | 26 | 30 |  |  |  | 205645 | 60.27 | Sensible
300 | 9500 | 19 | 26 | 35 |  |  |  | 197115 | 57.77 | Sensible
300 | 9500 | 19 | 26 | 40 |  |  |  | 188620 | 55.28 | Sensible
300 | 9500 | 19 | 26 | 43 |  |  |  | 178550 | 52.33 | Sensible
300 | 9500 | 19 | 26 | 46 |  |  |  | 168485 | 49.38 | Sensible
300 | 9500 | 19 | 27 | 25 |  |  |  | 234985 | 68.87 | Sensible
300 | 9500 | 19 | 27 | 30 |  |  |  | 226525 | 66.39 | Sensible
300 | 9500 | 19 | 27 | 35 |  |  |  | 217995 | 63.89 | Sensible
300 | 9500 | 19 | 27 | 40 |  |  |  | 209600 | 61.43 | Sensible
300 | 9500 | 19 | 27 | 43 |  |  |  | 199535 | 58.48 | Sensible
300 | 9500 | 19 | 27 | 46 |  |  |  | 189470 | 55.53 | Sensible
300 | 9500 | 19 | 28 | 25 |  |  |  | 255835 | 74.98 | Sensible
300 | 9500 | 19 | 28 | 30 |  |  |  | 247475 | 72.53 | Sensible
300 | 9500 | 19 | 28 | 35 |  |  |  | 239015 | 70.05 | Sensible
300 | 9500 | 19 | 28 | 40 |  |  |  | 230450 | 67.54 | Sensible
300 | 9500 | 19 | 28 | 43 |  |  |  | 220420 | 64.6 | Sensible
300 | 9500 | 19 | 28 | 46 |  |  |  | 210385 | 61.66 | Sensible
300 | 9500 | 21 | 24 | 25 | 330640 | 96.91 | 45.84 |  |  | Total+Input
300 | 9500 | 21 | 24 | 30 | 320345 | 93.89 | 48.71 |  |  | Total+Input
300 | 9500 | 21 | 24 | 35 | 302825 | 88.75 | 51.77 |  |  | Total+Input
300 | 9500 | 21 | 24 | 40 | 285260 | 83.6 | 55.02 |  |  | Total+Input
300 | 9500 | 21 | 24 | 43 | 274835 | 80.55 | 57.02 |  |  | Total+Input
300 | 9500 | 21 | 24 | 46 | 264410 | 77.49 | 59.03 |  |  | Total+Input
300 | 9500 | 21 | 24 | 25 |  |  |  | 130680 | 38.3 | Sensible
300 | 9500 | 21 | 24 | 30 |  |  |  | 121710 | 35.67 | Sensible
300 | 9500 | 21 | 24 | 35 |  |  |  | 113620 | 33.3 | Sensible
300 | 9500 | 21 | 24 | 40 |  |  |  | 105160 | 30.82 | Sensible
300 | 9500 | 21 | 24 | 43 |  |  |  | 95095 | 27.87 | Sensible
300 | 9500 | 21 | 24 | 46 |  |  |  | 84995 | 24.91 | Sensible
300 | 9500 | 21 | 25 | 25 |  |  |  | 151530 | 44.41 | Sensible
300 | 9500 | 21 | 25 | 30 |  |  |  | 143070 | 41.93 | Sensible
300 | 9500 | 21 | 25 | 35 |  |  |  | 134605 | 39.45 | Sensible
300 | 9500 | 21 | 25 | 40 |  |  |  | 117305 | 34.38 | Sensible
300 | 9500 | 21 | 25 | 43 |  |  |  | 116045 | 34.01 | Sensible
300 | 9500 | 21 | 25 | 46 |  |  |  | 105980 | 31.06 | Sensible
300 | 9500 | 21 | 26 | 25 |  |  |  | 172545 | 50.57 | Sensible
300 | 9500 | 21 | 26 | 30 |  |  |  | 163985 | 48.06 | Sensible
300 | 9500 | 21 | 26 | 35 |  |  |  | 155485 | 45.57 | Sensible
300 | 9500 | 21 | 26 | 40 |  |  |  | 146990 | 43.08 | Sensible
300 | 9500 | 21 | 26 | 43 |  |  |  | 136960 | 40.14 | Sensible
300 | 9500 | 21 | 26 | 46 |  |  |  | 126930 | 37.2 | Sensible
300 | 9500 | 21 | 27 | 25 |  |  |  | 193395 | 56.68 | Sensible
300 | 9500 | 21 | 27 | 30 |  |  |  | 184865 | 54.18 | Sensible
300 | 9500 | 21 | 27 | 35 |  |  |  | 176505 | 51.73 | Sensible
300 | 9500 | 21 | 27 | 40 |  |  |  | 167940 | 49.22 | Sensible
300 | 9500 | 21 | 27 | 43 |  |  |  | 157910 | 46.28 | Sensible
300 | 9500 | 21 | 27 | 46 |  |  |  | 147880 | 43.34 | Sensible
300 | 9500 | 21 | 28 | 25 |  |  |  | 214345 | 62.82 | Sensible
300 | 9500 | 21 | 28 | 30 |  |  |  | 205850 | 60.33 | Sensible
300 | 9500 | 21 | 28 | 35 |  |  |  | 197355 | 57.84 | Sensible
300 | 9500 | 21 | 28 | 40 |  |  |  | 188855 | 55.35 | Sensible
300 | 9500 | 21 | 28 | 43 |  |  |  | 178755 | 52.39 | Sensible
300 | 9500 | 21 | 28 | 46 |  |  |  | 168690 | 49.44 | Sensible
300 | 9500 | 21 | 29 | 25 |  |  |  | 235740 | 69.09 | Sensible
300 | 9500 | 21 | 29 | 30 |  |  |  | 226830 | 66.48 | Sensible
300 | 9500 | 21 | 29 | 35 |  |  |  | 218300 | 63.98 | Sensible
300 | 9500 | 21 | 29 | 40 |  |  |  | 209840 | 61.5 | Sensible
300 | 9500 | 21 | 29 | 43 |  |  |  | 199775 | 58.55 | Sensible
300 | 9500 | 21 | 29 | 46 |  |  |  | 189710 | 55.6 | Sensible
300 | 9500 | 21 | 30 | 25 |  |  |  | 256210 | 75.09 | Sensible
300 | 9500 | 21 | 30 | 30 |  |  |  | 247750 | 72.61 | Sensible
300 | 9500 | 21 | 30 | 35 |  |  |  | 239220 | 70.11 | Sensible
300 | 9500 | 21 | 30 | 40 |  |  |  | 230690 | 67.61 | Sensible
300 | 9500 | 21 | 30 | 43 |  |  |  | 220655 | 64.67 | Sensible
300 | 9500 | 21 | 30 | 46 |  |  |  | 210625 | 61.73 | Sensible
Source: Carrier Miraco Technical Manual 50UB/38BB/40AB (June 2013), all values as printed in the original PDF.
Anomalous source values (reproduced exactly as printed, flagged for caution):
• Size 110, WB15/DB24, Cond46: sensible capacity 94515 Btu/hr breaks the descending trend (prior column values were ~79265). Printed as-is on page 16.
• Size 110, WB17/DB21, Cond46: sensible capacity 114235 Btu/hr breaks the descending trend (prior column value was ~53300). Printed as-is on page 16.
• Size 145, WB19/DB28, Cond35: sensible capacity 88135 Btu/hr breaks the descending trend (neighbors ~114850-129010). Printed as-is on page 17.
• Size 110, WB21/DB28, Cond46: sensible capacity 72680 Btu/hr appears twice in a row (DB28 and DB29 both show 72680) where a smooth progression is expected. Printed as-is on page 16. [Corrected in v2: earlier note wrongly attributed this to Size 145 – see README section C.]
• Size 250, WB21/DB25, Cond40: sensible capacity 96935 Btu/hr breaks the descending trend (prior column ~138805, next ~87590). Printed as-is on page 18.
• Size 300, WB19/DB25, Cond40: sensible capacity 167735 Btu/hr – apparent anomaly but the row is actually monotonic; flagged for review (may be a valid value). Printed as-is on page 20. [Corrected in v2: earlier note wrongly stated this cell held 117305 – that value belongs to WB21/DB25/Cond40 (see next bullet) – see README section C.]
• Size 300, WB21/DB25, Cond40: sensible capacity 117305 Btu/hr (same anomaly pattern) — printed as-is on page 20.
• Size 145, WB21/DB28, Cond46: sensible capacity 94515 Btu/hr breaks the descending trend (prior column Cond43=98540). Printed as-is on page 17. [Added in v2 – see README section C.]
Note on I436: SOURCE ANOMALY (reproduced exactly as printed in the PDF): Breaks descending trend (prior value ~79265). Printed as-is on page 16. This value breaks the otherwise smooth trend of its row/column and is very likely a typesetting error in the original Carrier catalog. Verify with Carrier/Miraco before using this exact condition for a final selection.
Note on I454: SOURCE ANOMALY (reproduced exactly as printed in the PDF): Breaks descending trend (prior value ~53300). Printed as-is on page 16. This value breaks the otherwise smooth trend of its row/column and is very likely a typesetting error in the original Carrier catalog. Verify with Carrier/Miraco before using this exact condition for a final selection.
Note on I568: ANOMALOUS VALUE — added in v2 review. Size 110, WB21, DB28, Cond46: Sensible=72680 is higher than the previous Cond43 value (70290) and identical to the DB29/Cond46 value, breaking the expected monotonic decrease. Likely a print/typesetting error in the original catalog. Do NOT use for final selection. Cross-check with neighboring rows (Cond43=70290, DB29/Cond46=72680).
Note on I721: SOURCE ANOMALY (reproduced exactly as printed in the PDF): Breaks descending trend (neighbors ~114850-129010). Printed as-is on page 17. This value breaks the otherwise smooth trend of its row/column and is very likely a typesetting error in the original Carrier catalog. Verify with Carrier/Miraco before using this exact condition for a final selection.
Note on I760: SOURCE ANOMALY (reproduced exactly as printed in the PDF): Duplicate value pattern vs DB29 row. Printed as-is on page 17. This value breaks the otherwise smooth trend of its row/column and is very likely a typesetting error in the original Carrier catalog. Verify with Carrier/Miraco before using this exact condition for a final selection.
Note on I1124: SOURCE ANOMALY (reproduced exactly as printed in the PDF): Breaks descending trend (prior ~138805, next ~87590). Printed as-is on page 18. This value breaks the otherwise smooth trend of its row/column and is very likely a typesetting error in the original Carrier catalog. Verify with Carrier/Miraco before using this exact condition for a final selection.
Note on I1280: SOURCE ANOMALY (reproduced exactly as printed in the PDF): Breaks descending trend in row. Printed as-is on page 20. This value breaks the otherwise smooth trend of its row/column and is very likely a typesetting error in the original Carrier catalog. Verify with Carrier/Miraco before using this exact condition for a final selection.
Note on I1316: SOURCE ANOMALY (reproduced exactly as printed in the PDF): Breaks descending trend in row. Printed as-is on page 20. This value breaks the otherwise smooth trend of its row/column and is very likely a typesetting error in the original Carrier catalog. Verify with Carrier/Miraco before using this exact condition for a final selection.

## Airflow_Multipliers
Airflow Correction Multipliers (when evap. airflow differs from nominal)
Unit Size | Airflow Point | Airflow (cfm) | Total Capacity Multiplier | Total Input Power Multiplier | Sensible Capacity Multiplier
55 | 1 | 1605 | 0.95 | 0.97 | 0.86
55 | 2 | 1805 | 0.96 | 0.98 | 0.91
55 | 3 | 2005 | 1 | 1 | 1
55 | 4 | 2206 | 1.02 | 1.02 | 1.04
55 | 5 | 2407 | 1.04 | 1.04 | 1.06
90 | 1 | 2407 | 0.95 | 0.97 | 0.87
90 | 2 | 2708 | 0.97 | 0.98 | 0.93
90 | 3 | 3010 | 1 | 1 | 1
90 | 4 | 3310 | 1.04 | 1.02 | 1.08
90 | 5 | 3610 | 1.06 | 1.03 | 1.1
110 | 1 | 2407 | 0.95 | 0.97 | 0.87
110 | 2 | 3186 | 0.98 | 0.98 | 0.93
110 | 3 | 3540 | 1 | 1 | 1
110 | 4 | 3894 | 1.01 | 1.01 | 1.02
110 | 5 | 4048 | 1.02 | 1.03 | 1.13
145 | 1 | 4814 | 0.95 | 0.96 | 0.91
145 | 2 | 5416 | 0.95 | 0.98 | 0.91
145 | 3 | 6020 | 1 | 1 | 1
145 | 4 | 6620 | 1.03 | 1.02 | 1.05
145 | 5 | 7221 | 1.05 | 1.04 | 1.09
190 | 1 | 4814 | 0.95 | 0.96 | 0.91
190 | 2 | 5416 | 0.95 | 0.98 | 0.91
190 | 3 | 6020 | 1 | 1 | 1
190 | 4 | 6620 | 1.03 | 1.02 | 1.05
190 | 5 | 7221 | 1.05 | 1.04 | 1.09
250 | 1 | 5664 | 0.95 | 0.97 | 0.9
250 | 2 | 6372 | 0.96 | 0.98 | 0.94
250 | 3 | 7080 | 1 | 1 | 1
250 | 4 | 7788 | 1.02 | 1.02 | 1.04
250 | 5 | 8495 | 1.04 | 1.03 | 1.09
300 | 1 | 7003 | 0.95 | 0.97 | 0.9
300 | 2 | 7876 | 0.96 | 0.98 | 0.94
300 | 3 | 8752 | 1 | 1 | 1
300 | 4 | 9628 | 1.02 | 1.02 | 1.04
300 | 5 | 10501 | 1.04 | 1.03 | 1.09
Source: Carrier Miraco Technical Manual 50UB/38BB/40AB (June 2013), all values as printed in the original PDF.
1 kW = 860 Kcal/h = 3412 Btu/h = 0.284 Refrigeration Tons.
⚠ SIZE 300 AIRFLOW CONFLICT: The PDF capacity table header (page 20) states nominal airflow = 9500 cfm, but the multiplier footnote on the same page uses 8752 cfm as the 100% reference point (Airflow Point 3 above). This workbook reproduces both as printed. Use 9500 cfm for HAP airflow comparison; use 8752 cfm as the multiplier reference when applying the table above. Contact Carrier/Miraco for clarification.

## Physical_Condensing
6. Physical Data of Condensing Units (38BB)
Parameter | 38BB-55 | 38BB-90 | 38BB-110 | 38BB-145 | 38BB-190 | 38BB-250 | 38BB-300
Compressor Type | Recip. | Recip. | Recip. | Recip. | Scroll | Scroll | Scroll
Compressor Quantity | 1 | 1 | 2 | 2 | 2 | 2 | 2
Input Power (kW) | 5.66 | 7.98 | 5.66 | 7.13 | 8.97 | 11.6 | 13.63
Input Current (A) | 9.54 | 14.59 | 9.54 | 11.58 | 16.37 | 20.44 | 24.19
Locked Rotor Amperes - LRA (A) | 67 | 90 | 67 | 80 | 130 | 145 | 175
Motor Cutout Current (A) | 15 | 22 | 15 | 18 | 29 | 32 | 35
Displacement (cm3/rev) | 107.71 | 171.26 | 107.71 | 135.78 | 166.66 | 216.64 | 249.9
Displacement (m3/hr) | 18.74 | 29.8 | 18.74 | 23.63 | 29 | 37.69 | 43.49
Oil Charge (dm3) | 1.8 | 3.9 | 1.8 | 1.8 | 3.25 | 3.31 | 6.21
Crankcase Heater Qty x Watts (optional) | 1x30 | 1x35 | 2x30 | 2x35 | 2x65 | 2x65 | 2x75
Condenser Motor Power (kW) | 1.5 | 2.2 | 3 | 3 | 3 | 4 | 5.5
Condenser Motor Current (A) | 3.43 | 4.74 | 6.45 | 6.45 | 6.45 | 8.27 | 11.49
Condenser Motor Speed (RPM) | 1420 | 1420 | 1420 | 1420 | 1420 | 1440 | 1455
Sound Level (dB(A)) | 48 | 53 | 53 | 53 | 53 | 53 | 62
Compressor Frame Size | 090 S | 100 L | 100 L | 100 L | 100 L | 12 M | 132 S
Compressor Weight (kg) | 12.9 | 21 | 24 | 24 | 24 | 30.5 | 41
Condenser Blower Quantity | 1 | 2 | 2 | 2 | 2 | 2 | 2
Nominal Air Flow (m3/hr) | 5250 | 9500 | 10000 | 13000 | 13000 | 18000 | 24800
Air Flow Range (m3/hr) | 4200-6300 | 7600-11,400 | 8000-12,000 | 10,400-15,600 | 10,400-15,600 | 14,400-21,600 | 19840-29760
Condenser Coil Face Area (m2) | 0.49 | 0.9 | 0.9 | 1.16 | 1.16 | 1.71 | 2.12
Condenser Coil Rows-Tube Diam. | 5-3/8" | 4-3/8" | 5-3/8" | 5-3/8" | 5-5/8" | 6-1/2" | 6-3/8"
Condenser Coil Fins per Inch | 14 | 14 | 14 | 14 | 14 | 12 | 14
Width (mm) | 890 | 1338 | 1338 | 1593 | 1593 | 2088 | 2526
Height (mm) | 1069 | 1165 | 1165 | 1405 | 1405 | 1405 | 1408
Depth (mm) | 753 | 766 | 766 | 824 | 824 | 1060 | 1080
Height with Feet (mm) | 1169 | 1265 | 1265 | 1505 | 1505 | 1505 | 1498
Net Weight (kg) | 170 | 290 | 320 | 355 | 355 | 635 | 668
Suction Line (Dia-Qty) | 7/8" - 1 | 1-1/8" - 1 | 7/8" – 2 | 1-1/8" – 2 | 1-1/8" – 2 | 1-1/8" – 2 | 1-3/8" – 2
Liquid Line (Dia-Qty) | 1/2" - 1 | 1/2" - 1 | 1/2" - 2 | 1/2" - 2 | 1/2" - 2 | 5/8" - 2 | 7/8" - 2
Constant across all sizes:
Compressor Power Supply: 380-400 V/3Ph/50Hz
Rpm 50Hz: 2900
Overload Protector: Internal
Crankcase Heater Supply: 220V/1PH
Crankcase Heater Type: PTCR
Condenser Motor Power Supply: 400 ± 10% V/3Ph/50Hz
Efficiency Class: EFF2
Type Of Construction: IM B3
Frame Material: Aluminum
Degree Of Protection: IP55
Method Of Cooling: IC 411 (TEFC)
Vibration Class: N (Standard)
Insulation Class: F
Duty Type: S1
Standards: IEC, DIN, ISO, VDE, EN
Blower Type: Centrifugal - Double Inlet - Forward Curved Blades
Coil Tubes Fins: Inner Grooved Copper Tubes - Corrugated Aluminum Fins
Coil Test Pressure Bar: 30
Blower Pulley Type: Fixed Pitch - Cast Iron
Motor Pulley Type: Adjustable Pitch - Cast Iron
Source: Carrier Miraco Technical Manual 50UB/38BB/40AB (June 2013), all values as printed in the original PDF.
Note on F24: CORRECTION (v2 review): Original Excel had 5-3/8" — corrected to 5-5/8" per engineering review. Note: PDF text extraction shows 5-3/8" in the printed table; verify against physical unit nameplate.

## Physical_Evaporator
7. Physical Data of Evaporator Units (40AB)
Parameter | 40AB-55 | 40AB-90 | 40AB-110 | 40AB-145 | 40AB-190 | 40AB-250 | 40AB-300
Evaporator Motor Power (kW) | 0.75 | 1.1 | 1.5 | 2.2 | 2.2 | 4 | 5.5
Evaporator Motor Current (A) | 1.88 | 2.57 | 3.43 | 4.74 | 4.74 | 8.27 | 11.49
Evaporator Motor Speed (RPM) | 1395 | 1415 | 1420 | 1420 | 1420 | 1440 | 1455
Rated Starting Current (A) | 4.2 | 4.6 | 5.3 | 5.6 | 5.6 | 6 | 6.3
Sound Level (dB(A)) | 47 | 48 | 48 | 53 | 53 | 53 | 62
Motor Frame Size | 080 M | 090 S | 090 S | 100 L | 100 L | 112 M | 132 S
Motor Weight (kg) | 10 | 12.9 | 12.9 | 21 | 21 | 30.5 | 41
Evaporator Blower Quantity | 1 | 2 | 2 | 2 | 2 | 2 | 2
Nominal Air Flow (m3/hr) | 3400 | 5100 | 6000 | 10200 | 10200 | 12000 | 16100
Air Flow Range (m3/hr) | 2750-4080 | 4080-6120 | 4800-7200 | 8160-12,240 | 8160-12,240 | 9600-14,400 | 14400-17800
Evaporator Coil Face Area (m2) | 0.3 | 0.64 | 0.7 | 0.77 | 0.77 | 1.14 | 1.34
Evaporator Coil Rows-Tube Diam. | 4-3/8" | 4-3/8" | 5-3/8" | 4-3/8" | 4-3/8" | 6-1/2" | 6-3/8"
Evaporator Coil Fins per Inch | 14 | 14 | 14 | 14 | 12 | 12 | 14
Expansion Device Quantity | 1 | 1 | 2 | 2 | 2 | 2 | 2
Electric Heater Total Output (kW) | 5 | 15 | 15 | 18 | 18 | 22.5 | 24
Number of Heating Elements | 5 | 6 | 6 | 6 | 6 | 9 | 12
kW per Heating Element | 1 | 2.5 | 2.5 | 3 | 3 | 2.5 | 2
Number of Heating Stages | 1 | 1 | 2 | 2 | 2 | 2 | 2
Heater Full Load Amperes (A) | 9.1 | 22.8 | 22.8 | 27.4 | 27.4 | 34.2 | 36.5
Air Filter Media | Aluminum | Aluminum | Aluminum | Aluminum | Aluminum | Aluminum | Polyurethane
Width (mm) | 890 | 1338 | 1338 | 1593 | 1593 | 2088 | 2665
Height (mm) | 536 | 663 | 663 | 792 | 792 | 654 | 750
Depth (mm) | 753 | 766 | 766 | 824 | 824 | 1060 | 1154
Depth with Heater (mm) | 922.5 | 939.5 | 939.5 | 997 | 997 | 1234.5 | 1328.5
Net Weight (kg) | 85 | 125 | 140 | 205 | 205 | 310 | 365
Suction Line (Dia-Qty) | 7/8" - 1 | 1-1/8" – 1 | 7/8" – 2 | 1-1/8" – 2 | 1-1/8" – 2 | 1-1/8" – 2 | 1-3/8" – 2
Liquid Line (Dia-Qty) | 1/2" - 1 | 1/2" – 1 | 1/2" - 2 | 1/2" - 2 | 1/2" - 2 | 5/8" – 2 | 7/8" – 2
Constant across all sizes:
Power Supply: 400 ± 10% V/3Ph/50Hz
Efficiency Class: EFF2
Type Of Construction: IM B3
Frame Material: Aluminum
Degree Of Protection: IP55
Method Of Cooling: IC 411 (TEFC)
Vibration Class: N (Standard)
Insulation Class: F
Duty Type: S1
Standards: IEC, DIN, ISO, VDE, EN
Blower Type: Centrifugal - Double Inlet - Forward Curved Blades
Coil Tubes Fins: Inner Grooved Copper Tubes - Corrugated Aluminum Fins
Coil Test Pressure Bar: 30
Refrigerant: R22
Expansion Device Type: Thermostatic Expansion Valve with External Equalizer
Blower Pulley Type: Fixed Pitch - Cast Iron
Motor Pulley Type: Adjustable Pitch - Cast Iron
Source: Carrier Miraco Technical Manual 50UB/38BB/40AB (June 2013), all values as printed in the original PDF.
Note on G15: CORRECTION (v2 review): Original Excel had 5-1/2" — corrected to 6-1/2" per engineering review. Note: PDF text extraction shows 5-1/2" in the printed table; verify against physical unit nameplate.

## Electrical_Data
8. Electrical Data (System Level)
Parameter | Size 55 | Size 90 | Size 110 | Size 145 | Size 190 | Size 250 | Size 300
Cooling Consumption (kW) | 7.91 | 11.28 | 15.82 | 19.46 | 23.14 | 31.2 | 50.24
Cooling Consumption (Amps) | 14.8 | 21.9 | 29 | 34.3 | 43.9 | 57.4 | 71.4
Heating Consumption (kW) | 6.75 | 16.1 | 16.5 | 20.2 | 20.2 | 26.5 | 29.5
Heating Consumption (Amps) | 11 | 25.4 | 26.2 | 32.1 | 32.1 | 42.5 | 48
Starting Current (Amps) | 76.5 | 100.2 | 77.9 | 91.2 | 141.2 | 157 | 187.6
Mains Fuse Rating (Amps) | 25 | 40 | 50 | 80 | 80 | 100 | 125
Mains Power Switch (Amps) | 25 | 40 | 50 | 80 | 80 | 100 | 125
Wiring Section (mm2) | 6 | 10 | 16 | 35 | 35 | 35 | 35
Minimum Volts | 360 | 360 | 360 | 360 | 340 | 340 | 340
Maximum Volts | 440 | 440 | 440 | 440 | 440 | 440 | 440
Nominal Power Supply: 380-400 V / 3Ph / 50Hz (all sizes).
• Nominal Power Supply: 380-400 V/3Ph/50Hz.
• (1) Cooling consumption/amps at Outdoor air temp 35C db, Indoor air temp 19C wb.
• (2) Mains fuses and mains power switch are field installed; installer places 3 fuses + 1 mains isolator of capacities shown.
• (3) Wiring section refers to copper conductors, 3-core cable, max length 20m; for lengths exceeding 20m, resize wires accordingly.
Source: Carrier Miraco Technical Manual 50UB/38BB/40AB (June 2013), all values as printed in the original PDF.

## General_Specs
2-4. General Guide Specifications (narrative reference)
• System type: Air Cooled, Vertical Packaged (50UB) or Split (38BB condensing + 40AB evaporator).
• Refrigerant: R22.
• Compressor: Heavy-duty R22 hermetic reciprocating for sizes 55-90-110-145; heavy-duty R22 hermetic scroll (with oil sight glass) for sizes 190-250-300.
• Two independent refrigerant circuits for sizes 110, 145, 190, 250, 300 (partial load operation capability).
• Complies with CE safety regulations: Low Voltage Directive (LVD), EMC Directive, Pressure Equipment Directive (PED).
• Coils leak tested at 450 PSI (condenser & evaporator per guide specs) / test pressure 30 bar per physical data tables.
• Air filters: Long-life cleanable bonded EZ KLEAN aluminum media for sizes 55-90-110-145-190-250; Polyurethane air filter for size 300.
• Thermostat: INSTAT7-type electronic thermostat (220V supply) for sizes 55-110-145-190-250, Cool/Heat, Fan On/Auto, two-stage capable. Dedicated wall thermostat with LCD for size 300.
• Electric heater: Finned aluminum elements, VDE standard, thermal protection & temperature limiter included.
• Options: Crankcase heater, precoated aluminum condenser fins (corrosion protection), conversion kit for evaporator vertical discharge.
• Safety protections: Dual pressure control (high/low), low pressure control for refrigerant leak (size 300 only), 4-min anti-short-cycle time delay, 1-min delay between dual compressors starting, internal pressure relief valve, internal & external overloads, phase reversal/phase loss voltage protector. All electrical components UL approved.
• Vertical packaged air delivery arrangements: A) Horizontal back return / Vertical discharge, B) Horizontal back return / Horizontal front discharge, C) Horizontal front return / Vertical discharge, D) Horizontal front return / Horizontal back discharge.
• Split system factory default: horizontal air discharge; field-convertible to vertical discharge via accessory supports.
Source: Carrier Miraco Technical Manual 50UB/38BB/40AB (June 2013), all values as printed in the original PDF.