## Equipment_Models
system_model | nominal_kbtu | indoor_model | outdoor_model | cooling_btuh | cooling_input_w | cooling_current_a | heating_btuh | eer_btu_wh | eer_ww | cop_ww | max_esp_inwg | indoor_weight_kg | indoor_dims_mm | power_supply | compressor_type | refrigerant_type | outdoor_sound_dba | outdoor_dims_mm | outdoor_weight_kg | pipe_liquid_inch | pipe_gas_inch | max_pipe_length_m | max_height_diff_m | drain_hose_mm | nominal_airflow_cfm | nominal_airflow_m3h | indoor_sound_dba | heating_input_w | heating_current_a
53QDMT12-718 | 12 | 42QDMT12-718 | 38QDMT12-718 | 13000 | 1265 | 5.9 | 12700 | 10.28 | 3.01 | 3.56 | 0.16 | 20 | 700 × 210 × 635 | 220-240/1/50
53QDMT18-718 | 18 | 42QDMT18-718 | 38QDMT18-718 | 20500 | 1985 | 9.2 | 19000 | 10.33 | 3.03 | 3.28 | 0.24 | 24 | 920 × 210 × 635 | 220-240/1/50
53QDMT24-718 | 24 | 42QDMT24-718 | 38QDMT24-718 | 25700 | 2415 | 11.2 | 23500 | 10.64 | 3.12 | 3.24 | 0.24 | 28 | 920 × 270 × 635 | 220-240/1/50
53QDMT30-718 | 30 | 42QDMT30-718 | 38QDMT30-718 | 30000 | 3515 | 16.3 | 31000 | 8.53 | 2.5 | 3.3 | 0.32 | 41 | 1140 × 270 × 775 | 220-240/1/50 | Rotary | R22 / Flare | 62 | 860 × 570 × 350 | 62.4 | 3/8 | 3/4 | 25 | 10 | 25 | 910 | 1542 | 48.2 / 42.4 / 40.8 @ 0.16 in.wg (High/Medium/Low) | 2755 | 12.3
53QDMT36-718 | 36 | 42QDMT36-718 | 38QDMT36-718 | 37600 | 4195 | 20.9 | 37500 | 8.96 | 2.63 | 3.41 | 0.32 | 41 | 1140 × 270 × 775 | 220-240/1/50 | Reciprocating | R22 / Flare | 65 | 860 × 720 × 350 | 81 | 3/8” | 3/4” | 25 | 10 | 25 | 1080 / 730 / 645 | 1831 / 1237 / 1093 | 48.6 / 42.4 / 40.8 | 3220 | 16.8
53QDMT42-718 | 42 | 42QDMT42-718 | 38QDMT42-718 | 40000 | 4555 | 22.5 | 37500 | 8.78 | 2.57 | 3.43 | 0.4 | 47 | 1200 × 300 × 865 | 220-240/1/50 | Reciprocating | R22 / Flare | 65 | 860 × 720 × 350 | 81 | 3/8” | 3/4” | 25 | 10 | 25 | 1370 / 880 / 715 | 2322 / 1492 / 1212 | 48.2 / 40.6 / 38.4 | 3200 | 16.9
53QDMT48-518 | 48 | 42QDMT48-718 | 38QDMT48-518 | 44500 | 4200 | 7.5 | 47500 | 10.59 | 3.1 | 3.67 | 0.4 | 47 | 1200 × 300 × 865 | 380-420/3/50 | Scroll | R22 / Flare | 68 | 860 × 1150 × 350 | 90 | 3/8” | 3/4” | 30 | 15 | 25 | 1370 / 880 / 715 | 2322 / 1492 / 1212 | 48.2 / 40.6 / 38.4 | 3795 | 6.7
53QDMT60-518 | 60 | 42QDMT60-718 | 38QDMT60-518 | 52300 | 4725 | 8.3 | 55300 | 11.07 | 3.24 | 3.9 | 0.4 | 47 | 1200 × 300 × 865 | 380-420/3/50 | Scroll | R22 / Flare | 69 | 860 × 1150 × 350 | 92 | 3/8” | 3/4” | 30 | 15 | 25 | 1470 / 1020 / 860 | 2492 / 1729 / 1458 | 50.4 / 44.3 / 41.5 | 4155 | 7.6

## Airflow
system_model | nominal_kbtu | fan_speed | esp_inwg | airflow_cfm | airflow_m3h | esp_pa
53QDMT18-718 | 18 | High | 0 | 530 | 898 | 0
53QDMT18-718 | 18 | High | 0.04 | 508 | 861 | 10
53QDMT18-718 | 18 | High | 0.08 | 487 | 825 | 20
53QDMT18-718 | 18 | High | 0.12 | 465 | 788 | 30
53QDMT18-718 | 18 | High | 0.16 | 444 | 753 | 40
53QDMT18-718 | 18 | High | 0.2 | 423 | 717 | 50
53QDMT18-718 | 18 | High | 0.24 | 401 | 680 | 60
53QDMT18-718 | 18 | Medium | 0 | 350 | 593 | 0
53QDMT18-718 | 18 | Medium | 0.04 | 329 | 558 | 10
53QDMT18-718 | 18 | Medium | 0.08 | 308 | 522 | 20
53QDMT18-718 | 18 | Medium | 0.12 | 288 | 488 | 30
53QDMT18-718 | 18 | Medium | 0.16 | 267 | 453 | 40
53QDMT18-718 | 18 | Medium | 0.2 | 246 | 417 | 50
53QDMT18-718 | 18 | Medium | 0.24 | 226 | 383 | 60
53QDMT18-718 | 18 | Low | 0 | 295 | 500 | 0
53QDMT18-718 | 18 | Low | 0.04 | 276 | 468 | 10
53QDMT18-718 | 18 | Low | 0.08 | 256 | 434 | 20
53QDMT18-718 | 18 | Low | 0.12 | 237 | 402 | 30
53QDMT18-718 | 18 | Low | 0.16 | 218 | 369 | 40
53QDMT18-718 | 18 | Low | 0.2 | 199 | 337 | 50
53QDMT18-718 | 18 | Low | 0.24 | 180 | 305 | 60
53QDMT12-718 | 12 | High | 0 | 400 | 678 | 0
53QDMT12-718 | 12 | High | 0.04 | 375 | 636 | 10
53QDMT12-718 | 12 | High | 0.08 | 344 | 583 | 20
53QDMT12-718 | 12 | High | 0.12 | 312 | 529 | 30
53QDMT12-718 | 12 | High | 0.16 | 275 | 466 | 40
53QDMT12-718 | 12 | Medium | 0 | 290 | 492 | 0
53QDMT12-718 | 12 | Medium | 0.04 | 267 | 453 | 10
53QDMT12-718 | 12 | Medium | 0.08 | 242 | 410 | 20
53QDMT12-718 | 12 | Medium | 0.12 | 220 | 373 | 30
53QDMT12-718 | 12 | Medium | 0.16 | 193 | 327 | 40
53QDMT12-718 | 12 | Low | 0 | 250 | 424 | 0
53QDMT12-718 | 12 | Low | 0.04 | 228 | 386 | 10
53QDMT12-718 | 12 | Low | 0.08 | 203 | 344 | 20
53QDMT12-718 | 12 | Low | 0.12 | 180 | 305 | 30
53QDMT12-718 | 12 | Low | 0.16 | 156 | 264 | 40
53QDMT24-718 | 24 | High | 0 | 755 | 1280 | 0
53QDMT24-718 | 24 | High | 0.04 | 713 | 1208 | 10
53QDMT24-718 | 24 | High | 0.08 | 683 | 1158 | 20
53QDMT24-718 | 24 | High | 0.12 | 651 | 1103 | 30
53QDMT24-718 | 24 | High | 0.16 | 614 | 1041 | 40
53QDMT24-718 | 24 | High | 0.2 | 580 | 983 | 50
53QDMT24-718 | 24 | High | 0.24 | 545 | 924 | 60
53QDMT24-718 | 24 | Medium | 0 | 495 | 839 | 0
53QDMT24-718 | 24 | Medium | 0.04 | 455 | 771 | 10
53QDMT24-718 | 24 | Medium | 0.08 | 419 | 710 | 20
53QDMT24-718 | 24 | Medium | 0.12 | 373 | 632 | 30
53QDMT24-718 | 24 | Medium | 0.16 | 330 | 559 | 40
53QDMT24-718 | 24 | Medium | 0.2 | 290 | 491 | 50
53QDMT24-718 | 24 | Medium | 0.24 | 249 | 422 | 60
53QDMT24-718 | 24 | Low | 0 | 430 | 729 | 0
53QDMT24-718 | 24 | Low | 0.04 | 379 | 642 | 10
53QDMT24-718 | 24 | Low | 0.08 | 335 | 568 | 20
53QDMT24-718 | 24 | Low | 0.12 | 288 | 488 | 30
53QDMT24-718 | 24 | Low | 0.16 | 236 | 400 | 40
53QDMT24-718 | 24 | Low | 0.2 | 188 | 319 | 50
53QDMT24-718 | 24 | Low | 0.24 | 141 | 239 | 60
53QDMT36-718 | 36 | High | 0 | 1080 | 1831 | 0
53QDMT36-718 | 36 | High | 0.04 | 1036 | 1756 | 10
53QDMT36-718 | 36 | High | 0.08 | 1005 | 1703 | 20
53QDMT36-718 | 36 | High | 0.12 | 976 | 1654 | 30
53QDMT36-718 | 36 | High | 0.16 | 947 | 1605 | 40
53QDMT36-718 | 36 | High | 0.2 | 915 | 1551 | 50
53QDMT36-718 | 36 | High | 0.24 | 883 | 1497 | 60
53QDMT36-718 | 36 | High | 0.28 | 851 | 1442 | 70
53QDMT36-718 | 36 | High | 0.32 | 819 | 1388 | 80
53QDMT36-718 | 36 | Medium | 0 | 730 | 1237 | 0
53QDMT36-718 | 36 | Medium | 0.04 | 690 | 1169 | 10
53QDMT36-718 | 36 | Medium | 0.08 | 657 | 1114 | 20
53QDMT36-718 | 36 | Medium | 0.12 | 624 | 1058 | 30
53QDMT36-718 | 36 | Medium | 0.16 | 591 | 1002 | 40
53QDMT36-718 | 36 | Medium | 0.2 | 550 | 932 | 50
53QDMT36-718 | 36 | Medium | 0.24 | 509 | 863 | 60
53QDMT36-718 | 36 | Medium | 0.28 | 468 | 793 | 70
53QDMT36-718 | 36 | Medium | 0.32 | 427 | 724 | 80
53QDMT36-718 | 36 | Low | 0 | 645 | 1093 | 0
53QDMT36-718 | 36 | Low | 0.04 | 596 | 1010 | 10
53QDMT36-718 | 36 | Low | 0.08 | 562 | 952 | 20
53QDMT36-718 | 36 | Low | 0.12 | 525 | 890 | 30
53QDMT36-718 | 36 | Low | 0.16 | 495 | 839 | 40
53QDMT36-718 | 36 | Low | 0.2 | 453 | 768 | 50
53QDMT36-718 | 36 | Low | 0.24 | 411 | 697 | 60
53QDMT36-718 | 36 | Low | 0.28 | 369 | 625 | 70
53QDMT36-718 | 36 | Low | 0.32 | 327 | 554 | 80
53QDMT42-718 | 42 | High | 0 | 1370 | 2322 | 0
53QDMT42-718 | 42 | High | 0.04 | 1333 | 2259 | 10
53QDMT42-718 | 42 | High | 0.08 | 1300 | 2203 | 20
53QDMT42-718 | 42 | High | 0.12 | 1255 | 2127 | 30
53QDMT42-718 | 42 | High | 0.16 | 1223 | 2073 | 40
53QDMT42-718 | 42 | High | 0.2 | 1187 | 2012 | 50
53QDMT42-718 | 42 | High | 0.24 | 1151 | 1951 | 60
53QDMT42-718 | 42 | High | 0.28 | 1115 | 1890 | 70
53QDMT42-718 | 42 | High | 0.32 | 1079 | 1829 | 80
53QDMT42-718 | 42 | High | 0.36 | 1043 | 1768 | 90
53QDMT42-718 | 42 | High | 0.4 | 1007 | 1707 | 100
53QDMT42-718 | 42 | Medium | 0 | 880 | 1492 | 0
53QDMT42-718 | 42 | Medium | 0.04 | 835 | 1415 | 10
53QDMT42-718 | 42 | Medium | 0.08 | 803 | 1361 | 20
53QDMT42-718 | 42 | Medium | 0.12 | 770 | 1305 | 30
53QDMT42-718 | 42 | Medium | 0.16 | 733 | 1242 | 40
53QDMT42-718 | 42 | Medium | 0.2 | 693 | 1175 | 50
53QDMT42-718 | 42 | Medium | 0.24 | 653 | 1107 | 60
53QDMT42-718 | 42 | Medium | 0.28 | 613 | 1039 | 70
53QDMT42-718 | 42 | Medium | 0.32 | 573 | 971 | 80
53QDMT42-718 | 42 | Medium | 0.36 | 533 | 903 | 90
53QDMT42-718 | 42 | Medium | 0.4 | 493 | 836 | 100
53QDMT42-718 | 42 | Low | 0 | 715 | 1212 | 0
53QDMT42-718 | 42 | Low | 0.04 | 668 | 1132 | 10
53QDMT42-718 | 42 | Low | 0.08 | 636 | 1078 | 20
53QDMT42-718 | 42 | Low | 0.12 | 594 | 1007 | 30
53QDMT42-718 | 42 | Low | 0.16 | 548 | 929 | 40
53QDMT42-718 | 42 | Low | 0.2 | 491 | 832 | 50
53QDMT42-718 | 42 | Low | 0.24 | 434 | 736 | 60
53QDMT42-718 | 42 | Low | 0.28 | 377 | 639 | 70
53QDMT42-718 | 42 | Low | 0.32 | 320 | 542 | 80
53QDMT42-718 | 42 | Low | 0.36 | 263 | 446 | 90
53QDMT42-718 | 42 | Low | 0.4 | 206 | 349 | 100
53QDMT30-718 | 30 | High | 0 | 910 | 1542 | 0
53QDMT30-718 | 30 | High | 0.04 | 880 | 1492 | 10
53QDMT30-718 | 30 | High | 0.08 | 850 | 1441 | 20
53QDMT30-718 | 30 | High | 0.12 | 820 | 1390 | 30
53QDMT30-718 | 30 | High | 0.16 | 790 | 1339 | 40
53QDMT30-718 | 30 | High | 0.2 | 760 | 1288 | 50
53QDMT30-718 | 30 | High | 0.24 | 730 | 1237 | 60
53QDMT30-718 | 30 | High | 0.28 | 700 | 1186 | 70
53QDMT30-718 | 30 | High | 0.32 | 670 | 1136 | 80
53QDMT30-718 | 30 | Medium | 0 | 730 | 1237 | 0
53QDMT30-718 | 30 | Medium | 0.04 | 690 | 1169 | 10
53QDMT30-718 | 30 | Medium | 0.08 | 657 | 1114 | 20
53QDMT30-718 | 30 | Medium | 0.12 | 624 | 1058 | 30
53QDMT30-718 | 30 | Medium | 0.16 | 591 | 1002 | 40
53QDMT30-718 | 30 | Medium | 0.2 | 550 | 932 | 50
53QDMT30-718 | 30 | Medium | 0.24 | 509 | 863 | 60
53QDMT30-718 | 30 | Medium | 0.28 | 468 | 793 | 70
53QDMT30-718 | 30 | Medium | 0.32 | 427 | 724 | 80
53QDMT30-718 | 30 | Low | 0 | 645 | 1093 | 0
53QDMT30-718 | 30 | Low | 0.04 | 596 | 1010 | 10
53QDMT30-718 | 30 | Low | 0.08 | 562 | 952 | 20
53QDMT30-718 | 30 | Low | 0.12 | 525 | 890 | 30
53QDMT30-718 | 30 | Low | 0.16 | 495 | 839 | 40
53QDMT30-718 | 30 | Low | 0.2 | 453 | 768 | 50
53QDMT30-718 | 30 | Low | 0.24 | 411 | 697 | 60
53QDMT30-718 | 30 | Low | 0.28 | 369 | 625 | 70
53QDMT30-718 | 30 | Low | 0.32 | 327 | 554 | 80
53QDMT48-518 | 48 | High | 0 | 1370 | 2322 | 0
53QDMT48-518 | 48 | High | 0.04 | 1333 | 2259 | 10
53QDMT48-518 | 48 | High | 0.08 | 1300 | 2203 | 20
53QDMT48-518 | 48 | High | 0.12 | 1255 | 2127 | 30
53QDMT48-518 | 48 | High | 0.16 | 1223 | 2073 | 40
53QDMT48-518 | 48 | High | 0.2 | 1187 | 2012 | 50
53QDMT48-518 | 48 | High | 0.24 | 1151 | 1951 | 60
53QDMT48-518 | 48 | High | 0.28 | 1115 | 1890 | 70
53QDMT48-518 | 48 | High | 0.32 | 1079 | 1829 | 80
53QDMT48-518 | 48 | High | 0.36 | 1043 | 1768 | 90
53QDMT48-518 | 48 | High | 0.4 | 1007 | 1707 | 100
53QDMT48-518 | 48 | Medium | 0 | 880 | 1492 | 0
53QDMT48-518 | 48 | Medium | 0.04 | 835 | 1415 | 10
53QDMT48-518 | 48 | Medium | 0.08 | 803 | 1361 | 20
53QDMT48-518 | 48 | Medium | 0.12 | 770 | 1305 | 30
53QDMT48-518 | 48 | Medium | 0.16 | 733 | 1242 | 40
53QDMT48-518 | 48 | Medium | 0.2 | 693 | 1175 | 50
53QDMT48-518 | 48 | Medium | 0.24 | 653 | 1107 | 60
53QDMT48-518 | 48 | Medium | 0.28 | 613 | 1039 | 70
53QDMT48-518 | 48 | Medium | 0.32 | 573 | 971 | 80
53QDMT48-518 | 48 | Medium | 0.36 | 533 | 903 | 90
53QDMT48-518 | 48 | Medium | 0.4 | 493 | 836 | 100
53QDMT48-518 | 48 | Low | 0 | 715 | 1212 | 0
53QDMT48-518 | 48 | Low | 0.04 | 668 | 1132 | 10
53QDMT48-518 | 48 | Low | 0.08 | 636 | 1078 | 20
53QDMT48-518 | 48 | Low | 0.12 | 594 | 1007 | 30
53QDMT48-518 | 48 | Low | 0.16 | 548 | 929 | 40
53QDMT48-518 | 48 | Low | 0.2 | 491 | 832 | 50
53QDMT48-518 | 48 | Low | 0.24 | 434 | 736 | 60
53QDMT48-518 | 48 | Low | 0.28 | 377 | 639 | 70
53QDMT48-518 | 48 | Low | 0.32 | 320 | 542 | 80
53QDMT48-518 | 48 | Low | 0.36 | 263 | 446 | 90
53QDMT48-518 | 48 | Low | 0.4 | 206 | 349 | 100
53QDMT60-518 | 60 | High | 0 | 1470 | 2492 | 0
53QDMT60-518 | 60 | High | 0.04 | 1441 | 2442 | 10
53QDMT60-518 | 60 | High | 0.08 | 1405 | 2381 | 20
53QDMT60-518 | 60 | High | 0.12 | 1380 | 2339 | 30
53QDMT60-518 | 60 | High | 0.16 | 1345 | 2280 | 40
53QDMT60-518 | 60 | High | 0.2 | 1314 | 2227 | 50
53QDMT60-518 | 60 | High | 0.24 | 1283 | 2175 | 60
53QDMT60-518 | 60 | High | 0.28 | 1252 | 2122 | 70
53QDMT60-518 | 60 | High | 0.32 | 1221 | 2070 | 80
53QDMT60-518 | 60 | High | 0.36 | 1190 | 2017 | 90
53QDMT60-518 | 60 | High | 0.4 | 1159 | 1964 | 100
53QDMT60-518 | 60 | Medium | 0 | 1020 | 1729 | 0
53QDMT60-518 | 60 | Medium | 0.04 | 992 | 1681 | 10
53QDMT60-518 | 60 | Medium | 0.08 | 968 | 1641 | 20
53QDMT60-518 | 60 | Medium | 0.12 | 948 | 1607 | 30
53QDMT60-518 | 60 | Medium | 0.16 | 914 | 1549 | 40
53QDMT60-518 | 60 | Medium | 0.2 | 880 | 1492 | 50
53QDMT60-518 | 60 | Medium | 0.24 | 846 | 1434 | 60
53QDMT60-518 | 60 | Medium | 0.28 | 812 | 1376 | 70
53QDMT60-518 | 60 | Medium | 0.32 | 778 | 1319 | 80
53QDMT60-518 | 60 | Medium | 0.36 | 744 | 1361 | 90
53QDMT60-518 | 60 | Medium | 0.4 | 710 | 1203 | 100
53QDMT60-518 | 60 | Low | 0 | 860 | 1458 | 0
53QDMT60-518 | 60 | Low | 0.04 | 828 | 1403 | 10
53QDMT60-518 | 60 | Low | 0.08 | 800 | 1356 | 20
53QDMT60-518 | 60 | Low | 0.12 | 762 | 1292 | 30
53QDMT60-518 | 60 | Low | 0.16 | 728 | 1234 | 40
53QDMT60-518 | 60 | Low | 0.2 | 703 | 1192 | 50
53QDMT60-518 | 60 | Low | 0.24 | 678 | 1149 | 60
53QDMT60-518 | 60 | Low | 0.28 | 653 | 1107 | 70
53QDMT60-518 | 60 | Low | 0.32 | 628 | 1064 | 80
53QDMT60-518 | 60 | Low | 0.36 | 603 | 1022 | 90
53QDMT60-518 | 60 | Low | 0.4 | 578 | 980 | 100

## Sound_Level
system_model | fan_speed | esp_inwg | sound_dba | esp_pa
53QDMT12-718 | High | 0 | 39.6 | 0
53QDMT12-718 | High | 0.04 | 39.2 | 10
53QDMT12-718 | High | 0.08 | 38.8 | 20
53QDMT12-718 | High | 0.12 | 38.5 | 30
53QDMT12-718 | High | 0.16 | 38.1 | 40
53QDMT12-718 | Medium | 0 | 31 | 0
53QDMT12-718 | Medium | 0.04 | 30.6 | 10
53QDMT12-718 | Medium | 0.08 | 30.2 | 20
53QDMT12-718 | Medium | 0.12 | 29.8 | 30
53QDMT12-718 | Medium | 0.16 | 29.4 | 40
53QDMT12-718 | Low | 0 | 27.2 | 0
53QDMT12-718 | Low | 0.04 | 26.8 | 10
53QDMT12-718 | Low | 0.08 | 26.4 | 20
53QDMT12-718 | Low | 0.12 | 26 | 30
53QDMT12-718 | Low | 0.16 | 25.6 | 40
53QDMT18-718 | High | 0 | 44.7 | 0
53QDMT18-718 | High | 0.04 | 44.3 | 10
53QDMT18-718 | High | 0.08 | 43.9 | 20
53QDMT18-718 | High | 0.12 | 43.6 | 30
53QDMT18-718 | High | 0.16 | 43.2 | 40
53QDMT18-718 | High | 0.2 | 42.8 | 50
53QDMT18-718 | High | 0.24 | 42.4 | 60
53QDMT18-718 | Medium | 0 | 35.4 | 0
53QDMT18-718 | Medium | 0.04 | 35 | 10
53QDMT18-718 | Medium | 0.08 | 34.6 | 20
53QDMT18-718 | Medium | 0.12 | 34.2 | 30
53QDMT18-718 | Medium | 0.16 | 33.8 | 40
53QDMT18-718 | Medium | 0.2 | 33.4 | 50
53QDMT18-718 | Medium | 0.24 | 33 | 60
53QDMT18-718 | Low | 0 | 31.6 | 0
53QDMT18-718 | Low | 0.04 | 31.2 | 10
53QDMT18-718 | Low | 0.08 | 30.8 | 20
53QDMT18-718 | Low | 0.12 | 30.4 | 30
53QDMT18-718 | Low | 0.16 | 30 | 40
53QDMT18-718 | Low | 0.2 | 29.6 | 50
53QDMT18-718 | Low | 0.24 | 29.2 | 60
53QDMT24-718 | High | 0 | 47.2 | 0
53QDMT24-718 | High | 0.04 | 46.8 | 10
53QDMT24-718 | High | 0.08 | 46.4 | 20
53QDMT24-718 | High | 0.12 | 46.1 | 30
53QDMT24-718 | High | 0.16 | 45.7 | 40
53QDMT24-718 | High | 0.2 | 45.3 | 50
53QDMT24-718 | High | 0.24 | 44.9 | 60
53QDMT24-718 | Medium | 0 | 41.3 | 0
53QDMT24-718 | Medium | 0.04 | 40.9 | 10
53QDMT24-718 | Medium | 0.08 | 40.6 | 20
53QDMT24-718 | Medium | 0.12 | 40.2 | 30
53QDMT24-718 | Medium | 0.16 | 39.8 | 40
53QDMT24-718 | Medium | 0.2 | 39.4 | 50
53QDMT24-718 | Medium | 0.24 | 39 | 60
53QDMT24-718 | Low | 0 | 40.4 | 0
53QDMT24-718 | Low | 0.04 | 40 | 10
53QDMT24-718 | Low | 0.08 | 39.6 | 20
53QDMT24-718 | Low | 0.12 | 39.2 | 30
53QDMT24-718 | Low | 0.16 | 38.8 | 40
53QDMT24-718 | Low | 0.2 | 38.4 | 50
53QDMT24-718 | Low | 0.24 | 38 | 60
53QDMT30-718 | High | 0 | 49.7 | 0
53QDMT30-718 | High | 0.04 | 49.3 | 10
53QDMT30-718 | High | 0.08 | 48.9 | 20
53QDMT30-718 | High | 0.12 | 48.6 | 30
53QDMT30-718 | High | 0.16 | 48.2 | 40
53QDMT30-718 | High | 0.2 | 47.8 | 50
53QDMT30-718 | High | 0.24 | 47.4 | 60
53QDMT30-718 | High | 0.28 | 47.1 | 70
53QDMT30-718 | High | 0.32 | 46.8 | 80
53QDMT30-718 | Medium | 0 | 45.4 | 0
53QDMT30-718 | Medium | 0.04 | 45 | 10
53QDMT30-718 | Medium | 0.08 | 44.7 | 20
53QDMT30-718 | Medium | 0.12 | 44.3 | 30
53QDMT30-718 | Medium | 0.16 | 43.9 | 40
53QDMT30-718 | Medium | 0.2 | 43.5 | 50
53QDMT30-718 | Medium | 0.24 | 43.1 | 60
53QDMT30-718 | Medium | 0.28 | 42.8 | 70
53QDMT30-718 | Medium | 0.32 | 42.4 | 80
53QDMT30-718 | Low | 0 | 44 | 0
53QDMT30-718 | Low | 0.04 | 43.6 | 10
53QDMT30-718 | Low | 0.08 | 43.2 | 20
53QDMT30-718 | Low | 0.12 | 42.8 | 30
53QDMT30-718 | Low | 0.16 | 42.4 | 40
53QDMT30-718 | Low | 0.2 | 42 | 50
53QDMT30-718 | Low | 0.24 | 41.6 | 60
53QDMT30-718 | Low | 0.28 | 41.2 | 70
53QDMT30-718 | Low | 0.32 | 40.8 | 80
53QDMT36-718 | High | 0 | 51.5 | 0
53QDMT36-718 | High | 0.04 | 51.1 | 10
53QDMT36-718 | High | 0.08 | 50.7 | 20
53QDMT36-718 | High | 0.12 | 50.4 | 30
53QDMT36-718 | High | 0.16 | 50 | 40
53QDMT36-718 | High | 0.2 | 49.6 | 50
53QDMT36-718 | High | 0.24 | 49.2 | 60
53QDMT36-718 | High | 0.28 | 48.9 | 70
53QDMT36-718 | High | 0.32 | 48.6 | 80
53QDMT36-718 | Medium | 0 | 45.4 | 0
53QDMT36-718 | Medium | 0.04 | 45 | 10
53QDMT36-718 | Medium | 0.08 | 44.7 | 20
53QDMT36-718 | Medium | 0.12 | 44.3 | 30
53QDMT36-718 | Medium | 0.16 | 43.9 | 40
53QDMT36-718 | Medium | 0.2 | 43.5 | 50
53QDMT36-718 | Medium | 0.24 | 43.1 | 60
53QDMT36-718 | Medium | 0.28 | 42.8 | 70
53QDMT36-718 | Medium | 0.32 | 42.4 | 80
53QDMT36-718 | Low | 0 | 44 | 0
53QDMT36-718 | Low | 0.04 | 43.6 | 10
53QDMT36-718 | Low | 0.08 | 43.2 | 20
53QDMT36-718 | Low | 0.12 | 42.8 | 30
53QDMT36-718 | Low | 0.16 | 42.4 | 40
53QDMT36-718 | Low | 0.2 | 42 | 50
53QDMT36-718 | Low | 0.24 | 41.6 | 60
53QDMT36-718 | Low | 0.28 | 41.2 | 70
53QDMT36-718 | Low | 0.32 | 40.8 | 80
53QDMT42-718 | High | 0 | 52 | 0
53QDMT42-718 | High | 0.04 | 51.6 | 10
53QDMT42-718 | High | 0.08 | 51.2 | 20
53QDMT42-718 | High | 0.12 | 50.9 | 30
53QDMT42-718 | High | 0.16 | 50.5 | 40
53QDMT42-718 | High | 0.2 | 50.1 | 50
53QDMT42-718 | High | 0.24 | 49.7 | 60
53QDMT42-718 | High | 0.28 | 49.3 | 70
53QDMT42-718 | High | 0.32 | 49 | 80
53QDMT42-718 | High | 0.36 | 48.6 | 90
53QDMT42-718 | High | 0.4 | 48.2 | 100
53QDMT42-718 | Medium | 0 | 44.2 | 0
53QDMT42-718 | Medium | 0.04 | 43.8 | 10
53QDMT42-718 | Medium | 0.08 | 43.5 | 20
53QDMT42-718 | Medium | 0.12 | 43.1 | 30
53QDMT42-718 | Medium | 0.16 | 42.8 | 40
53QDMT42-718 | Medium | 0.2 | 42.4 | 50
53QDMT42-718 | Medium | 0.24 | 42 | 60
53QDMT42-718 | Medium | 0.28 | 41.7 | 70
53QDMT42-718 | Medium | 0.32 | 41.3 | 80
53QDMT42-718 | Medium | 0.36 | 41 | 90
53QDMT42-718 | Medium | 0.4 | 40.6 | 100
53QDMT42-718 | Low | 0 | 42.4 | 0
53QDMT42-718 | Low | 0.04 | 42 | 10
53QDMT42-718 | Low | 0.08 | 41.6 | 20
53QDMT42-718 | Low | 0.12 | 41.2 | 30
53QDMT42-718 | Low | 0.16 | 40.8 | 40
53QDMT42-718 | Low | 0.2 | 40.4 | 50
53QDMT42-718 | Low | 0.24 | 40 | 60
53QDMT42-718 | Low | 0.28 | 39.6 | 70
53QDMT42-718 | Low | 0.32 | 39.2 | 80
53QDMT42-718 | Low | 0.36 | 38.8 | 90
53QDMT42-718 | Low | 0.4 | 38.4 | 100
53QDMT48-518 | High | 0 | 52 | 0
53QDMT48-518 | High | 0.04 | 51.6 | 10
53QDMT48-518 | High | 0.08 | 51.2 | 20
53QDMT48-518 | High | 0.12 | 50.9 | 30
53QDMT48-518 | High | 0.16 | 50.5 | 40
53QDMT48-518 | High | 0.2 | 50.1 | 50
53QDMT48-518 | High | 0.24 | 49.7 | 60
53QDMT48-518 | High | 0.28 | 49.3 | 70
53QDMT48-518 | High | 0.32 | 49 | 80
53QDMT48-518 | High | 0.36 | 48.6 | 90
53QDMT48-518 | High | 0.4 | 48.2 | 100
53QDMT48-518 | Medium | 0 | 44.2 | 0
53QDMT48-518 | Medium | 0.04 | 43.8 | 10
53QDMT48-518 | Medium | 0.08 | 43.5 | 20
53QDMT48-518 | Medium | 0.12 | 43.1 | 30
53QDMT48-518 | Medium | 0.16 | 42.8 | 40
53QDMT48-518 | Medium | 0.2 | 42.4 | 50
53QDMT48-518 | Medium | 0.24 | 42 | 60
53QDMT48-518 | Medium | 0.28 | 41.7 | 70
53QDMT48-518 | Medium | 0.32 | 41.3 | 80
53QDMT48-518 | Medium | 0.36 | 41 | 90
53QDMT48-518 | Medium | 0.4 | 40.6 | 100
53QDMT48-518 | Low | 0 | 42.4 | 0
53QDMT48-518 | Low | 0.04 | 42 | 10
53QDMT48-518 | Low | 0.08 | 41.6 | 20
53QDMT48-518 | Low | 0.12 | 41.2 | 30
53QDMT48-518 | Low | 0.16 | 40.8 | 40
53QDMT48-518 | Low | 0.2 | 40.4 | 50
53QDMT48-518 | Low | 0.24 | 40 | 60
53QDMT48-518 | Low | 0.28 | 39.6 | 70
53QDMT48-518 | Low | 0.32 | 39.2 | 80
53QDMT48-518 | Low | 0.36 | 38.8 | 90
53QDMT48-518 | Low | 0.4 | 38.4 | 100
53QDMT60-518 | High | 0 | 54.2 | 0
53QDMT60-518 | High | 0.04 | 53.8 | 10
53QDMT60-518 | High | 0.08 | 53.4 | 20
53QDMT60-518 | High | 0.12 | 53.1 | 30
53QDMT60-518 | High | 0.16 | 52.7 | 40
53QDMT60-518 | High | 0.2 | 52.3 | 50
53QDMT60-518 | High | 0.24 | 51.9 | 60
53QDMT60-518 | High | 0.28 | 51.5 | 70
53QDMT60-518 | High | 0.32 | 51.1 | 80
53QDMT60-518 | High | 0.36 | 50.8 | 90
53QDMT60-518 | High | 0.4 | 50.4 | 100
53QDMT60-518 | Medium | 0 | 47.9 | 0
53QDMT60-518 | Medium | 0.04 | 47.5 | 10
53QDMT60-518 | Medium | 0.08 | 47.2 | 20
53QDMT60-518 | Medium | 0.12 | 46.8 | 30
53QDMT60-518 | Medium | 0.16 | 46.5 | 40
53QDMT60-518 | Medium | 0.2 | 46.1 | 50
53QDMT60-518 | Medium | 0.24 | 45.7 | 60
53QDMT60-518 | Medium | 0.28 | 45.4 | 70
53QDMT60-518 | Medium | 0.32 | 45 | 80
53QDMT60-518 | Medium | 0.36 | 44.7 | 90
53QDMT60-518 | Medium | 0.4 | 44.3 | 100
53QDMT60-518 | Low | 0 | 44.9 | 0
53QDMT60-518 | Low | 0.04 | 44.6 | 10
53QDMT60-518 | Low | 0.08 | 44.2 | 20
53QDMT60-518 | Low | 0.12 | 43.9 | 30
53QDMT60-518 | Low | 0.16 | 43.5 | 40
53QDMT60-518 | Low | 0.2 | 43.2 | 50
53QDMT60-518 | Low | 0.24 | 42.9 | 60
53QDMT60-518 | Low | 0.28 | 42.5 | 70
53QDMT60-518 | Low | 0.32 | 42.2 | 80
53QDMT60-518 | Low | 0.36 | 41.8 | 90
53QDMT60-518 | Low | 0.4 | 41.5 | 100

## Cooling_Performance
system_model | esp_inwg | fan_speed | airflow_cfm | indoor_db_c | indoor_wb_c | outdoor_db_c | total_capacity_btuh | sensible_capacity_btuh | input_w | source_page
53QDMT12-718 | 0 | High | 400 | 21 | 15 | 35 | 12105 | 9670 | 1195 | 15
53QDMT12-718 | 0 | High | 400 | 21 | 15 | 43 | 11580 | 9710 | 1230 | 15
53QDMT12-718 | 0 | High | 400 | 21 | 15 | 46 | 11300 | 9610 | 1245 | 15
53QDMT12-718 | 0 | High | 400 | 21 | 15 | 52 | 10735 | 9405 | 1275 | 15
53QDMT12-718 | 0 | High | 400 | 24 | 17 | 35 | 12475 | 10120 | 1240 | 15
53QDMT12-718 | 0 | High | 400 | 24 | 17 | 43 | 11705 | 9835 | 1305 | 15
53QDMT12-718 | 0 | High | 400 | 24 | 17 | 46 | 11460 | 9745 | 1330 | 15
53QDMT12-718 | 0 | High | 400 | 24 | 17 | 52 | 10975 | 9560 | 1380 | 15
53QDMT12-718 | 0 | High | 400 | 27 | 19 | 35 | 13000 | 10155 | 1265 | 15
53QDMT12-718 | 0 | High | 400 | 27 | 19 | 43 | 12105 | 9910 | 1330 | 15
53QDMT12-718 | 0 | High | 400 | 27 | 19 | 46 | 11700 | 9710 | 1355 | 15
53QDMT12-718 | 0 | High | 400 | 27 | 19 | 52 | 10885 | 9310 | 1400 | 15
53QDMT12-718 | 0 | High | 400 | 32 | 23 | 35 | 13530 | 11905 | 1325 | 15
53QDMT12-718 | 0 | High | 400 | 32 | 23 | 43 | 12475 | 11625 | 1380 | 15
53QDMT12-718 | 0 | High | 400 | 32 | 23 | 46 | 12110 | 11505 | 1395 | 15
53QDMT12-718 | 0 | High | 400 | 32 | 23 | 52 | 11385 | 11265 | 1420 | 15
53QDMT12-718 | 0 | Medium | 290 | 21 | 15 | 35 | 11625 | 8900 | 1160 | 15
53QDMT12-718 | 0 | Medium | 290 | 21 | 15 | 43 | 11120 | 8935 | 1200 | 15
53QDMT12-718 | 0 | Medium | 290 | 21 | 15 | 46 | 10850 | 8840 | 1215 | 15
53QDMT12-718 | 0 | Medium | 290 | 21 | 15 | 52 | 10305 | 8655 | 1245 | 15
53QDMT12-718 | 0 | Medium | 290 | 24 | 17 | 35 | 11975 | 9310 | 1205 | 15
53QDMT12-718 | 0 | Medium | 290 | 24 | 17 | 43 | 11240 | 9050 | 1260 | 15
53QDMT12-718 | 0 | Medium | 290 | 24 | 17 | 46 | 11005 | 8965 | 1285 | 15
53QDMT12-718 | 0 | Medium | 290 | 24 | 17 | 52 | 10535 | 8795 | 1335 | 15
53QDMT12-718 | 0 | Medium | 290 | 27 | 19 | 35 | 12480 | 9345 | 1225 | 15
53QDMT12-718 | 0 | Medium | 290 | 27 | 19 | 43 | 11625 | 9120 | 1285 | 15
53QDMT12-718 | 0 | Medium | 290 | 27 | 19 | 46 | 11235 | 8935 | 1310 | 15
53QDMT12-718 | 0 | Medium | 290 | 27 | 19 | 52 | 10455 | 8570 | 1360 | 15
53QDMT12-718 | 0 | Medium | 290 | 32 | 23 | 35 | 12990 | 10955 | 1285 | 15
53QDMT12-718 | 0 | Medium | 290 | 32 | 23 | 43 | 11975 | 10695 | 1335 | 15
53QDMT12-718 | 0 | Medium | 290 | 32 | 23 | 46 | 11630 | 10585 | 1350 | 15
53QDMT12-718 | 0 | Medium | 290 | 32 | 23 | 52 | 10930 | 10365 | 1380 | 15
53QDMT12-718 | 0 | Low | 250 | 21 | 15 | 35 | 11140 | 8220 | 1115 | 15
53QDMT12-718 | 0 | Low | 250 | 21 | 15 | 43 | 10655 | 8255 | 1150 | 15
53QDMT12-718 | 0 | Low | 250 | 21 | 15 | 46 | 10400 | 8170 | 1160 | 15
53QDMT12-718 | 0 | Low | 250 | 21 | 15 | 52 | 9880 | 7995 | 1190 | 15
53QDMT12-718 | 0 | Low | 250 | 24 | 17 | 35 | 11475 | 8600 | 1155 | 15
53QDMT12-718 | 0 | Low | 250 | 24 | 17 | 43 | 10775 | 8365 | 1215 | 15
53QDMT12-718 | 0 | Low | 250 | 24 | 17 | 46 | 10545 | 8285 | 1240 | 15
53QDMT12-718 | 0 | Low | 250 | 24 | 17 | 52 | 10095 | 8130 | 1290 | 15
53QDMT12-718 | 0 | Low | 250 | 27 | 19 | 35 | 11960 | 8635 | 1175 | 15
53QDMT12-718 | 0 | Low | 250 | 27 | 19 | 43 | 11140 | 8430 | 1235 | 15
53QDMT12-718 | 0 | Low | 250 | 27 | 19 | 46 | 10770 | 8255 | 1260 | 15
53QDMT12-718 | 0 | Low | 250 | 27 | 19 | 52 | 10020 | 7920 | 1310 | 15
53QDMT12-718 | 0 | Low | 250 | 21 | 23 | 35 | 12450 | 10125 | 1230 | 15
53QDMT12-718 | 0 | Low | 250 | 21 | 23 | 43 | 11475 | 9885 | 1285 | 15
53QDMT12-718 | 0 | Low | 250 | 21 | 23 | 46 | 11145 | 9780 | 1300 | 15
53QDMT12-718 | 0 | Low | 250 | 21 | 23 | 52 | 10475 | 9575 | 1330 | 15
53QDMT12-718 | 0.08 | High | 344 | 21 | 15 | 35 | 11860 | 9305 | 1180 | 15
53QDMT12-718 | 0.08 | High | 344 | 21 | 15 | 43 | 11345 | 9515 | 1215 | 15
53QDMT12-718 | 0.08 | High | 344 | 21 | 15 | 46 | 11070 | 9420 | 1230 | 15
53QDMT12-718 | 0.08 | High | 344 | 21 | 15 | 52 | 10520 | 9220 | 1260 | 15
53QDMT12-718 | 0.08 | High | 344 | 24 | 17 | 35 | 12225 | 9730 | 1225 | 15
53QDMT12-718 | 0.08 | High | 344 | 24 | 17 | 43 | 11470 | 9640 | 1290 | 15
53QDMT12-718 | 0.08 | High | 344 | 24 | 17 | 46 | 11235 | 9550 | 1315 | 15
53QDMT12-718 | 0.08 | High | 344 | 24 | 17 | 52 | 10755 | 9370 | 1365 | 15
53QDMT12-718 | 0.08 | High | 344 | 27 | 19 | 35 | 12740 | 9755 | 1250 | 15
53QDMT12-718 | 0.08 | High | 344 | 27 | 19 | 43 | 11860 | 9715 | 1315 | 15
53QDMT12-718 | 0.08 | High | 344 | 27 | 19 | 46 | 11465 | 9515 | 1340 | 15
53QDMT12-718 | 0.08 | High | 344 | 27 | 19 | 52 | 10670 | 9120 | 1390 | 15
53QDMT12-718 | 0.08 | High | 344 | 32 | 23 | 35 | 13250 | 11480 | 1310 | 15
53QDMT12-718 | 0.08 | High | 344 | 32 | 23 | 43 | 12220 | 11385 | 1365 | 15
53QDMT12-718 | 0.08 | High | 344 | 32 | 23 | 46 | 11860 | 11270 | 1380 | 15
53QDMT12-718 | 0.08 | High | 344 | 32 | 23 | 52 | 11150 | 11040 | 1405 | 15
53QDMT12-718 | 0.08 | Medium | 242 | 21 | 15 | 35 | 11390 | 8565 | 1150 | 15
53QDMT12-718 | 0.08 | Medium | 242 | 21 | 15 | 43 | 10895 | 8760 | 1185 | 15
53QDMT12-718 | 0.08 | Medium | 242 | 21 | 15 | 46 | 10630 | 8665 | 1200 | 15
53QDMT12-718 | 0.08 | Medium | 242 | 21 | 15 | 52 | 10100 | 8480 | 1230 | 15
53QDMT12-718 | 0.08 | Medium | 242 | 24 | 17 | 35 | 11735 | 8955 | 1190 | 15
53QDMT12-718 | 0.08 | Medium | 242 | 24 | 17 | 43 | 11010 | 8870 | 1245 | 15
53QDMT12-718 | 0.08 | Medium | 242 | 24 | 17 | 46 | 10785 | 8785 | 1270 | 15
53QDMT12-718 | 0.08 | Medium | 242 | 24 | 17 | 52 | 10330 | 8625 | 1320 | 15
53QDMT12-718 | 0.08 | Medium | 242 | 27 | 19 | 35 | 12230 | 8975 | 1210 | 15
53QDMT12-718 | 0.08 | Medium | 242 | 27 | 19 | 43 | 11390 | 8945 | 1270 | 15
53QDMT12-718 | 0.08 | Medium | 242 | 27 | 19 | 46 | 11005 | 8760 | 1295 | 15
53QDMT12-718 | 0.08 | Medium | 242 | 27 | 19 | 52 | 10240 | 8395 | 1345 | 15
53QDMT12-718 | 0.08 | Medium | 242 | 32 | 23 | 35 | 12720 | 10565 | 1270 | 15
53QDMT12-718 | 0.08 | Medium | 242 | 32 | 23 | 43 | 11730 | 10480 | 1315 | 15
53QDMT12-718 | 0.08 | Medium | 242 | 32 | 23 | 46 | 11390 | 10365 | 1330 | 15
53QDMT12-718 | 0.08 | Medium | 242 | 32 | 23 | 52 | 10710 | 10155 | 1360 | 15
53QDMT12-718 | 0.08 | Low | 203 | 21 | 15 | 35 | 10920 | 7915 | 1100 | 15
53QDMT12-718 | 0.08 | Low | 203 | 21 | 15 | 43 | 10445 | 8095 | 1135 | 15
53QDMT12-718 | 0.08 | Low | 203 | 21 | 15 | 46 | 10190 | 8005 | 1150 | 15
53QDMT12-718 | 0.08 | Low | 203 | 21 | 15 | 52 | 9680 | 7840 | 1170 | 15
53QDMT12-718 | 0.08 | Low | 203 | 24 | 17 | 35 | 11250 | 8270 | 1140 | 15
53QDMT12-718 | 0.08 | Low | 203 | 24 | 17 | 43 | 8930 | 8195 | 1200 | 15
53QDMT12-718 | 0.08 | Low | 203 | 24 | 17 | 46 | 10335 | 8120 | 1225 | 15
53QDMT12-718 | 0.08 | Low | 203 | 24 | 17 | 52 | 9895 | 7970 | 1275 | 15
53QDMT12-718 | 0.08 | Low | 203 | 27 | 19 | 35 | 11720 | 8295 | 1175 | 15
53QDMT12-718 | 0.08 | Low | 203 | 27 | 19 | 43 | 10920 | 8260 | 1235 | 15
53QDMT12-718 | 0.08 | Low | 203 | 27 | 19 | 46 | 10550 | 8095 | 1260 | 15
53QDMT12-718 | 0.08 | Low | 203 | 27 | 19 | 52 | 9820 | 7755 | 1310 | 15
53QDMT12-718 | 0.08 | Low | 203 | 21 | 23 | 35 | 12190 | 9765 | 1230 | 15
53QDMT12-718 | 0.08 | Low | 203 | 21 | 23 | 43 | 11245 | 9685 | 1280 | 15
53QDMT12-718 | 0.08 | Low | 203 | 21 | 23 | 46 | 10920 | 9580 | 1295 | 15
53QDMT12-718 | 0.08 | Low | 203 | 21 | 23 | 52 | 10265 | 9380 | 1325 | 15
53QDMT12-718 | 0.12 | High | 312 | 21 | 15 | 35 | 11740 | 9120 | 1170 | 15
53QDMT12-718 | 0.12 | High | 312 | 21 | 15 | 43 | 11235 | 9425 | 1205 | 15
53QDMT12-718 | 0.12 | High | 312 | 21 | 15 | 46 | 10960 | 9325 | 1220 | 15
53QDMT12-718 | 0.12 | High | 312 | 21 | 15 | 52 | 10420 | 9130 | 1250 | 15
53QDMT12-718 | 0.12 | High | 312 | 24 | 17 | 35 | 12100 | 9535 | 1215 | 15
53QDMT12-718 | 0.12 | High | 312 | 24 | 17 | 43 | 11360 | 9550 | 1280 | 15
53QDMT12-718 | 0.12 | High | 312 | 24 | 17 | 46 | 11125 | 9465 | 1305 | 15
53QDMT12-718 | 0.12 | High | 312 | 24 | 17 | 52 | 10660 | 9290 | 1355 | 15
53QDMT12-718 | 0.12 | High | 312 | 27 | 19 | 35 | 12610 | 9555 | 1240 | 15
53QDMT12-718 | 0.12 | High | 312 | 27 | 19 | 43 | 11740 | 9620 | 1305 | 15
53QDMT12-718 | 0.12 | High | 312 | 27 | 19 | 46 | 11350 | 9425 | 1330 | 15
53QDMT12-718 | 0.12 | High | 312 | 27 | 19 | 52 | 10575 | 9035 | 1380 | 15
53QDMT12-718 | 0.12 | High | 312 | 32 | 23 | 35 | 13105 | 11270 | 1300 | 15
53QDMT12-718 | 0.12 | High | 312 | 32 | 23 | 43 | 12085 | 11260 | 1355 | 15
53QDMT12-718 | 0.12 | High | 312 | 32 | 23 | 46 | 11730 | 11145 | 1370 | 15
53QDMT12-718 | 0.12 | High | 312 | 32 | 23 | 52 | 11025 | 10920 | 1400 | 15
53QDMT12-718 | 0.12 | Medium | 220 | 21 | 15 | 35 | 11275 | 8395 | 1140 | 15
53QDMT12-718 | 0.12 | Medium | 220 | 21 | 15 | 43 | 10785 | 8670 | 1175 | 15
53QDMT12-718 | 0.12 | Medium | 220 | 21 | 15 | 46 | 10525 | 8585 | 1190 | 15
53QDMT12-718 | 0.12 | Medium | 220 | 21 | 15 | 52 | 10005 | 8405 | 1220 | 15
53QDMT12-718 | 0.12 | Medium | 220 | 24 | 17 | 35 | 11620 | 8775 | 1180 | 15
53QDMT12-718 | 0.12 | Medium | 220 | 24 | 17 | 43 | 10910 | 8785 | 1235 | 15
53QDMT12-718 | 0.12 | Medium | 220 | 24 | 17 | 46 | 10680 | 8710 | 1260 | 15
53QDMT12-718 | 0.12 | Medium | 220 | 24 | 17 | 52 | 10235 | 8545 | 1310 | 15
53QDMT12-718 | 0.12 | Medium | 220 | 27 | 19 | 35 | 12105 | 8790 | 1205 | 15
53QDMT12-718 | 0.12 | Medium | 220 | 27 | 19 | 43 | 11275 | 8850 | 1260 | 15
53QDMT12-718 | 0.12 | Medium | 220 | 27 | 19 | 46 | 10905 | 8670 | 1285 | 15
53QDMT12-718 | 0.12 | Medium | 220 | 27 | 19 | 52 | 10150 | 8315 | 1335 | 15
53QDMT12-718 | 0.12 | Medium | 220 | 32 | 23 | 35 | 12585 | 10370 | 1260 | 15
53QDMT12-718 | 0.12 | Medium | 220 | 32 | 23 | 43 | 11600 | 10360 | 1305 | 15
53QDMT12-718 | 0.12 | Medium | 220 | 32 | 23 | 46 | 11265 | 10260 | 1320 | 15
53QDMT12-718 | 0.12 | Medium | 220 | 32 | 23 | 52 | 10590 | 10045 | 1350 | 15
53QDMT12-718 | 0.12 | Low | 180 | 21 | 15 | 35 | 10805 | 7755 | 1095 | 15
53QDMT12-718 | 0.12 | Low | 180 | 21 | 15 | 43 | 10335 | 8010 | 1130 | 15
53QDMT12-718 | 0.12 | Low | 180 | 21 | 15 | 46 | 10085 | 7930 | 1140 | 15
53QDMT12-718 | 0.12 | Low | 180 | 21 | 15 | 52 | 9585 | 7770 | 1155 | 15
53QDMT12-718 | 0.12 | Low | 180 | 24 | 17 | 35 | 11135 | 8105 | 1135 | 15
53QDMT12-718 | 0.12 | Low | 180 | 24 | 17 | 43 | 10455 | 8120 | 1190 | 15
53QDMT12-718 | 0.12 | Low | 180 | 24 | 17 | 46 | 10235 | 8045 | 1215 | 15
53QDMT12-718 | 0.12 | Low | 180 | 24 | 17 | 52 | 9810 | 7900 | 1265 | 15
53QDMT12-718 | 0.12 | Low | 180 | 27 | 19 | 35 | 11600 | 8125 | 1175 | 15
53QDMT12-718 | 0.12 | Low | 180 | 27 | 19 | 43 | 10805 | 8180 | 1230 | 15
53QDMT12-718 | 0.12 | Low | 180 | 27 | 19 | 46 | 10450 | 8010 | 1255 | 15
53QDMT12-718 | 0.12 | Low | 180 | 27 | 19 | 52 | 9730 | 7680 | 1305 | 15
53QDMT12-718 | 0.12 | Low | 180 | 21 | 23 | 35 | 12060 | 9580 | 1235 | 15
53QDMT12-718 | 0.12 | Low | 180 | 21 | 23 | 43 | 11120 | 9575 | 1280 | 15
53QDMT12-718 | 0.12 | Low | 180 | 21 | 23 | 46 | 10795 | 9480 | 1295 | 15
53QDMT12-718 | 0.12 | Low | 180 | 21 | 23 | 52 | 10165 | 9285 | 1325 | 15
53QDMT12-718 | 0.16 | High | 275 | 21 | 15 | 35 | 11620 | 8935 | 1160 | 15
53QDMT12-718 | 0.16 | High | 275 | 21 | 15 | 43 | 11115 | 9320 | 1195 | 15
53QDMT12-718 | 0.16 | High | 275 | 21 | 15 | 46 | 10845 | 9225 | 1210 | 15
53QDMT12-718 | 0.16 | High | 275 | 21 | 15 | 52 | 10300 | 9030 | 1240 | 15
53QDMT12-718 | 0.16 | High | 275 | 24 | 17 | 35 | 11970 | 9335 | 1205 | 15
53QDMT12-718 | 0.16 | High | 275 | 24 | 17 | 43 | 11235 | 9440 | 1270 | 15
53QDMT12-718 | 0.16 | High | 275 | 24 | 17 | 46 | 11000 | 9355 | 1295 | 15
53QDMT12-718 | 0.16 | High | 275 | 24 | 17 | 52 | 10535 | 9180 | 1345 | 15
53QDMT12-718 | 0.16 | High | 275 | 27 | 19 | 35 | 12475 | 9350 | 1230 | 15
53QDMT12-718 | 0.16 | High | 275 | 27 | 19 | 43 | 11620 | 9515 | 1295 | 15
53QDMT12-718 | 0.16 | High | 275 | 27 | 19 | 46 | 11230 | 9320 | 1320 | 15
53QDMT12-718 | 0.16 | High | 275 | 27 | 19 | 52 | 10450 | 8930 | 1370 | 15
53QDMT12-718 | 0.16 | High | 275 | 32 | 23 | 35 | 12965 | 11060 | 1290 | 15
53QDMT12-718 | 0.16 | High | 275 | 32 | 23 | 43 | 11960 | 11145 | 1345 | 15
53QDMT12-718 | 0.16 | High | 275 | 32 | 23 | 46 | 11610 | 11035 | 1360 | 15
53QDMT12-718 | 0.16 | High | 275 | 32 | 23 | 52 | 10920 | 10805 | 1390 | 15
53QDMT12-718 | 0.16 | Medium | 193 | 21 | 15 | 35 | 11155 | 8220 | 1130 | 15
53QDMT12-718 | 0.16 | Medium | 193 | 21 | 15 | 43 | 10670 | 8580 | 1165 | 15
53QDMT12-718 | 0.16 | Medium | 193 | 21 | 15 | 46 | 10410 | 8490 | 1180 | 15
53QDMT12-718 | 0.16 | Medium | 193 | 21 | 15 | 52 | 9890 | 8310 | 1210 | 15
53QDMT12-718 | 0.16 | Medium | 193 | 24 | 17 | 35 | 11495 | 8590 | 1170 | 15
53QDMT12-718 | 0.16 | Medium | 193 | 24 | 17 | 43 | 10785 | 8690 | 1225 | 15
53QDMT12-718 | 0.16 | Medium | 193 | 24 | 17 | 46 | 10560 | 8605 | 1250 | 15
53QDMT12-718 | 0.16 | Medium | 193 | 24 | 17 | 52 | 10120 | 8450 | 1300 | 15
53QDMT12-718 | 0.16 | Medium | 193 | 27 | 19 | 35 | 11975 | 8600 | 1195 | 15
53QDMT12-718 | 0.16 | Medium | 193 | 27 | 19 | 43 | 11155 | 8760 | 1250 | 15
53QDMT12-718 | 0.16 | Medium | 193 | 27 | 19 | 46 | 10780 | 8580 | 1275 | 15
53QDMT12-718 | 0.16 | Medium | 193 | 27 | 19 | 52 | 10030 | 8215 | 1325 | 15
53QDMT12-718 | 0.16 | Medium | 193 | 32 | 23 | 35 | 12450 | 10175 | 1250 | 15
53QDMT12-718 | 0.16 | Medium | 193 | 32 | 23 | 43 | 11480 | 10260 | 1295 | 15
53QDMT12-718 | 0.16 | Medium | 193 | 32 | 23 | 46 | 11150 | 10150 | 1310 | 15
53QDMT12-718 | 0.16 | Medium | 193 | 32 | 23 | 52 | 10485 | 9945 | 1340 | 15
53QDMT12-718 | 0.16 | Low | 156 | 21 | 15 | 35 | 10690 | 7600 | 1085 | 15
53QDMT12-718 | 0.16 | Low | 156 | 21 | 15 | 43 | 10225 | 7925 | 1120 | 15
53QDMT12-718 | 0.16 | Low | 156 | 21 | 15 | 46 | 9975 | 7845 | 1130 | 15
53QDMT12-718 | 0.16 | Low | 156 | 21 | 15 | 52 | 9480 | 7675 | 1150 | 15
53QDMT12-718 | 0.16 | Low | 156 | 24 | 17 | 35 | 11015 | 7935 | 1125 | 15
53QDMT12-718 | 0.16 | Low | 156 | 24 | 17 | 43 | 7085 | 8030 | 1180 | 15
53QDMT12-718 | 0.16 | Low | 156 | 24 | 17 | 46 | 10125 | 7950 | 1205 | 15
53QDMT12-718 | 0.16 | Low | 156 | 24 | 17 | 52 | 9695 | 7805 | 1255 | 15
53QDMT12-718 | 0.16 | Low | 156 | 27 | 19 | 35 | 11475 | 7945 | 1180 | 15
53QDMT12-718 | 0.16 | Low | 156 | 27 | 19 | 43 | 10690 | 8095 | 1230 | 15
53QDMT12-718 | 0.16 | Low | 156 | 27 | 19 | 46 | 10335 | 7925 | 1255 | 15
53QDMT12-718 | 0.16 | Low | 156 | 27 | 19 | 52 | 9615 | 7595 | 1305 | 15
53QDMT12-718 | 0.16 | Low | 156 | 21 | 23 | 35 | 11930 | 9405 | 1230 | 15
53QDMT12-718 | 0.16 | Low | 156 | 21 | 23 | 43 | 11005 | 9480 | 1275 | 15
53QDMT12-718 | 0.16 | Low | 156 | 21 | 23 | 46 | 10685 | 9380 | 1290 | 15
53QDMT12-718 | 0.16 | Low | 156 | 21 | 23 | 52 | 10045 | 9185 | 1320 | 15
53QDMT18-718 | 0 | High | 530 | 21 | 15 | 35 | 19070 | 15240 | 1865 | 16
53QDMT18-718 | 0 | High | 530 | 21 | 15 | 43 | 18260 | 15320 | 1915 | 16
53QDMT18-718 | 0 | High | 530 | 21 | 15 | 46 | 17835 | 15160 | 1935 | 16
53QDMT18-718 | 0 | High | 530 | 21 | 15 | 52 | 16985 | 14835 | 1975 | 16
53QDMT18-718 | 0 | High | 530 | 24 | 17 | 35 | 19690 | 15940 | 1940 | 16
53QDMT18-718 | 0 | High | 530 | 24 | 17 | 43 | 18455 | 15515 | 2050 | 16
53QDMT18-718 | 0 | High | 530 | 24 | 17 | 46 | 18030 | 15320 | 2085 | 16
53QDMT18-718 | 0 | High | 530 | 24 | 17 | 52 | 17180 | 14930 | 2155 | 16
53QDMT18-718 | 0 | High | 530 | 27 | 19 | 35 | 20500 | 15975 | 1985 | 16
53QDMT18-718 | 0 | High | 530 | 27 | 19 | 43 | 19070 | 15630 | 2095 | 16
53QDMT18-718 | 0 | High | 530 | 27 | 19 | 46 | 18455 | 15325 | 2135 | 16
53QDMT18-718 | 0 | High | 530 | 27 | 19 | 52 | 17225 | 14720 | 2210 | 16
53QDMT18-718 | 0 | High | 530 | 32 | 23 | 35 | 21315 | 18760 | 2080 | 16
53QDMT18-718 | 0 | High | 530 | 32 | 23 | 43 | 19695 | 18300 | 2155 | 16
53QDMT18-718 | 0 | High | 530 | 32 | 23 | 46 | 19080 | 18125 | 2175 | 16
53QDMT18-718 | 0 | High | 530 | 32 | 23 | 52 | 17850 | 17775 | 2215 | 16
53QDMT18-718 | 0 | Medium | 350 | 21 | 15 | 35 | 18305 | 14025 | 1810 | 16
53QDMT18-718 | 0 | Medium | 350 | 21 | 15 | 43 | 17530 | 14095 | 1855 | 16
53QDMT18-718 | 0 | Medium | 350 | 21 | 15 | 46 | 17120 | 13950 | 1875 | 16
53QDMT18-718 | 0 | Medium | 350 | 21 | 15 | 52 | 16305 | 13650 | 1915 | 16
53QDMT18-718 | 0 | Medium | 350 | 24 | 17 | 35 | 18900 | 14665 | 1885 | 16
53QDMT18-718 | 0 | Medium | 350 | 24 | 17 | 43 | 17715 | 14275 | 1985 | 16
53QDMT18-718 | 0 | Medium | 350 | 24 | 17 | 46 | 17310 | 14095 | 2020 | 16
53QDMT18-718 | 0 | Medium | 350 | 24 | 17 | 52 | 16495 | 13740 | 2095 | 16
53QDMT18-718 | 0 | Medium | 350 | 27 | 19 | 35 | 19680 | 14700 | 1925 | 16
53QDMT18-718 | 0 | Medium | 350 | 27 | 19 | 43 | 18305 | 14380 | 2020 | 16
53QDMT18-718 | 0 | Medium | 350 | 27 | 19 | 46 | 17715 | 14100 | 2060 | 16
53QDMT18-718 | 0 | Medium | 350 | 27 | 19 | 52 | 16535 | 13545 | 2130 | 16
53QDMT18-718 | 0 | Medium | 350 | 32 | 23 | 35 | 20465 | 17265 | 2020 | 16
53QDMT18-718 | 0 | Medium | 350 | 32 | 23 | 43 | 18905 | 16840 | 2095 | 16
53QDMT18-718 | 0 | Medium | 350 | 32 | 23 | 46 | 18315 | 16675 | 2115 | 16
53QDMT18-718 | 0 | Medium | 350 | 32 | 23 | 52 | 17135 | 16355 | 2155 | 16
53QDMT18-718 | 0 | Low | 295 | 21 | 15 | 35 | 17545 | 12960 | 1735 | 16
53QDMT18-718 | 0 | Low | 295 | 21 | 15 | 43 | 16800 | 13025 | 1785 | 16
53QDMT18-718 | 0 | Low | 295 | 21 | 15 | 46 | 16410 | 12885 | 1805 | 16
53QDMT18-718 | 0 | Low | 295 | 21 | 15 | 52 | 15630 | 12610 | 1845 | 16
53QDMT18-718 | 0 | Low | 295 | 24 | 17 | 35 | 18115 | 13555 | 1805 | 16
53QDMT18-718 | 0 | Low | 295 | 24 | 17 | 43 | 16980 | 13195 | 1905 | 16
53QDMT18-718 | 0 | Low | 295 | 24 | 17 | 46 | 16590 | 13025 | 1940 | 16
53QDMT18-718 | 0 | Low | 295 | 24 | 17 | 52 | 15810 | 12690 | 2010 | 16
53QDMT18-718 | 0 | Low | 295 | 27 | 19 | 35 | 18860 | 13580 | 1850 | 16
53QDMT18-718 | 0 | Low | 295 | 27 | 19 | 43 | 17545 | 13285 | 1945 | 16
53QDMT18-718 | 0 | Low | 295 | 27 | 19 | 46 | 16980 | 14370 | 1980 | 16
53QDMT18-718 | 0 | Low | 295 | 27 | 19 | 52 | 15845 | 12515 | 2050 | 16
53QDMT18-718 | 0 | Low | 295 | 21 | 23 | 35 | 19610 | 15950 | 1930 | 16
53QDMT18-718 | 0 | Low | 295 | 21 | 23 | 43 | 18120 | 15560 | 2000 | 16
53QDMT18-718 | 0 | Low | 295 | 21 | 23 | 46 | 17555 | 16680 | 2025 | 16
53QDMT18-718 | 0 | Low | 295 | 21 | 23 | 52 | 16420 | 15110 | 2060 | 16
53QDMT18-718 | 0.08 | High | 487 | 21 | 15 | 35 | 18275 | 14610 | 1850 | 16
53QDMT18-718 | 0.08 | High | 487 | 21 | 15 | 43 | 17495 | 14680 | 1900 | 16
53QDMT18-718 | 0.08 | High | 487 | 21 | 15 | 46 | 17090 | 14530 | 1920 | 16
53QDMT18-718 | 0.08 | High | 487 | 21 | 15 | 52 | 16280 | 14225 | 1960 | 16
53QDMT18-718 | 0.08 | High | 487 | 24 | 17 | 35 | 18865 | 15275 | 1925 | 16
53QDMT18-718 | 0.08 | High | 487 | 24 | 17 | 43 | 17680 | 14870 | 2030 | 16
53QDMT18-718 | 0.08 | High | 487 | 24 | 17 | 46 | 17275 | 14685 | 2070 | 16
53QDMT18-718 | 0.08 | High | 487 | 24 | 17 | 52 | 16465 | 14315 | 2140 | 16
53QDMT18-718 | 0.08 | High | 487 | 27 | 19 | 35 | 19640 | 15305 | 1965 | 16
53QDMT18-718 | 0.08 | High | 487 | 27 | 19 | 43 | 18275 | 14975 | 2075 | 16
53QDMT18-718 | 0.08 | High | 487 | 27 | 19 | 46 | 17680 | 14690 | 2115 | 16
53QDMT18-718 | 0.08 | High | 487 | 27 | 19 | 52 | 16505 | 14120 | 2190 | 16
53QDMT18-718 | 0.08 | High | 487 | 32 | 23 | 35 | 20420 | 17975 | 2060 | 16
53QDMT18-718 | 0.08 | High | 487 | 32 | 23 | 43 | 18870 | 17535 | 2135 | 16
53QDMT18-718 | 0.08 | High | 487 | 32 | 23 | 46 | 18280 | 17370 | 2155 | 16
53QDMT18-718 | 0.08 | High | 487 | 32 | 23 | 52 | 17100 | 17040 | 2195 | 16
53QDMT18-718 | 0.08 | Medium | 308 | 21 | 15 | 35 | 17540 | 13440 | 1795 | 16
53QDMT18-718 | 0.08 | Medium | 308 | 21 | 15 | 43 | 16800 | 13510 | 1840 | 16
53QDMT18-718 | 0.08 | Medium | 308 | 21 | 15 | 46 | 16410 | 13375 | 1860 | 16
53QDMT18-718 | 0.08 | Medium | 308 | 21 | 15 | 52 | 15635 | 13090 | 1900 | 16
53QDMT18-718 | 0.08 | Medium | 308 | 24 | 17 | 35 | 18110 | 14055 | 1870 | 16
53QDMT18-718 | 0.08 | Medium | 308 | 24 | 17 | 43 | 16985 | 13680 | 1970 | 16
53QDMT18-718 | 0.08 | Medium | 308 | 24 | 17 | 46 | 16590 | 13510 | 2010 | 16
53QDMT18-718 | 0.08 | Medium | 308 | 24 | 17 | 52 | 15815 | 13175 | 2080 | 16
53QDMT18-718 | 0.08 | Medium | 308 | 27 | 19 | 35 | 18855 | 14085 | 1910 | 16
53QDMT18-718 | 0.08 | Medium | 308 | 27 | 19 | 43 | 17540 | 13780 | 2010 | 16
53QDMT18-718 | 0.08 | Medium | 308 | 27 | 19 | 46 | 16980 | 13515 | 2040 | 16
53QDMT18-718 | 0.08 | Medium | 308 | 27 | 19 | 52 | 15845 | 12995 | 2115 | 16
53QDMT18-718 | 0.08 | Medium | 308 | 32 | 23 | 35 | 19605 | 16540 | 2000 | 16
53QDMT18-718 | 0.08 | Medium | 308 | 32 | 23 | 43 | 18115 | 16135 | 2075 | 16
53QDMT18-718 | 0.08 | Medium | 308 | 32 | 23 | 46 | 17550 | 15980 | 2095 | 16
53QDMT18-718 | 0.08 | Medium | 308 | 32 | 23 | 52 | 16420 | 15675 | 2135 | 16
53QDMT18-718 | 0.08 | Low | 256 | 21 | 15 | 35 | 16815 | 12415 | 1720 | 16
53QDMT18-718 | 0.08 | Low | 256 | 21 | 15 | 43 | 16095 | 12485 | 1770 | 16
53QDMT18-718 | 0.08 | Low | 256 | 21 | 15 | 46 | 15725 | 12355 | 1790 | 16
53QDMT18-718 | 0.08 | Low | 256 | 21 | 15 | 52 | 14980 | 12095 | 1830 | 16
53QDMT18-718 | 0.08 | Low | 256 | 24 | 17 | 35 | 17360 | 12990 | 1790 | 16
53QDMT18-718 | 0.08 | Low | 256 | 24 | 17 | 43 | 16270 | 12640 | 1890 | 16
53QDMT18-718 | 0.08 | Low | 256 | 24 | 17 | 46 | 15900 | 12485 | 1925 | 16
53QDMT18-718 | 0.08 | Low | 256 | 24 | 17 | 52 | 15155 | 12170 | 2000 | 16
53QDMT18-718 | 0.08 | Low | 256 | 27 | 19 | 35 | 18075 | 13010 | 1835 | 16
53QDMT18-718 | 0.08 | Low | 256 | 27 | 19 | 43 | 16815 | 12730 | 1935 | 16
53QDMT18-718 | 0.08 | Low | 256 | 27 | 19 | 46 | 16270 | 13160 | 1970 | 16
53QDMT18-718 | 0.08 | Low | 256 | 27 | 19 | 52 | 15190 | 12000 | 2040 | 16
53QDMT18-718 | 0.08 | Low | 256 | 21 | 23 | 35 | 18785 | 15280 | 1915 | 16
53QDMT18-718 | 0.08 | Low | 256 | 21 | 23 | 43 | 17360 | 14905 | 1985 | 16
53QDMT18-718 | 0.08 | Low | 256 | 21 | 23 | 46 | 16820 | 15405 | 2010 | 16
53QDMT18-718 | 0.08 | Low | 256 | 21 | 23 | 52 | 15735 | 14485 | 2050 | 16
53QDMT18-718 | 0.12 | High | 465 | 21 | 15 | 35 | 17875 | 14290 | 1840 | 16
53QDMT18-718 | 0.12 | High | 465 | 21 | 15 | 43 | 17115 | 14365 | 1890 | 16
53QDMT18-718 | 0.12 | High | 465 | 21 | 15 | 46 | 16720 | 14215 | 1910 | 16
53QDMT18-718 | 0.12 | High | 465 | 21 | 15 | 52 | 15930 | 13925 | 1950 | 16
53QDMT18-718 | 0.12 | High | 465 | 24 | 17 | 35 | 18455 | 14945 | 1915 | 16
53QDMT18-718 | 0.12 | High | 465 | 24 | 17 | 43 | 17295 | 14545 | 2020 | 16
53QDMT18-718 | 0.12 | High | 465 | 24 | 17 | 46 | 16900 | 14365 | 2060 | 16
53QDMT18-718 | 0.12 | High | 465 | 24 | 17 | 52 | 16110 | 14005 | 2130 | 16
53QDMT18-718 | 0.12 | High | 465 | 27 | 19 | 35 | 19210 | 14975 | 1955 | 16
53QDMT18-718 | 0.12 | High | 465 | 27 | 19 | 43 | 17875 | 14650 | 2060 | 16
53QDMT18-718 | 0.12 | High | 465 | 27 | 19 | 46 | 17295 | 14370 | 2105 | 16
53QDMT18-718 | 0.12 | High | 465 | 27 | 19 | 52 | 16145 | 13805 | 2185 | 16
53QDMT18-718 | 0.12 | High | 465 | 32 | 23 | 35 | 19975 | 17580 | 2050 | 16
53QDMT18-718 | 0.12 | High | 465 | 32 | 23 | 43 | 18455 | 17150 | 2125 | 16
53QDMT18-718 | 0.12 | High | 465 | 32 | 23 | 46 | 17875 | 16990 | 2145 | 16
53QDMT18-718 | 0.12 | High | 465 | 32 | 23 | 52 | 16725 | 16665 | 2185 | 16
53QDMT18-718 | 0.12 | Medium | 288 | 21 | 15 | 35 | 17160 | 13150 | 1790 | 16
53QDMT18-718 | 0.12 | Medium | 288 | 21 | 15 | 43 | 16435 | 13215 | 1835 | 16
53QDMT18-718 | 0.12 | Medium | 288 | 21 | 15 | 46 | 16050 | 13080 | 1855 | 16
53QDMT18-718 | 0.12 | Medium | 288 | 21 | 15 | 52 | 15295 | 12810 | 1895 | 16
53QDMT18-718 | 0.12 | Medium | 288 | 24 | 17 | 35 | 17715 | 13750 | 1860 | 16
53QDMT18-718 | 0.12 | Medium | 288 | 24 | 17 | 43 | 16610 | 13385 | 1960 | 16
53QDMT18-718 | 0.12 | Medium | 288 | 24 | 17 | 46 | 16230 | 13215 | 2000 | 16
53QDMT18-718 | 0.12 | Medium | 288 | 24 | 17 | 52 | 15465 | 12885 | 2070 | 16
53QDMT18-718 | 0.12 | Medium | 288 | 27 | 19 | 35 | 18445 | 13780 | 1900 | 16
53QDMT18-718 | 0.12 | Medium | 288 | 27 | 19 | 43 | 17160 | 13480 | 2000 | 16
53QDMT18-718 | 0.12 | Medium | 288 | 27 | 19 | 46 | 16610 | 13220 | 2040 | 16
53QDMT18-718 | 0.12 | Medium | 288 | 27 | 19 | 52 | 15500 | 12700 | 2110 | 16
53QDMT18-718 | 0.12 | Medium | 288 | 32 | 23 | 35 | 19180 | 16180 | 1985 | 16
53QDMT18-718 | 0.12 | Medium | 288 | 32 | 23 | 43 | 17715 | 15780 | 2060 | 16
53QDMT18-718 | 0.12 | Medium | 288 | 32 | 23 | 46 | 17165 | 15635 | 2080 | 16
53QDMT18-718 | 0.12 | Medium | 288 | 32 | 23 | 52 | 16055 | 15335 | 2120 | 16
53QDMT18-718 | 0.12 | Low | 237 | 21 | 15 | 35 | 16445 | 12150 | 1715 | 16
53QDMT18-718 | 0.12 | Low | 237 | 21 | 15 | 43 | 15750 | 12210 | 1765 | 16
53QDMT18-718 | 0.12 | Low | 237 | 21 | 15 | 46 | 15385 | 12085 | 1785 | 16
53QDMT18-718 | 0.12 | Low | 237 | 21 | 15 | 52 | 14655 | 11835 | 1825 | 16
53QDMT18-718 | 0.12 | Low | 237 | 24 | 17 | 35 | 16980 | 12700 | 1785 | 16
53QDMT18-718 | 0.12 | Low | 237 | 24 | 17 | 43 | 15915 | 12365 | 1885 | 16
53QDMT18-718 | 0.12 | Low | 237 | 24 | 17 | 46 | 15550 | 11235 | 1920 | 16
53QDMT18-718 | 0.12 | Low | 237 | 24 | 17 | 52 | 14825 | 11905 | 1990 | 16
53QDMT18-718 | 0.12 | Low | 237 | 27 | 19 | 35 | 17675 | 13325 | 1845 | 16
53QDMT18-718 | 0.12 | Low | 237 | 27 | 19 | 43 | 16450 | 12455 | 1950 | 16
53QDMT18-718 | 0.12 | Low | 237 | 27 | 19 | 46 | 15915 | 11240 | 1985 | 16
53QDMT18-718 | 0.12 | Low | 237 | 27 | 19 | 52 | 14855 | 11735 | 2060 | 16
53QDMT18-718 | 0.12 | Low | 237 | 21 | 23 | 35 | 18380 | 14945 | 1905 | 16
53QDMT18-718 | 0.12 | Low | 237 | 21 | 23 | 43 | 16980 | 14580 | 1975 | 16
53QDMT18-718 | 0.12 | Low | 237 | 21 | 23 | 46 | 16450 | 13290 | 2000 | 16
53QDMT18-718 | 0.12 | Low | 237 | 21 | 23 | 52 | 15390 | 14170 | 2040 | 16
53QDMT18-718 | 0.16 | High | 444 | 21 | 15 | 35 | 17470 | 13970 | 1830 | 16
53QDMT18-718 | 0.16 | High | 444 | 21 | 15 | 43 | 16730 | 14040 | 1880 | 16
53QDMT18-718 | 0.16 | High | 444 | 21 | 15 | 46 | 16345 | 13900 | 1900 | 16
53QDMT18-718 | 0.16 | High | 444 | 21 | 15 | 52 | 15575 | 13615 | 1940 | 16
53QDMT18-718 | 0.16 | High | 444 | 24 | 17 | 35 | 18040 | 14610 | 1905 | 16
53QDMT18-718 | 0.16 | High | 444 | 24 | 17 | 43 | 16910 | 14220 | 2010 | 16
53QDMT18-718 | 0.16 | High | 444 | 24 | 17 | 46 | 16525 | 14045 | 2050 | 16
53QDMT18-718 | 0.16 | High | 444 | 24 | 17 | 52 | 15755 | 13695 | 2120 | 16
53QDMT18-718 | 0.16 | High | 444 | 27 | 19 | 35 | 18780 | 14635 | 1945 | 16
53QDMT18-718 | 0.16 | High | 444 | 27 | 19 | 43 | 17470 | 14320 | 2050 | 16
53QDMT18-718 | 0.16 | High | 444 | 27 | 19 | 46 | 16910 | 14050 | 2090 | 16
53QDMT18-718 | 0.16 | High | 444 | 27 | 19 | 52 | 15790 | 13515 | 2160 | 16
53QDMT18-718 | 0.16 | High | 444 | 32 | 23 | 35 | 19520 | 17185 | 2040 | 16
53QDMT18-718 | 0.16 | High | 444 | 32 | 23 | 43 | 18040 | 16765 | 2115 | 16
53QDMT18-718 | 0.16 | High | 444 | 32 | 23 | 46 | 17475 | 16610 | 2135 | 16
53QDMT18-718 | 0.16 | High | 444 | 32 | 23 | 52 | 16355 | 16295 | 2175 | 16
53QDMT18-718 | 0.16 | Medium | 267 | 21 | 15 | 35 | 16775 | 12850 | 1780 | 16
53QDMT18-718 | 0.16 | Medium | 267 | 21 | 15 | 43 | 16060 | 12920 | 1825 | 16
53QDMT18-718 | 0.16 | Medium | 267 | 21 | 15 | 46 | 15690 | 12790 | 1845 | 16
53QDMT18-718 | 0.16 | Medium | 267 | 21 | 15 | 52 | 14955 | 12530 | 1885 | 16
53QDMT18-718 | 0.16 | Medium | 267 | 24 | 17 | 35 | 17320 | 13440 | 1850 | 16
53QDMT18-718 | 0.16 | Medium | 267 | 24 | 17 | 43 | 16240 | 13085 | 1950 | 16
53QDMT18-718 | 0.16 | Medium | 267 | 24 | 17 | 46 | 15865 | 12925 | 1985 | 16
53QDMT18-718 | 0.16 | Medium | 267 | 24 | 17 | 52 | 15125 | 12600 | 2060 | 16
53QDMT18-718 | 0.16 | Medium | 267 | 27 | 19 | 35 | 18030 | 13465 | 1890 | 16
53QDMT18-718 | 0.16 | Medium | 267 | 27 | 19 | 43 | 16775 | 13180 | 1990 | 16
53QDMT18-718 | 0.16 | Medium | 267 | 27 | 19 | 46 | 16240 | 12930 | 2030 | 16
53QDMT18-718 | 0.16 | Medium | 267 | 27 | 19 | 52 | 15160 | 12435 | 2100 | 16
53QDMT18-718 | 0.16 | Medium | 267 | 32 | 23 | 35 | 18740 | 15815 | 1975 | 16
53QDMT18-718 | 0.16 | Medium | 267 | 32 | 23 | 43 | 17320 | 15430 | 2050 | 16
53QDMT18-718 | 0.16 | Medium | 267 | 32 | 23 | 46 | 16780 | 15280 | 2070 | 16
53QDMT18-718 | 0.16 | Medium | 267 | 32 | 23 | 52 | 15700 | 14995 | 2110 | 16
53QDMT18-718 | 0.16 | Low | 218 | 21 | 15 | 35 | 16075 | 11875 | 1705 | 16
53QDMT18-718 | 0.16 | Low | 218 | 21 | 15 | 43 | 15395 | 11940 | 1755 | 16
53QDMT18-718 | 0.16 | Low | 218 | 21 | 15 | 46 | 15035 | 11815 | 1775 | 16
53QDMT18-718 | 0.16 | Low | 218 | 21 | 15 | 52 | 14330 | 11575 | 1815 | 16
53QDMT18-718 | 0.16 | Low | 218 | 24 | 17 | 35 | 16600 | 12415 | 1775 | 16
53QDMT18-718 | 0.16 | Low | 218 | 24 | 17 | 43 | 15560 | 12090 | 1875 | 16
53QDMT18-718 | 0.16 | Low | 218 | 24 | 17 | 46 | 15210 | 11945 | 1910 | 16
53QDMT18-718 | 0.16 | Low | 218 | 24 | 17 | 52 | 14495 | 11645 | 1975 | 16
53QDMT18-718 | 0.16 | Low | 218 | 27 | 19 | 35 | 17280 | 12445 | 1815 | 16
53QDMT18-718 | 0.16 | Low | 218 | 27 | 19 | 43 | 16075 | 12175 | 1920 | 16
53QDMT18-718 | 0.16 | Low | 218 | 27 | 19 | 46 | 15560 | 11950 | 1955 | 16
53QDMT18-718 | 0.16 | Low | 218 | 27 | 19 | 52 | 14530 | 11490 | 2030 | 16
53QDMT18-718 | 0.16 | Low | 218 | 21 | 23 | 35 | 17960 | 14610 | 1895 | 16
53QDMT18-718 | 0.16 | Low | 218 | 21 | 23 | 43 | 16600 | 14250 | 1965 | 16
53QDMT18-718 | 0.16 | Low | 218 | 21 | 23 | 46 | 16080 | 14120 | 1985 | 16
53QDMT18-718 | 0.16 | Low | 218 | 21 | 23 | 52 | 15045 | 13855 | 2030 | 16
53QDMT18-718 | 0.2 | High | 423 | 21 | 15 | 35 | 17070 | 13645 | 1820 | 17
53QDMT18-718 | 0.2 | High | 423 | 21 | 15 | 43 | 16345 | 13720 | 1870 | 17
53QDMT18-718 | 0.2 | High | 423 | 21 | 15 | 46 | 15970 | 13585 | 1890 | 17
53QDMT18-718 | 0.2 | High | 423 | 21 | 15 | 52 | 15220 | 13310 | 1930 | 17
53QDMT18-718 | 0.2 | High | 423 | 24 | 17 | 35 | 17625 | 14270 | 1895 | 17
53QDMT18-718 | 0.2 | High | 423 | 24 | 17 | 43 | 16525 | 13900 | 2000 | 17
53QDMT18-718 | 0.2 | High | 423 | 24 | 17 | 46 | 16150 | 13730 | 2040 | 17
53QDMT18-718 | 0.2 | High | 423 | 24 | 17 | 52 | 15400 | 13390 | 2110 | 17
53QDMT18-718 | 0.2 | High | 423 | 27 | 19 | 35 | 18350 | 14300 | 1935 | 17
53QDMT18-718 | 0.2 | High | 423 | 27 | 19 | 43 | 17070 | 13990 | 2040 | 17
53QDMT18-718 | 0.2 | High | 423 | 27 | 19 | 46 | 16525 | 13735 | 2075 | 17
53QDMT18-718 | 0.2 | High | 423 | 27 | 19 | 52 | 15435 | 13225 | 2135 | 17
53QDMT18-718 | 0.2 | High | 423 | 32 | 23 | 35 | 19075 | 16790 | 2030 | 17
53QDMT18-718 | 0.2 | High | 423 | 32 | 23 | 43 | 17625 | 16380 | 2105 | 17
53QDMT18-718 | 0.2 | High | 423 | 32 | 23 | 46 | 17075 | 16230 | 2125 | 17
53QDMT18-718 | 0.2 | High | 423 | 32 | 23 | 52 | 15985 | 15925 | 2165 | 17
53QDMT18-718 | 0.2 | Medium | 246 | 21 | 15 | 35 | 16390 | 12555 | 1770 | 17
53QDMT18-718 | 0.2 | Medium | 246 | 21 | 15 | 43 | 15690 | 12620 | 1815 | 17
53QDMT18-718 | 0.2 | Medium | 246 | 21 | 15 | 46 | 15330 | 12505 | 1835 | 17
53QDMT18-718 | 0.2 | Medium | 246 | 21 | 15 | 52 | 14615 | 12245 | 1875 | 17
53QDMT18-718 | 0.2 | Medium | 246 | 24 | 17 | 35 | 16920 | 13135 | 1840 | 17
53QDMT18-718 | 0.2 | Medium | 246 | 24 | 17 | 43 | 15865 | 12790 | 1940 | 17
53QDMT18-718 | 0.2 | Medium | 246 | 24 | 17 | 46 | 15505 | 12630 | 1975 | 17
53QDMT18-718 | 0.2 | Medium | 246 | 24 | 17 | 52 | 14785 | 12320 | 2050 | 17
53QDMT18-718 | 0.2 | Medium | 246 | 27 | 19 | 35 | 17620 | 13155 | 1880 | 17
53QDMT18-718 | 0.2 | Medium | 246 | 27 | 19 | 43 | 16390 | 12875 | 1980 | 17
53QDMT18-718 | 0.2 | Medium | 246 | 27 | 19 | 46 | 15865 | 12635 | 2020 | 17
53QDMT18-718 | 0.2 | Medium | 246 | 27 | 19 | 52 | 14820 | 12175 | 2090 | 17
53QDMT18-718 | 0.2 | Medium | 246 | 32 | 23 | 35 | 18310 | 15445 | 1965 | 17
53QDMT18-718 | 0.2 | Medium | 246 | 32 | 23 | 43 | 16925 | 15075 | 2040 | 17
53QDMT18-718 | 0.2 | Medium | 246 | 32 | 23 | 46 | 16395 | 14930 | 2060 | 17
53QDMT18-718 | 0.2 | Medium | 246 | 32 | 23 | 52 | 15345 | 14650 | 2100 | 17
53QDMT18-718 | 0.2 | Low | 199 | 21 | 15 | 35 | 15710 | 11600 | 1695 | 17
53QDMT18-718 | 0.2 | Low | 199 | 21 | 15 | 43 | 15035 | 11665 | 1745 | 17
53QDMT18-718 | 0.2 | Low | 199 | 21 | 15 | 46 | 14690 | 11550 | 1765 | 17
53QDMT18-718 | 0.2 | Low | 199 | 21 | 15 | 52 | 14005 | 11320 | 1805 | 17
53QDMT18-718 | 0.2 | Low | 199 | 24 | 17 | 35 | 16220 | 12135 | 1765 | 17
53QDMT18-718 | 0.2 | Low | 199 | 24 | 17 | 43 | 15205 | 11815 | 1865 | 17
53QDMT18-718 | 0.2 | Low | 199 | 24 | 17 | 46 | 14865 | 12650 | 1900 | 17
53QDMT18-718 | 0.2 | Low | 199 | 24 | 17 | 52 | 14170 | 11385 | 1960 | 17
53QDMT18-718 | 0.2 | Low | 199 | 27 | 19 | 35 | 16885 | 11570 | 1785 | 17
53QDMT18-718 | 0.2 | Low | 199 | 27 | 19 | 43 | 15705 | 11890 | 1890 | 17
53QDMT18-718 | 0.2 | Low | 199 | 27 | 19 | 46 | 15205 | 12655 | 1925 | 17
53QDMT18-718 | 0.2 | Low | 199 | 27 | 19 | 52 | 14205 | 11245 | 2000 | 17
53QDMT18-718 | 0.2 | Low | 199 | 21 | 23 | 35 | 17550 | 14270 | 1885 | 17
53QDMT18-718 | 0.2 | Low | 199 | 21 | 23 | 43 | 16220 | 13925 | 1955 | 17
53QDMT18-718 | 0.2 | Low | 199 | 21 | 23 | 46 | 15715 | 14950 | 1975 | 17
53QDMT18-718 | 0.2 | Low | 199 | 21 | 23 | 52 | 14705 | 13545 | 2020 | 17
53QDMT18-718 | 0.24 | High | 401 | 21 | 15 | 35 | 16670 | 13320 | 1810 | 17
53QDMT18-718 | 0.24 | High | 401 | 21 | 15 | 43 | 15960 | 13400 | 1860 | 17
53QDMT18-718 | 0.24 | High | 401 | 21 | 15 | 46 | 15595 | 13270 | 1880 | 17
53QDMT18-718 | 0.24 | High | 401 | 21 | 15 | 52 | 14865 | 13005 | 1920 | 17
53QDMT18-718 | 0.24 | High | 401 | 24 | 17 | 35 | 17210 | 13930 | 1885 | 17
53QDMT18-718 | 0.24 | High | 401 | 24 | 17 | 43 | 16140 | 13580 | 1990 | 17
53QDMT18-718 | 0.24 | High | 401 | 24 | 17 | 46 | 15775 | 13415 | 2030 | 17
53QDMT18-718 | 0.24 | High | 401 | 24 | 17 | 52 | 15045 | 13085 | 2100 | 17
53QDMT18-718 | 0.24 | High | 401 | 27 | 19 | 35 | 17920 | 13965 | 1925 | 17
53QDMT18-718 | 0.24 | High | 401 | 27 | 19 | 43 | 16670 | 13660 | 2030 | 17
53QDMT18-718 | 0.24 | High | 401 | 27 | 19 | 46 | 16140 | 13420 | 2060 | 17
53QDMT18-718 | 0.24 | High | 401 | 27 | 19 | 52 | 15080 | 12935 | 2110 | 17
53QDMT18-718 | 0.24 | High | 401 | 32 | 23 | 35 | 18630 | 16395 | 2020 | 17
53QDMT18-718 | 0.24 | High | 401 | 32 | 23 | 43 | 17210 | 15995 | 2095 | 17
53QDMT18-718 | 0.24 | High | 401 | 32 | 23 | 46 | 16675 | 15850 | 2115 | 17
53QDMT18-718 | 0.24 | High | 401 | 32 | 23 | 52 | 15615 | 15555 | 2155 | 17
53QDMT18-718 | 0.24 | Medium | 226 | 21 | 15 | 35 | 16005 | 12260 | 1760 | 17
53QDMT18-718 | 0.24 | Medium | 226 | 21 | 15 | 43 | 15320 | 12320 | 1805 | 17
53QDMT18-718 | 0.24 | Medium | 226 | 21 | 15 | 46 | 14970 | 12220 | 1825 | 17
53QDMT18-718 | 0.24 | Medium | 226 | 21 | 15 | 52 | 14275 | 11960 | 1865 | 17
53QDMT18-718 | 0.24 | Medium | 226 | 24 | 17 | 35 | 16520 | 12830 | 1830 | 17
53QDMT18-718 | 0.24 | Medium | 226 | 24 | 17 | 43 | 15490 | 12495 | 1930 | 17
53QDMT18-718 | 0.24 | Medium | 226 | 24 | 17 | 46 | 15145 | 12335 | 1965 | 17
53QDMT18-718 | 0.24 | Medium | 226 | 24 | 17 | 52 | 14445 | 12040 | 2040 | 17
53QDMT18-718 | 0.24 | Medium | 226 | 27 | 19 | 35 | 17210 | 12845 | 1870 | 17
53QDMT18-718 | 0.24 | Medium | 226 | 27 | 19 | 43 | 16005 | 12570 | 1970 | 17
53QDMT18-718 | 0.24 | Medium | 226 | 27 | 19 | 46 | 15490 | 12340 | 2010 | 17
53QDMT18-718 | 0.24 | Medium | 226 | 27 | 19 | 52 | 14480 | 11915 | 2080 | 17
53QDMT18-718 | 0.24 | Medium | 226 | 32 | 23 | 35 | 17880 | 15075 | 1955 | 17
53QDMT18-718 | 0.24 | Medium | 226 | 32 | 23 | 43 | 16530 | 14720 | 2030 | 17
53QDMT18-718 | 0.24 | Medium | 226 | 32 | 23 | 46 | 16010 | 14580 | 2050 | 17
53QDMT18-718 | 0.24 | Medium | 226 | 32 | 23 | 52 | 14990 | 14305 | 2090 | 17
53QDMT18-718 | 0.24 | Low | 180 | 21 | 15 | 35 | 15345 | 11325 | 1685 | 17
53QDMT18-718 | 0.24 | Low | 180 | 21 | 15 | 43 | 14675 | 11390 | 1735 | 17
53QDMT18-718 | 0.24 | Low | 180 | 21 | 15 | 46 | 14345 | 11285 | 1755 | 17
53QDMT18-718 | 0.24 | Low | 180 | 21 | 15 | 52 | 13680 | 11065 | 1795 | 17
53QDMT18-718 | 0.24 | Low | 180 | 24 | 17 | 35 | 15840 | 11855 | 1755 | 17
53QDMT18-718 | 0.24 | Low | 180 | 24 | 17 | 43 | 14850 | 11540 | 1855 | 17
53QDMT18-718 | 0.24 | Low | 180 | 24 | 17 | 46 | 14520 | 13355 | 1890 | 17
53QDMT18-718 | 0.24 | Low | 180 | 24 | 17 | 52 | 13845 | 11125 | 1945 | 17
53QDMT18-718 | 0.24 | Low | 180 | 27 | 19 | 35 | 16490 | 10695 | 1755 | 17
53QDMT18-718 | 0.24 | Low | 180 | 27 | 19 | 43 | 15335 | 11605 | 1860 | 17
53QDMT18-718 | 0.24 | Low | 180 | 27 | 19 | 46 | 14850 | 13360 | 1895 | 17
53QDMT18-718 | 0.24 | Low | 180 | 27 | 19 | 52 | 13880 | 11000 | 1970 | 17
53QDMT18-718 | 0.24 | Low | 180 | 21 | 23 | 35 | 17140 | 13930 | 1875 | 17
53QDMT18-718 | 0.24 | Low | 180 | 21 | 23 | 43 | 15840 | 13600 | 1945 | 17
53QDMT18-718 | 0.24 | Low | 180 | 21 | 23 | 46 | 15350 | 15780 | 1965 | 17
53QDMT18-718 | 0.24 | Low | 180 | 21 | 23 | 52 | 14365 | 13235 | 2010 | 17
53QDMT24-718 | 0 | High | 755 | 21 | 15 | 35 | 23890 | 19115 | 2265 | 18
53QDMT24-718 | 0 | High | 755 | 21 | 15 | 43 | 22880 | 19225 | 2335 | 18
53QDMT24-718 | 0 | High | 755 | 21 | 15 | 46 | 22375 | 19025 | 2358 | 18
53QDMT24-718 | 0 | High | 755 | 21 | 15 | 52 | 21365 | 18625 | 2405 | 18
53QDMT24-718 | 0 | High | 755 | 24 | 17 | 35 | 24690 | 19985 | 2365 | 18
53QDMT24-718 | 0 | High | 755 | 24 | 17 | 43 | 23135 | 19445 | 2490 | 18
53QDMT24-718 | 0 | High | 755 | 24 | 17 | 46 | 22630 | 19235 | 2535 | 18
53QDMT24-718 | 0 | High | 755 | 24 | 17 | 52 | 21620 | 18815 | 2625 | 18
53QDMT24-718 | 0 | High | 755 | 27 | 19 | 35 | 25700 | 20055 | 2415 | 18
53QDMT24-718 | 0 | High | 755 | 27 | 19 | 43 | 23890 | 19585 | 2540 | 18
53QDMT24-718 | 0 | High | 755 | 27 | 19 | 46 | 23130 | 19195 | 2585 | 18
53QDMT24-718 | 0 | High | 755 | 27 | 19 | 52 | 21610 | 18415 | 2675 | 18
53QDMT24-718 | 0 | High | 755 | 32 | 23 | 35 | 26715 | 23530 | 2535 | 18
53QDMT24-718 | 0 | High | 755 | 32 | 23 | 43 | 24690 | 22955 | 2630 | 18
53QDMT24-718 | 0 | High | 755 | 32 | 23 | 46 | 23895 | 22710 | 2655 | 18
53QDMT24-718 | 0 | High | 755 | 32 | 23 | 52 | 22305 | 22220 | 2705 | 18
53QDMT24-718 | 0 | Medium | 495 | 21 | 15 | 35 | 22935 | 17590 | 2200 | 18
53QDMT24-718 | 0 | Medium | 495 | 21 | 15 | 43 | 21965 | 17690 | 2270 | 18
53QDMT24-718 | 0 | Medium | 495 | 21 | 15 | 46 | 21480 | 17505 | 2295 | 18
53QDMT24-718 | 0 | Medium | 495 | 21 | 15 | 52 | 20510 | 17135 | 2345 | 18
53QDMT24-718 | 0 | Medium | 495 | 24 | 17 | 35 | 23705 | 18390 | 2295 | 18
53QDMT24-718 | 0 | Medium | 495 | 24 | 17 | 43 | 22210 | 17890 | 2405 | 18
53QDMT24-718 | 0 | Medium | 495 | 24 | 17 | 46 | 21725 | 17700 | 2450 | 18
53QDMT24-718 | 0 | Medium | 495 | 24 | 17 | 52 | 20755 | 17310 | 2540 | 18
53QDMT24-718 | 0 | Medium | 495 | 27 | 19 | 35 | 24675 | 18455 | 2345 | 18
53QDMT24-718 | 0 | Medium | 495 | 27 | 19 | 43 | 22935 | 18020 | 2455 | 18
53QDMT24-718 | 0 | Medium | 495 | 27 | 19 | 46 | 22205 | 17660 | 2500 | 18
53QDMT24-718 | 0 | Medium | 495 | 27 | 19 | 52 | 20750 | 16945 | 2590 | 18
53QDMT24-718 | 0 | Medium | 495 | 32 | 23 | 35 | 25650 | 21650 | 2460 | 18
53QDMT24-718 | 0 | Medium | 495 | 32 | 23 | 43 | 23705 | 21120 | 2545 | 18
53QDMT24-718 | 0 | Medium | 495 | 32 | 23 | 46 | 22940 | 20895 | 2570 | 18
53QDMT24-718 | 0 | Medium | 495 | 32 | 23 | 52 | 21415 | 20445 | 2620 | 18
53QDMT24-718 | 0 | Low | 430 | 21 | 15 | 35 | 21980 | 16250 | 2105 | 18
53QDMT24-718 | 0 | Low | 430 | 21 | 15 | 43 | 21050 | 16345 | 2170 | 18
53QDMT24-718 | 0 | Low | 430 | 21 | 15 | 46 | 20585 | 16175 | 2195 | 18
53QDMT24-718 | 0 | Low | 430 | 21 | 15 | 52 | 19660 | 15835 | 2245 | 18
53QDMT24-718 | 0 | Low | 430 | 24 | 17 | 35 | 22715 | 16990 | 2200 | 18
53QDMT24-718 | 0 | Low | 430 | 24 | 17 | 43 | 21285 | 16530 | 2315 | 18
53QDMT24-718 | 0 | Low | 430 | 24 | 17 | 46 | 20820 | 16350 | 2360 | 18
53QDMT24-718 | 0 | Low | 430 | 24 | 17 | 52 | 19890 | 15995 | 2450 | 18
53QDMT24-718 | 0 | Low | 430 | 27 | 19 | 35 | 23645 | 17050 | 2245 | 18
53QDMT24-718 | 0 | Low | 430 | 27 | 19 | 43 | 21980 | 16650 | 2365 | 18
53QDMT24-718 | 0 | Low | 430 | 27 | 19 | 46 | 21280 | 16320 | 2410 | 18
53QDMT24-718 | 0 | Low | 430 | 27 | 19 | 52 | 19885 | 15655 | 2500 | 18
53QDMT24-718 | 0 | Low | 430 | 21 | 23 | 35 | 24580 | 20000 | 2360 | 18
53QDMT24-718 | 0 | Low | 430 | 21 | 23 | 43 | 22715 | 19515 | 2450 | 18
53QDMT24-718 | 0 | Low | 430 | 21 | 23 | 46 | 21985 | 19305 | 2475 | 18
53QDMT24-718 | 0 | Low | 430 | 21 | 23 | 52 | 20525 | 18890 | 2525 | 18
53QDMT24-718 | 0.08 | High | 683 | 21 | 15 | 35 | 23135 | 18505 | 2255 | 18
53QDMT24-718 | 0.08 | High | 683 | 21 | 15 | 43 | 22160 | 18620 | 2325 | 18
53QDMT24-718 | 0.08 | High | 683 | 21 | 15 | 46 | 21670 | 18425 | 2350 | 18
53QDMT24-718 | 0.08 | High | 683 | 21 | 15 | 52 | 20040 | 18040 | 2400 | 18
53QDMT24-718 | 0.08 | High | 683 | 24 | 17 | 35 | 23900 | 19375 | 2355 | 18
53QDMT24-718 | 0.08 | High | 683 | 24 | 17 | 43 | 22395 | 18820 | 2480 | 18
53QDMT24-718 | 0.08 | High | 683 | 24 | 17 | 46 | 21905 | 18620 | 2525 | 18
53QDMT24-718 | 0.08 | High | 683 | 24 | 17 | 52 | 20930 | 18215 | 2615 | 18
53QDMT24-718 | 0.08 | High | 683 | 27 | 19 | 35 | 24875 | 19410 | 2405 | 18
53QDMT24-718 | 0.08 | High | 683 | 27 | 19 | 43 | 23125 | 18960 | 2530 | 18
53QDMT24-718 | 0.08 | High | 683 | 27 | 19 | 46 | 22390 | 18585 | 2575 | 18
53QDMT24-718 | 0.08 | High | 683 | 27 | 19 | 52 | 20925 | 17830 | 2665 | 18
53QDMT24-718 | 0.08 | High | 683 | 32 | 23 | 35 | 25855 | 22765 | 2525 | 18
53QDMT24-718 | 0.08 | High | 683 | 32 | 23 | 43 | 23900 | 22220 | 2620 | 18
53QDMT24-718 | 0.08 | High | 683 | 32 | 23 | 46 | 23130 | 21985 | 2645 | 18
53QDMT24-718 | 0.08 | High | 683 | 32 | 23 | 52 | 21590 | 21510 | 2700 | 18
53QDMT24-718 | 0.08 | Medium | 419 | 21 | 15 | 35 | 22210 | 17025 | 2190 | 18
53QDMT24-718 | 0.08 | Medium | 419 | 21 | 15 | 43 | 21275 | 17130 | 2265 | 18
53QDMT24-718 | 0.08 | Medium | 419 | 21 | 15 | 46 | 20805 | 16955 | 2290 | 18
53QDMT24-718 | 0.08 | Medium | 419 | 21 | 15 | 52 | 19240 | 16595 | 2340 | 18
53QDMT24-718 | 0.08 | Medium | 419 | 24 | 17 | 35 | 22945 | 17830 | 2285 | 18
53QDMT24-718 | 0.08 | Medium | 419 | 24 | 17 | 43 | 21500 | 17320 | 2395 | 18
53QDMT24-718 | 0.08 | Medium | 419 | 24 | 17 | 46 | 21030 | 17135 | 2440 | 18
53QDMT24-718 | 0.08 | Medium | 419 | 24 | 17 | 52 | 20095 | 16760 | 2530 | 18
53QDMT24-718 | 0.08 | Medium | 419 | 27 | 19 | 35 | 23880 | 17860 | 2335 | 18
53QDMT24-718 | 0.08 | Medium | 419 | 27 | 19 | 43 | 22200 | 17445 | 2450 | 18
53QDMT24-718 | 0.08 | Medium | 419 | 27 | 19 | 46 | 21560 | 17100 | 2495 | 18
53QDMT24-718 | 0.08 | Medium | 419 | 27 | 19 | 52 | 20090 | 16405 | 2585 | 18
53QDMT24-718 | 0.08 | Medium | 419 | 32 | 23 | 35 | 24825 | 20950 | 2450 | 18
53QDMT24-718 | 0.08 | Medium | 419 | 32 | 23 | 43 | 22945 | 20445 | 2535 | 18
53QDMT24-718 | 0.08 | Medium | 419 | 32 | 23 | 46 | 22205 | 20225 | 2560 | 18
53QDMT24-718 | 0.08 | Medium | 419 | 32 | 23 | 52 | 20520 | 19790 | 2610 | 18
53QDMT24-718 | 0.08 | Low | 335 | 21 | 15 | 35 | 21230 | 15730 | 2100 | 18
53QDMT24-718 | 0.08 | Low | 335 | 21 | 15 | 43 | 20385 | 15830 | 2165 | 18
53QDMT24-718 | 0.08 | Low | 335 | 21 | 15 | 46 | 19940 | 15665 | 2190 | 18
53QDMT24-718 | 0.08 | Low | 335 | 21 | 15 | 52 | 18440 | 15335 | 2235 | 18
53QDMT24-718 | 0.08 | Low | 335 | 24 | 17 | 35 | 21985 | 16470 | 2195 | 18
53QDMT24-718 | 0.08 | Low | 335 | 24 | 17 | 43 | 20605 | 16000 | 2310 | 18
53QDMT24-718 | 0.08 | Low | 335 | 24 | 17 | 46 | 20155 | 15830 | 2355 | 18
53QDMT24-718 | 0.08 | Low | 335 | 24 | 17 | 52 | 19255 | 15485 | 2440 | 18
53QDMT24-718 | 0.08 | Low | 335 | 27 | 19 | 35 | 22885 | 16500 | 2235 | 18
53QDMT24-718 | 0.08 | Low | 335 | 27 | 19 | 43 | 21275 | 16120 | 2355 | 18
53QDMT24-718 | 0.08 | Low | 335 | 27 | 19 | 46 | 20600 | 15800 | 2400 | 18
53QDMT24-718 | 0.08 | Low | 335 | 27 | 19 | 52 | 19255 | 15160 | 2490 | 18
53QDMT24-718 | 0.08 | Low | 335 | 21 | 23 | 35 | 23789 | 19355 | 2350 | 18
53QDMT24-718 | 0.08 | Low | 335 | 21 | 23 | 43 | 21985 | 18890 | 2440 | 18
53QDMT24-718 | 0.08 | Low | 335 | 21 | 23 | 46 | 21280 | 18690 | 2465 | 18
53QDMT24-718 | 0.08 | Low | 335 | 21 | 23 | 52 | 19870 | 18285 | 2515 | 18
53QDMT24-718 | 0.12 | High | 651 | 21 | 15 | 35 | 22780 | 18195 | 2250 | 18
53QDMT24-718 | 0.12 | High | 651 | 21 | 15 | 43 | 21820 | 18335 | 2320 | 18
53QDMT24-718 | 0.12 | High | 651 | 21 | 15 | 46 | 21340 | 18145 | 2345 | 18
53QDMT24-718 | 0.12 | High | 651 | 21 | 15 | 52 | 17765 | 17765 | 2395 | 18
53QDMT24-718 | 0.12 | High | 651 | 24 | 17 | 35 | 23500 | 19070 | 2350 | 18
53QDMT24-718 | 0.12 | High | 651 | 24 | 17 | 43 | 22020 | 18510 | 2475 | 18
53QDMT24-718 | 0.12 | High | 651 | 24 | 17 | 46 | 21540 | 18310 | 2520 | 18
53QDMT24-718 | 0.12 | High | 651 | 24 | 17 | 52 | 20580 | 17910 | 2610 | 18
53QDMT24-718 | 0.12 | High | 651 | 27 | 19 | 35 | 24460 | 19085 | 2400 | 18
53QDMT24-718 | 0.12 | High | 651 | 27 | 19 | 43 | 22740 | 18645 | 2525 | 18
53QDMT24-718 | 0.12 | High | 651 | 27 | 19 | 46 | 22020 | 18275 | 2570 | 18
53QDMT24-718 | 0.12 | High | 651 | 27 | 19 | 52 | 20580 | 17535 | 2660 | 18
53QDMT24-718 | 0.12 | High | 651 | 32 | 23 | 35 | 25425 | 22385 | 2520 | 18
53QDMT24-718 | 0.12 | High | 651 | 32 | 23 | 43 | 23500 | 21850 | 2615 | 18
53QDMT24-718 | 0.12 | High | 651 | 32 | 23 | 46 | 22745 | 21620 | 2640 | 18
53QDMT24-718 | 0.12 | High | 651 | 32 | 23 | 52 | 21235 | 21160 | 2690 | 18
53QDMT24-718 | 0.12 | Medium | 373 | 21 | 15 | 35 | 21870 | 16740 | 2185 | 18
53QDMT24-718 | 0.12 | Medium | 373 | 21 | 15 | 43 | 20950 | 16870 | 2260 | 18
53QDMT24-718 | 0.12 | Medium | 373 | 21 | 15 | 46 | 20490 | 16695 | 2285 | 18
53QDMT24-718 | 0.12 | Medium | 373 | 21 | 15 | 52 | 17055 | 16345 | 2335 | 18
53QDMT24-718 | 0.12 | Medium | 373 | 24 | 17 | 35 | 22560 | 17545 | 2280 | 18
53QDMT24-718 | 0.12 | Medium | 373 | 24 | 17 | 43 | 21140 | 17030 | 2390 | 18
53QDMT24-718 | 0.12 | Medium | 373 | 24 | 17 | 46 | 20680 | 16845 | 2435 | 18
53QDMT24-718 | 0.12 | Medium | 373 | 24 | 17 | 52 | 19760 | 16480 | 2525 | 18
53QDMT24-718 | 0.12 | Medium | 373 | 27 | 19 | 35 | 23485 | 17560 | 2325 | 18
53QDMT24-718 | 0.12 | Medium | 373 | 27 | 19 | 43 | 21830 | 17155 | 2445 | 18
53QDMT24-718 | 0.12 | Medium | 373 | 27 | 19 | 46 | 21395 | 16815 | 2490 | 18
53QDMT24-718 | 0.12 | Medium | 373 | 27 | 19 | 52 | 19760 | 16135 | 2580 | 18
53QDMT24-718 | 0.12 | Medium | 373 | 32 | 23 | 35 | 24410 | 20595 | 2440 | 18
53QDMT24-718 | 0.12 | Medium | 373 | 32 | 23 | 43 | 22560 | 20105 | 2530 | 18
53QDMT24-718 | 0.12 | Medium | 373 | 32 | 23 | 46 | 21835 | 19890 | 2555 | 18
53QDMT24-718 | 0.12 | Medium | 373 | 32 | 23 | 52 | 19540 | 19470 | 2605 | 18
53QDMT24-718 | 0.12 | Low | 288 | 21 | 15 | 35 | 20690 | 15470 | 2095 | 18
53QDMT24-718 | 0.12 | Low | 288 | 21 | 15 | 43 | 20075 | 15585 | 2160 | 18
53QDMT24-718 | 0.12 | Low | 288 | 21 | 15 | 46 | 19635 | 15425 | 2185 | 18
53QDMT24-718 | 0.12 | Low | 288 | 21 | 15 | 52 | 16345 | 15100 | 2235 | 18
53QDMT24-718 | 0.12 | Low | 288 | 24 | 17 | 35 | 21620 | 16210 | 2185 | 18
53QDMT24-718 | 0.12 | Low | 288 | 24 | 17 | 43 | 20260 | 15735 | 2305 | 18
53QDMT24-718 | 0.12 | Low | 288 | 24 | 17 | 46 | 19820 | 15565 | 2345 | 18
53QDMT24-718 | 0.12 | Low | 288 | 24 | 17 | 52 | 18935 | 15225 | 2425 | 18
53QDMT24-718 | 0.12 | Low | 288 | 27 | 19 | 35 | 22505 | 16225 | 2230 | 18
53QDMT24-718 | 0.12 | Low | 288 | 27 | 19 | 43 | 20925 | 15850 | 2350 | 18
53QDMT24-718 | 0.12 | Low | 288 | 27 | 19 | 46 | 20260 | 15535 | 2395 | 18
53QDMT24-718 | 0.12 | Low | 288 | 27 | 19 | 52 | 18935 | 14905 | 2485 | 18
53QDMT24-718 | 0.12 | Low | 288 | 21 | 23 | 35 | 23395 | 19030 | 2340 | 18
53QDMT24-718 | 0.12 | Low | 288 | 21 | 23 | 43 | 21620 | 18575 | 2435 | 18
53QDMT24-718 | 0.12 | Low | 288 | 21 | 23 | 46 | 20925 | 18380 | 2460 | 18
53QDMT24-718 | 0.12 | Low | 288 | 21 | 23 | 52 | 19540 | 17990 | 2510 | 18
53QDMT24-718 | 0.16 | High | 614 | 21 | 15 | 35 | 22375 | 17890 | 2245 | 18
53QDMT24-718 | 0.16 | High | 614 | 21 | 15 | 43 | 21435 | 18010 | 2315 | 18
53QDMT24-718 | 0.16 | High | 614 | 21 | 15 | 46 | 20965 | 17825 | 2340 | 18
53QDMT24-718 | 0.16 | High | 614 | 21 | 15 | 52 | 18715 | 17450 | 2390 | 18
53QDMT24-718 | 0.16 | High | 614 | 24 | 17 | 35 | 23105 | 18765 | 2345 | 18
53QDMT24-718 | 0.16 | High | 614 | 24 | 17 | 43 | 21650 | 18195 | 2470 | 18
53QDMT24-718 | 0.16 | High | 614 | 24 | 17 | 46 | 21180 | 18005 | 2515 | 18
53QDMT24-718 | 0.16 | High | 614 | 24 | 17 | 52 | 20240 | 17615 | 2605 | 18
53QDMT24-718 | 0.16 | High | 614 | 27 | 19 | 35 | 24045 | 18760 | 2395 | 18
53QDMT24-718 | 0.16 | High | 614 | 27 | 19 | 43 | 22355 | 18330 | 2520 | 18
53QDMT24-718 | 0.16 | High | 614 | 27 | 19 | 46 | 21650 | 17970 | 2565 | 18
53QDMT24-718 | 0.16 | High | 614 | 27 | 19 | 52 | 20235 | 17245 | 2655 | 18
53QDMT24-718 | 0.16 | High | 614 | 32 | 23 | 35 | 24995 | 22000 | 2515 | 18
53QDMT24-718 | 0.16 | High | 614 | 32 | 23 | 43 | 23105 | 21480 | 2610 | 18
53QDMT24-718 | 0.16 | High | 614 | 32 | 23 | 46 | 22360 | 21255 | 2635 | 18
53QDMT24-718 | 0.16 | High | 614 | 32 | 23 | 52 | 20875 | 20800 | 2690 | 18
53QDMT24-718 | 0.16 | Medium | 330 | 21 | 15 | 35 | 21485 | 16460 | 2180 | 18
53QDMT24-718 | 0.16 | Medium | 330 | 21 | 15 | 43 | 20580 | 16570 | 2255 | 18
53QDMT24-718 | 0.16 | Medium | 330 | 21 | 15 | 46 | 20130 | 16400 | 2280 | 18
53QDMT24-718 | 0.16 | Medium | 330 | 21 | 15 | 52 | 17970 | 16055 | 2330 | 18
53QDMT24-718 | 0.16 | Medium | 330 | 24 | 17 | 35 | 22180 | 17265 | 2275 | 18
53QDMT24-718 | 0.16 | Medium | 330 | 24 | 17 | 43 | 20785 | 16745 | 2385 | 18
53QDMT24-718 | 0.16 | Medium | 330 | 24 | 17 | 46 | 20333 | 16565 | 2430 | 18
53QDMT24-718 | 0.16 | Medium | 330 | 24 | 17 | 52 | 19430 | 16205 | 2520 | 18
53QDMT24-718 | 0.16 | Medium | 330 | 27 | 19 | 35 | 23085 | 17260 | 2320 | 18
53QDMT24-718 | 0.16 | Medium | 330 | 27 | 19 | 43 | 21465 | 16865 | 2440 | 18
53QDMT24-718 | 0.16 | Medium | 330 | 27 | 19 | 46 | 20910 | 16535 | 2485 | 18
53QDMT24-718 | 0.16 | Medium | 330 | 27 | 19 | 52 | 19430 | 15865 | 2575 | 18
53QDMT24-718 | 0.16 | Medium | 330 | 32 | 23 | 35 | 23995 | 20245 | 2435 | 18
53QDMT24-718 | 0.16 | Medium | 330 | 32 | 23 | 43 | 22180 | 19765 | 2525 | 18
53QDMT24-718 | 0.16 | Medium | 330 | 32 | 23 | 46 | 21470 | 19555 | 2550 | 18
53QDMT24-718 | 0.16 | Medium | 330 | 32 | 23 | 52 | 19620 | 19135 | 2600 | 18
53QDMT24-718 | 0.16 | Low | 236 | 21 | 15 | 35 | 20455 | 15210 | 2090 | 18
53QDMT24-718 | 0.16 | Low | 236 | 21 | 15 | 43 | 19720 | 15310 | 2155 | 18
53QDMT24-718 | 0.16 | Low | 236 | 21 | 15 | 46 | 19290 | 15150 | 2180 | 18
53QDMT24-718 | 0.16 | Low | 236 | 21 | 15 | 52 | 17220 | 14835 | 2225 | 18
53QDMT24-718 | 0.16 | Low | 236 | 24 | 17 | 35 | 21255 | 15950 | 2185 | 18
53QDMT24-718 | 0.16 | Low | 236 | 24 | 17 | 43 | 19920 | 15470 | 2305 | 18
53QDMT24-718 | 0.16 | Low | 236 | 24 | 17 | 46 | 19485 | 15305 | 2345 | 18
53QDMT24-718 | 0.16 | Low | 236 | 24 | 17 | 52 | 18620 | 14975 | 2425 | 18
53QDMT24-718 | 0.16 | Low | 236 | 27 | 19 | 35 | 22125 | 15950 | 2225 | 18
53QDMT24-718 | 0.16 | Low | 236 | 27 | 19 | 43 | 20570 | 15585 | 2345 | 18
53QDMT24-718 | 0.16 | Low | 236 | 27 | 19 | 46 | 19920 | 15275 | 2390 | 18
53QDMT24-718 | 0.16 | Low | 236 | 27 | 19 | 52 | 18620 | 14660 | 2480 | 18
53QDMT24-718 | 0.16 | Low | 236 | 21 | 23 | 35 | 22998 | 18705 | 2335 | 18
53QDMT24-718 | 0.16 | Low | 236 | 21 | 23 | 43 | 21255 | 18260 | 2430 | 18
53QDMT24-718 | 0.16 | Low | 236 | 21 | 23 | 46 | 20575 | 18070 | 2455 | 18
53QDMT24-718 | 0.16 | Low | 236 | 21 | 23 | 52 | 19210 | 17680 | 2505 | 18
53QDMT24-718 | 0.2 | High | 580 | 21 | 15 | 35 | 21970 | 17580 | 2240 | 19
53QDMT24-718 | 0.2 | High | 580 | 21 | 15 | 43 | 21045 | 17685 | 2310 | 19
53QDMT24-718 | 0.2 | High | 580 | 21 | 15 | 46 | 20585 | 17500 | 2335 | 19
53QDMT24-718 | 0.2 | High | 580 | 21 | 15 | 52 | 19665 | 17130 | 2385 | 19
53QDMT24-718 | 0.2 | High | 580 | 24 | 17 | 35 | 22705 | 18455 | 2340 | 19
53QDMT24-718 | 0.2 | High | 580 | 24 | 17 | 43 | 21275 | 17885 | 2465 | 19
53QDMT24-718 | 0.2 | High | 580 | 24 | 17 | 46 | 20815 | 17695 | 2510 | 19
53QDMT24-718 | 0.2 | High | 580 | 24 | 17 | 52 | 19895 | 17315 | 2600 | 19
53QDMT24-718 | 0.2 | High | 580 | 27 | 19 | 35 | 23630 | 18435 | 2385 | 19
53QDMT24-718 | 0.2 | High | 580 | 27 | 19 | 43 | 21970 | 18015 | 2510 | 19
53QDMT24-718 | 0.2 | High | 580 | 27 | 19 | 46 | 21275 | 17660 | 2555 | 19
53QDMT24-718 | 0.2 | High | 580 | 27 | 19 | 52 | 19885 | 16950 | 2645 | 19
53QDMT24-718 | 0.2 | High | 580 | 32 | 23 | 35 | 24565 | 21615 | 2505 | 19
53QDMT24-718 | 0.2 | High | 580 | 32 | 23 | 43 | 22705 | 21110 | 2600 | 19
53QDMT24-718 | 0.2 | High | 580 | 32 | 23 | 46 | 21975 | 20885 | 2630 | 19
53QDMT24-718 | 0.2 | High | 580 | 32 | 23 | 52 | 20515 | 20435 | 2690 | 19
53QDMT24-718 | 0.2 | Medium | 290 | 21 | 15 | 35 | 21095 | 16175 | 2175 | 19
53QDMT24-718 | 0.2 | Medium | 290 | 21 | 15 | 43 | 20205 | 16270 | 2250 | 19
53QDMT24-718 | 0.2 | Medium | 290 | 21 | 15 | 46 | 19765 | 16100 | 2275 | 19
53QDMT24-718 | 0.2 | Medium | 290 | 21 | 15 | 52 | 18880 | 15760 | 2325 | 19
53QDMT24-718 | 0.2 | Medium | 290 | 24 | 17 | 35 | 21800 | 16980 | 2270 | 19
53QDMT24-718 | 0.2 | Medium | 290 | 24 | 17 | 43 | 20425 | 16455 | 2380 | 19
53QDMT24-718 | 0.2 | Medium | 290 | 24 | 17 | 46 | 19985 | 16280 | 2425 | 19
53QDMT24-718 | 0.2 | Medium | 290 | 24 | 17 | 52 | 19100 | 15930 | 2515 | 19
53QDMT24-718 | 0.2 | Medium | 290 | 27 | 19 | 35 | 22685 | 16960 | 2315 | 19
53QDMT24-718 | 0.2 | Medium | 290 | 27 | 19 | 43 | 21095 | 16575 | 2435 | 19
53QDMT24-718 | 0.2 | Medium | 290 | 27 | 19 | 46 | 20425 | 16250 | 2480 | 19
53QDMT24-718 | 0.2 | Medium | 290 | 27 | 19 | 52 | 19100 | 15595 | 2570 | 19
53QDMT24-718 | 0.2 | Medium | 290 | 32 | 23 | 35 | 23585 | 19890 | 2430 | 19
53QDMT24-718 | 0.2 | Medium | 290 | 32 | 23 | 43 | 21800 | 19425 | 2520 | 19
53QDMT24-718 | 0.2 | Medium | 290 | 32 | 23 | 46 | 21100 | 19215 | 2545 | 19
53QDMT24-718 | 0.2 | Medium | 290 | 32 | 23 | 52 | 19695 | 18800 | 2595 | 19
53QDMT24-718 | 0.2 | Low | 188 | 21 | 15 | 35 | 20215 | 14945 | 2085 | 19
53QDMT24-718 | 0.2 | Low | 188 | 21 | 15 | 43 | 19365 | 15035 | 2150 | 19
53QDMT24-718 | 0.2 | Low | 188 | 21 | 15 | 46 | 18940 | 14875 | 2170 | 19
53QDMT24-718 | 0.2 | Low | 188 | 21 | 15 | 52 | 18095 | 14565 | 2210 | 19
53QDMT24-718 | 0.2 | Low | 188 | 24 | 17 | 35 | 20890 | 15690 | 2180 | 19
53QDMT24-718 | 0.2 | Low | 188 | 24 | 17 | 43 | 19575 | 15205 | 2300 | 19
53QDMT24-718 | 0.2 | Low | 188 | 24 | 17 | 46 | 19150 | 15045 | 2340 | 19
53QDMT24-718 | 0.2 | Low | 188 | 24 | 17 | 52 | 18305 | 14720 | 2420 | 19
53QDMT24-718 | 0.2 | Low | 188 | 27 | 19 | 35 | 21740 | 15670 | 2220 | 19
53QDMT24-718 | 0.2 | Low | 188 | 27 | 19 | 43 | 20215 | 15315 | 2340 | 19
53QDMT24-718 | 0.2 | Low | 188 | 27 | 19 | 46 | 19575 | 15015 | 2385 | 19
53QDMT24-718 | 0.2 | Low | 188 | 27 | 19 | 52 | 18305 | 14410 | 2475 | 19
53QDMT24-718 | 0.2 | Low | 188 | 21 | 23 | 35 | 22600 | 18375 | 2330 | 19
53QDMT24-718 | 0.2 | Low | 188 | 21 | 23 | 43 | 20890 | 17945 | 2425 | 19
53QDMT24-718 | 0.2 | Low | 188 | 21 | 23 | 46 | 20220 | 17755 | 2450 | 19
53QDMT24-718 | 0.2 | Low | 188 | 21 | 23 | 52 | 18875 | 17370 | 2500 | 19
53QDMT24-718 | 0.24 | High | 545 | 21 | 15 | 35 | 21565 | 17270 | 2235 | 19
53QDMT24-718 | 0.24 | High | 545 | 21 | 15 | 43 | 20655 | 17360 | 2305 | 19
53QDMT24-718 | 0.24 | High | 545 | 21 | 15 | 46 | 20205 | 17175 | 2330 | 19
53QDMT24-718 | 0.24 | High | 545 | 21 | 15 | 52 | 20615 | 16810 | 2380 | 19
53QDMT24-718 | 0.24 | High | 545 | 24 | 17 | 35 | 22305 | 18145 | 2335 | 19
53QDMT24-718 | 0.24 | High | 545 | 24 | 17 | 43 | 20900 | 17575 | 2460 | 19
53QDMT24-718 | 0.24 | High | 545 | 24 | 17 | 46 | 20450 | 17385 | 2505 | 19
53QDMT24-718 | 0.24 | High | 545 | 24 | 17 | 52 | 19550 | 17015 | 2595 | 19
53QDMT24-718 | 0.24 | High | 545 | 27 | 19 | 35 | 23215 | 18110 | 2375 | 19
53QDMT24-718 | 0.24 | High | 545 | 27 | 19 | 43 | 21585 | 17700 | 2500 | 19
53QDMT24-718 | 0.24 | High | 545 | 27 | 19 | 46 | 20900 | 17350 | 2545 | 19
53QDMT24-718 | 0.24 | High | 545 | 27 | 19 | 52 | 19535 | 16655 | 2635 | 19
53QDMT24-718 | 0.24 | High | 545 | 32 | 23 | 35 | 24135 | 21230 | 2495 | 19
53QDMT24-718 | 0.24 | High | 545 | 32 | 23 | 43 | 22305 | 20740 | 2590 | 19
53QDMT24-718 | 0.24 | High | 545 | 32 | 23 | 46 | 21590 | 20515 | 2625 | 19
53QDMT24-718 | 0.24 | High | 545 | 32 | 23 | 52 | 20155 | 20070 | 2690 | 19
53QDMT24-718 | 0.24 | Medium | 249 | 21 | 15 | 35 | 20705 | 15890 | 2170 | 19
53QDMT24-718 | 0.24 | Medium | 249 | 21 | 15 | 43 | 19830 | 15970 | 2245 | 19
53QDMT24-718 | 0.24 | Medium | 249 | 21 | 15 | 46 | 19400 | 15800 | 2270 | 19
53QDMT24-718 | 0.24 | Medium | 249 | 21 | 15 | 52 | 19790 | 15465 | 2320 | 19
53QDMT24-718 | 0.24 | Medium | 249 | 24 | 17 | 35 | 21420 | 16695 | 2265 | 19
53QDMT24-718 | 0.24 | Medium | 249 | 24 | 17 | 43 | 20065 | 16165 | 2375 | 19
53QDMT24-718 | 0.24 | Medium | 249 | 24 | 17 | 46 | 19637 | 15995 | 2420 | 19
53QDMT24-718 | 0.24 | Medium | 249 | 24 | 17 | 52 | 18770 | 15655 | 2510 | 19
53QDMT24-718 | 0.24 | Medium | 249 | 27 | 19 | 35 | 22285 | 16660 | 2310 | 19
53QDMT24-718 | 0.24 | Medium | 249 | 27 | 19 | 43 | 20725 | 16285 | 2430 | 19
53QDMT24-718 | 0.24 | Medium | 249 | 27 | 19 | 46 | 19940 | 15965 | 2475 | 19
53QDMT24-718 | 0.24 | Medium | 249 | 27 | 19 | 52 | 18770 | 15325 | 2565 | 19
53QDMT24-718 | 0.24 | Medium | 249 | 32 | 23 | 35 | 23175 | 19535 | 2425 | 19
53QDMT24-718 | 0.24 | Medium | 249 | 32 | 23 | 43 | 21420 | 19085 | 2515 | 19
53QDMT24-718 | 0.24 | Medium | 249 | 32 | 23 | 46 | 20730 | 18875 | 2540 | 19
53QDMT24-718 | 0.24 | Medium | 249 | 32 | 23 | 52 | 19770 | 18465 | 2590 | 19
53QDMT24-718 | 0.24 | Low | 141 | 21 | 15 | 35 | 19975 | 14680 | 2080 | 19
53QDMT24-718 | 0.24 | Low | 141 | 21 | 15 | 43 | 19010 | 14760 | 2145 | 19
53QDMT24-718 | 0.24 | Low | 141 | 21 | 15 | 46 | 18590 | 14600 | 2160 | 19
53QDMT24-718 | 0.24 | Low | 141 | 21 | 15 | 52 | 18970 | 14295 | 2195 | 19
53QDMT24-718 | 0.24 | Low | 141 | 24 | 17 | 35 | 20525 | 15430 | 2175 | 19
53QDMT24-718 | 0.24 | Low | 141 | 24 | 17 | 43 | 19230 | 14940 | 2295 | 19
53QDMT24-718 | 0.24 | Low | 141 | 24 | 17 | 46 | 18815 | 14785 | 2335 | 19
53QDMT24-718 | 0.24 | Low | 141 | 24 | 17 | 52 | 17990 | 14465 | 2415 | 19
53QDMT24-718 | 0.24 | Low | 141 | 27 | 19 | 35 | 21355 | 15390 | 2215 | 19
53QDMT24-718 | 0.24 | Low | 141 | 27 | 19 | 43 | 19860 | 15045 | 2335 | 19
53QDMT24-718 | 0.24 | Low | 141 | 27 | 19 | 46 | 19230 | 14755 | 2380 | 19
53QDMT24-718 | 0.24 | Low | 141 | 27 | 19 | 52 | 17990 | 14160 | 2470 | 19
53QDMT24-718 | 0.24 | Low | 141 | 21 | 23 | 35 | 22202 | 18045 | 2325 | 19
53QDMT24-718 | 0.24 | Low | 141 | 21 | 23 | 43 | 20525 | 17630 | 2420 | 19
53QDMT24-718 | 0.24 | Low | 141 | 21 | 23 | 46 | 19865 | 17440 | 2445 | 19
53QDMT24-718 | 0.24 | Low | 141 | 21 | 23 | 52 | 18540 | 17060 | 2495 | 19
53QDMT30-718 | 0 | High | 910 | 21 | 15 | 35 | 27900 | 22335 | 3305 | 20
53QDMT30-718 | 0 | High | 910 | 21 | 15 | 43 | 26700 | 22420 | 3415 | 20
53QDMT30-718 | 0 | High | 910 | 21 | 15 | 46 | 26100 | 22185 | 3450 | 20
53QDMT30-718 | 0 | High | 910 | 21 | 15 | 52 | 24900 | 21715 | 3520 | 20
53QDMT30-718 | 0 | High | 910 | 24 | 17 | 35 | 28800 | 23335 | 3450 | 20
53QDMT30-718 | 0 | High | 910 | 24 | 17 | 43 | 27000 | 22690 | 3625 | 20
53QDMT30-718 | 0 | High | 910 | 24 | 17 | 46 | 26400 | 22445 | 3690 | 20
53QDMT30-718 | 0 | High | 910 | 24 | 17 | 52 | 25200 | 21955 | 3820 | 20
53QDMT30-718 | 0 | High | 910 | 27 | 19 | 35 | 30000 | 23400 | 3515 | 20
53QDMT30-718 | 0 | High | 910 | 27 | 19 | 43 | 27900 | 22890 | 3690 | 20
53QDMT30-718 | 0 | High | 910 | 27 | 19 | 46 | 27000 | 22425 | 3760 | 20
53QDMT30-718 | 0 | High | 910 | 27 | 19 | 52 | 25215 | 21495 | 3900 | 20
53QDMT30-718 | 0 | High | 910 | 32 | 23 | 35 | 31200 | 27470 | 3695 | 20
53QDMT30-718 | 0 | High | 910 | 32 | 23 | 43 | 28800 | 26775 | 3835 | 20
53QDMT30-718 | 0 | High | 910 | 32 | 23 | 46 | 27900 | 26505 | 3875 | 20
53QDMT30-718 | 0 | High | 910 | 32 | 23 | 52 | 26100 | 25965 | 3955 | 20
53QDMT30-718 | 0 | Medium | 730 | 21 | 15 | 35 | 26785 | 20550 | 3205 | 20
53QDMT30-718 | 0 | Medium | 730 | 21 | 15 | 43 | 25635 | 20630 | 3305 | 20
53QDMT30-718 | 0 | Medium | 730 | 21 | 15 | 46 | 25060 | 20410 | 3340 | 20
53QDMT30-718 | 0 | Medium | 730 | 21 | 15 | 52 | 23905 | 19980 | 3410 | 20
53QDMT30-718 | 0 | Medium | 730 | 24 | 17 | 35 | 27650 | 21470 | 3345 | 20
53QDMT30-718 | 0 | Medium | 730 | 24 | 17 | 43 | 25920 | 20875 | 3515 | 20
53QDMT30-718 | 0 | Medium | 730 | 24 | 17 | 46 | 25345 | 20650 | 3580 | 20
53QDMT30-718 | 0 | Medium | 730 | 24 | 17 | 52 | 24195 | 20200 | 3710 | 20
53QDMT30-718 | 0 | Medium | 730 | 27 | 19 | 35 | 28800 | 21530 | 3410 | 20
53QDMT30-718 | 0 | Medium | 730 | 27 | 19 | 43 | 26785 | 21060 | 3570 | 20
53QDMT30-718 | 0 | Medium | 730 | 27 | 19 | 46 | 25920 | 20635 | 3615 | 20
53QDMT30-718 | 0 | Medium | 730 | 27 | 19 | 52 | 24210 | 19775 | 3705 | 20
53QDMT30-718 | 0 | Medium | 730 | 32 | 23 | 35 | 29955 | 25275 | 3585 | 20
53QDMT30-718 | 0 | Medium | 730 | 32 | 23 | 43 | 27650 | 24635 | 3715 | 20
53QDMT30-718 | 0 | Medium | 730 | 32 | 23 | 46 | 26785 | 24385 | 3755 | 20
53QDMT30-718 | 0 | Medium | 730 | 32 | 23 | 52 | 25060 | 23890 | 3835 | 20
53QDMT30-718 | 0 | Low | 645 | 21 | 15 | 35 | 25670 | 18985 | 3075 | 20
53QDMT30-718 | 0 | Low | 645 | 21 | 15 | 43 | 24565 | 19060 | 3175 | 20
53QDMT30-718 | 0 | Low | 645 | 21 | 15 | 46 | 24015 | 18860 | 3210 | 20
53QDMT30-718 | 0 | Low | 645 | 21 | 15 | 52 | 22910 | 18460 | 3280 | 20
53QDMT30-718 | 0 | Low | 645 | 24 | 17 | 35 | 26500 | 19835 | 3210 | 20
53QDMT30-718 | 0 | Low | 645 | 24 | 17 | 43 | 24840 | 19290 | 3370 | 20
53QDMT30-718 | 0 | Low | 645 | 24 | 17 | 46 | 24290 | 19080 | 3430 | 20
53QDMT30-718 | 0 | Low | 645 | 24 | 17 | 52 | 23185 | 18665 | 3550 | 20
53QDMT30-718 | 0 | Low | 645 | 27 | 19 | 35 | 27600 | 19890 | 3270 | 20
53QDMT30-718 | 0 | Low | 645 | 27 | 19 | 43 | 25670 | 19460 | 3435 | 20
53QDMT30-718 | 0 | Low | 645 | 27 | 19 | 46 | 24840 | 19065 | 3500 | 20
53QDMT30-718 | 0 | Low | 645 | 27 | 19 | 52 | 23200 | 18275 | 3630 | 20
53QDMT30-718 | 0 | Low | 645 | 21 | 23 | 35 | 28705 | 23350 | 3435 | 20
53QDMT30-718 | 0 | Low | 645 | 21 | 23 | 43 | 26500 | 22760 | 3605 | 20
53QDMT30-718 | 0 | Low | 645 | 21 | 23 | 46 | 25670 | 22530 | 3640 | 20
53QDMT30-718 | 0 | Low | 645 | 21 | 23 | 52 | 24015 | 22070 | 3710 | 20
53QDMT30-718 | 0.08 | High | 850 | 21 | 15 | 35 | 27215 | 21785 | 3290 | 20
53QDMT30-718 | 0.08 | High | 850 | 21 | 15 | 43 | 26045 | 21870 | 3400 | 20
53QDMT30-718 | 0.08 | High | 850 | 21 | 15 | 46 | 25460 | 21645 | 3435 | 20
53QDMT30-718 | 0.08 | High | 850 | 21 | 15 | 52 | 24155 | 21190 | 3505 | 20
53QDMT30-718 | 0.08 | High | 850 | 24 | 17 | 35 | 28090 | 22765 | 3430 | 20
53QDMT30-718 | 0.08 | High | 850 | 24 | 17 | 43 | 26335 | 22135 | 3605 | 20
53QDMT30-718 | 0.08 | High | 850 | 24 | 17 | 46 | 25755 | 21860 | 3670 | 20
53QDMT30-718 | 0.08 | High | 850 | 24 | 17 | 52 | 24585 | 21310 | 3800 | 20
53QDMT30-718 | 0.08 | High | 850 | 27 | 19 | 35 | 29260 | 22825 | 3495 | 20
53QDMT30-718 | 0.08 | High | 850 | 27 | 19 | 43 | 27220 | 22330 | 3670 | 20
53QDMT30-718 | 0.08 | High | 850 | 27 | 19 | 46 | 26345 | 21875 | 3740 | 20
53QDMT30-718 | 0.08 | High | 850 | 27 | 19 | 52 | 24595 | 20970 | 3875 | 20
53QDMT30-718 | 0.08 | High | 850 | 32 | 23 | 35 | 30435 | 26795 | 3675 | 20
53QDMT30-718 | 0.08 | High | 850 | 32 | 23 | 43 | 28095 | 26120 | 3815 | 20
53QDMT30-718 | 0.08 | High | 850 | 32 | 23 | 46 | 27215 | 25860 | 3855 | 20
53QDMT30-718 | 0.08 | High | 850 | 32 | 23 | 52 | 25460 | 25335 | 3935 | 20
53QDMT30-718 | 0.08 | Medium | 657 | 21 | 15 | 35 | 26125 | 20045 | 3190 | 20
53QDMT30-718 | 0.08 | Medium | 657 | 21 | 15 | 43 | 25005 | 20125 | 3290 | 20
53QDMT30-718 | 0.08 | Medium | 657 | 21 | 15 | 46 | 24445 | 20410 | 3325 | 20
53QDMT30-718 | 0.08 | Medium | 657 | 21 | 15 | 52 | 23190 | 19495 | 3395 | 20
53QDMT30-718 | 0.08 | Medium | 657 | 24 | 17 | 35 | 26970 | 20945 | 3325 | 20
53QDMT30-718 | 0.08 | Medium | 657 | 24 | 17 | 43 | 25285 | 20365 | 3500 | 20
53QDMT30-718 | 0.08 | Medium | 657 | 24 | 17 | 46 | 24725 | 20110 | 3565 | 20
53QDMT30-718 | 0.08 | Medium | 657 | 24 | 17 | 52 | 23605 | 19605 | 3695 | 20
53QDMT30-718 | 0.08 | Medium | 657 | 27 | 19 | 35 | 28090 | 21000 | 3390 | 20
53QDMT30-718 | 0.08 | Medium | 657 | 27 | 19 | 43 | 26135 | 20545 | 3555 | 20
53QDMT30-718 | 0.08 | Medium | 657 | 27 | 19 | 46 | 25290 | 20130 | 3610 | 20
53QDMT30-718 | 0.08 | Medium | 657 | 27 | 19 | 52 | 23615 | 19295 | 3710 | 20
53QDMT30-718 | 0.08 | Medium | 657 | 32 | 23 | 35 | 29220 | 24655 | 3565 | 20
53QDMT30-718 | 0.08 | Medium | 657 | 32 | 23 | 43 | 26970 | 24030 | 3695 | 20
53QDMT30-718 | 0.08 | Medium | 657 | 32 | 23 | 46 | 26130 | 23790 | 3735 | 20
53QDMT30-718 | 0.08 | Medium | 657 | 32 | 23 | 52 | 24445 | 23310 | 3815 | 20
53QDMT30-718 | 0.08 | Low | 562 | 21 | 15 | 35 | 25040 | 18520 | 3060 | 20
53QDMT30-718 | 0.08 | Low | 562 | 21 | 15 | 43 | 18640 | 18595 | 3155 | 20
53QDMT30-718 | 0.08 | Low | 562 | 21 | 15 | 46 | 23425 | 18400 | 3190 | 20
53QDMT30-718 | 0.08 | Low | 562 | 21 | 15 | 52 | 22225 | 18015 | 3255 | 20
53QDMT30-718 | 0.08 | Low | 562 | 24 | 17 | 35 | 25850 | 19350 | 3190 | 20
53QDMT30-718 | 0.08 | Low | 562 | 24 | 17 | 43 | 24230 | 18820 | 3355 | 20
53QDMT30-718 | 0.08 | Low | 562 | 24 | 17 | 46 | 23695 | 18215 | 3415 | 20
53QDMT30-718 | 0.08 | Low | 562 | 24 | 17 | 52 | 22620 | 18115 | 3535 | 20
53QDMT30-718 | 0.08 | Low | 562 | 27 | 19 | 35 | 26920 | 19405 | 3255 | 20
53QDMT30-718 | 0.08 | Low | 562 | 27 | 19 | 43 | 25045 | 18980 | 3420 | 20
53QDMT30-718 | 0.08 | Low | 562 | 27 | 19 | 46 | 24240 | 18230 | 3480 | 20
53QDMT30-718 | 0.08 | Low | 562 | 27 | 19 | 52 | 22630 | 17830 | 3605 | 20
53QDMT30-718 | 0.08 | Low | 562 | 21 | 23 | 35 | 28000 | 22780 | 3415 | 20
53QDMT30-718 | 0.08 | Low | 562 | 21 | 23 | 43 | 25850 | 22205 | 3570 | 20
53QDMT30-718 | 0.08 | Low | 562 | 21 | 23 | 46 | 25040 | 21550 | 3605 | 20
53QDMT30-718 | 0.08 | Low | 562 | 21 | 23 | 52 | 23425 | 21535 | 3675 | 20
53QDMT30-718 | 0.12 | High | 820 | 21 | 15 | 35 | 26870 | 21510 | 3280 | 20
53QDMT30-718 | 0.12 | High | 820 | 21 | 15 | 43 | 25715 | 21595 | 3390 | 20
53QDMT30-718 | 0.12 | High | 820 | 21 | 15 | 46 | 25140 | 21370 | 3425 | 20
53QDMT30-718 | 0.12 | High | 820 | 21 | 15 | 52 | 23990 | 20920 | 3495 | 20
53QDMT30-718 | 0.12 | High | 820 | 24 | 17 | 35 | 27735 | 22475 | 3420 | 20
53QDMT30-718 | 0.12 | High | 820 | 24 | 17 | 43 | 26000 | 21850 | 3595 | 20
53QDMT30-718 | 0.12 | High | 820 | 24 | 17 | 46 | 25425 | 21465 | 3660 | 20
53QDMT30-718 | 0.12 | High | 820 | 24 | 17 | 52 | 24275 | 20695 | 3790 | 20
53QDMT30-718 | 0.12 | High | 820 | 27 | 19 | 35 | 28890 | 22540 | 3485 | 20
53QDMT30-718 | 0.12 | High | 820 | 27 | 19 | 43 | 26885 | 22045 | 3660 | 20
53QDMT30-718 | 0.12 | High | 820 | 27 | 19 | 46 | 26020 | 21600 | 3725 | 20
53QDMT30-718 | 0.12 | High | 820 | 27 | 19 | 52 | 24290 | 20710 | 3855 | 20
53QDMT30-718 | 0.12 | High | 820 | 32 | 23 | 35 | 30050 | 26460 | 3665 | 20
53QDMT30-718 | 0.12 | High | 820 | 32 | 23 | 43 | 27740 | 25790 | 3805 | 20
53QDMT30-718 | 0.12 | High | 820 | 32 | 23 | 46 | 26875 | 25535 | 3845 | 20
53QDMT30-718 | 0.12 | High | 820 | 32 | 23 | 52 | 25145 | 25025 | 3925 | 20
53QDMT30-718 | 0.12 | Medium | 624 | 21 | 15 | 35 | 25795 | 19790 | 3180 | 20
53QDMT30-718 | 0.12 | Medium | 624 | 21 | 15 | 43 | 24690 | 19870 | 3280 | 20
53QDMT30-718 | 0.12 | Medium | 624 | 21 | 15 | 46 | 24135 | 19660 | 3315 | 20
53QDMT30-718 | 0.12 | Medium | 624 | 21 | 15 | 52 | 23030 | 19250 | 3385 | 20
53QDMT30-718 | 0.12 | Medium | 624 | 24 | 17 | 35 | 26630 | 20680 | 3315 | 20
53QDMT30-718 | 0.12 | Medium | 624 | 24 | 17 | 43 | 24960 | 20105 | 3490 | 20
53QDMT30-718 | 0.12 | Medium | 624 | 24 | 17 | 46 | 24410 | 19750 | 3555 | 20
53QDMT30-718 | 0.12 | Medium | 624 | 24 | 17 | 52 | 23305 | 19040 | 3685 | 20
53QDMT30-718 | 0.12 | Medium | 624 | 27 | 19 | 35 | 27735 | 20735 | 3380 | 20
53QDMT30-718 | 0.12 | Medium | 624 | 27 | 19 | 43 | 25810 | 20285 | 3545 | 20
53QDMT30-718 | 0.12 | Medium | 624 | 27 | 19 | 46 | 24980 | 19875 | 3610 | 20
53QDMT30-718 | 0.12 | Medium | 624 | 27 | 19 | 52 | 23320 | 19055 | 3740 | 20
53QDMT30-718 | 0.12 | Medium | 624 | 32 | 23 | 35 | 28850 | 24345 | 3555 | 20
53QDMT30-718 | 0.12 | Medium | 624 | 32 | 23 | 43 | 26630 | 23730 | 3685 | 20
53QDMT30-718 | 0.12 | Medium | 624 | 32 | 23 | 46 | 25800 | 23495 | 3725 | 20
53QDMT30-718 | 0.12 | Medium | 624 | 32 | 23 | 52 | 24140 | 23025 | 3805 | 20
53QDMT30-718 | 0.12 | Low | 525 | 21 | 15 | 35 | 24720 | 18285 | 3055 | 20
53QDMT30-718 | 0.12 | Low | 525 | 21 | 15 | 43 | 2360 | 18360 | 3135 | 20
53QDMT30-718 | 0.12 | Low | 525 | 21 | 15 | 46 | 23130 | 18165 | 3165 | 20
53QDMT30-718 | 0.12 | Low | 525 | 21 | 15 | 52 | 22075 | 17785 | 3225 | 20
53QDMT30-718 | 0.12 | Low | 525 | 24 | 17 | 35 | 25520 | 19105 | 3180 | 20
53QDMT30-718 | 0.12 | Low | 525 | 24 | 17 | 43 | 23920 | 18575 | 3345 | 20
53QDMT30-718 | 0.12 | Low | 525 | 24 | 17 | 46 | 23395 | 16790 | 3405 | 20
53QDMT30-718 | 0.12 | Low | 525 | 24 | 17 | 52 | 22335 | 17595 | 3525 | 20
53QDMT30-718 | 0.12 | Low | 525 | 27 | 19 | 35 | 26580 | 19160 | 3245 | 20
53QDMT30-718 | 0.12 | Low | 525 | 27 | 19 | 43 | 24735 | 18740 | 3410 | 20
53QDMT30-718 | 0.12 | Low | 525 | 27 | 19 | 46 | 23940 | 16895 | 3470 | 20
53QDMT30-718 | 0.12 | Low | 525 | 27 | 19 | 52 | 22350 | 17605 | 3590 | 20
53QDMT30-718 | 0.12 | Low | 525 | 21 | 23 | 35 | 27650 | 22495 | 3405 | 20
53QDMT30-718 | 0.12 | Low | 525 | 21 | 23 | 43 | 25525 | 21925 | 3540 | 20
53QDMT30-718 | 0.12 | Low | 525 | 21 | 23 | 46 | 24725 | 19975 | 3575 | 20
53QDMT30-718 | 0.12 | Low | 525 | 21 | 23 | 52 | 23135 | 21275 | 3645 | 20
53QDMT30-718 | 0.16 | High | 790 | 21 | 15 | 35 | 26525 | 21235 | 3270 | 20
53QDMT30-718 | 0.16 | High | 790 | 21 | 15 | 43 | 25385 | 21320 | 3380 | 20
53QDMT30-718 | 0.16 | High | 790 | 21 | 15 | 46 | 24820 | 21100 | 3415 | 20
53QDMT30-718 | 0.16 | High | 790 | 21 | 15 | 52 | 23405 | 20660 | 3485 | 20
53QDMT30-718 | 0.16 | High | 790 | 24 | 17 | 35 | 27380 | 22190 | 3410 | 20
53QDMT30-718 | 0.16 | High | 790 | 24 | 17 | 43 | 25670 | 21575 | 3585 | 20
53QDMT30-718 | 0.16 | High | 790 | 24 | 17 | 46 | 25105 | 21270 | 3650 | 20
53QDMT30-718 | 0.16 | High | 790 | 24 | 17 | 52 | 23970 | 20660 | 3780 | 20
53QDMT30-718 | 0.16 | High | 790 | 27 | 19 | 35 | 28520 | 22250 | 3475 | 20
53QDMT30-718 | 0.16 | High | 790 | 27 | 19 | 43 | 26540 | 21765 | 3650 | 20
53QDMT30-718 | 0.16 | High | 790 | 27 | 19 | 46 | 25685 | 21325 | 3715 | 20
53QDMT30-718 | 0.16 | High | 790 | 27 | 19 | 52 | 23975 | 20445 | 3845 | 20
53QDMT30-718 | 0.16 | High | 790 | 32 | 23 | 35 | 29665 | 26120 | 3655 | 20
53QDMT30-718 | 0.16 | High | 790 | 32 | 23 | 43 | 27385 | 25460 | 3795 | 20
53QDMT30-718 | 0.16 | High | 790 | 32 | 23 | 46 | 26530 | 25210 | 3835 | 20
53QDMT30-718 | 0.16 | High | 790 | 32 | 23 | 52 | 24820 | 24705 | 3915 | 20
53QDMT30-718 | 0.16 | Medium | 591 | 21 | 15 | 35 | 25465 | 19540 | 3170 | 20
53QDMT30-718 | 0.16 | Medium | 591 | 21 | 15 | 43 | 24375 | 19615 | 3270 | 20
53QDMT30-718 | 0.16 | Medium | 591 | 21 | 15 | 46 | 23825 | 20410 | 3305 | 20
53QDMT30-718 | 0.16 | Medium | 591 | 21 | 15 | 52 | 22470 | 19010 | 3375 | 20
53QDMT30-718 | 0.16 | Medium | 591 | 24 | 17 | 35 | 26290 | 20415 | 3305 | 20
53QDMT30-718 | 0.16 | Medium | 591 | 24 | 17 | 43 | 24645 | 19850 | 3480 | 20
53QDMT30-718 | 0.16 | Medium | 591 | 24 | 17 | 46 | 24100 | 19570 | 3545 | 20
53QDMT30-718 | 0.16 | Medium | 591 | 24 | 17 | 52 | 23010 | 19005 | 3675 | 20
53QDMT30-718 | 0.16 | Medium | 591 | 27 | 19 | 35 | 27380 | 20470 | 3370 | 20
53QDMT30-718 | 0.16 | Medium | 591 | 27 | 19 | 43 | 25480 | 20025 | 3535 | 20
53QDMT30-718 | 0.16 | Medium | 591 | 27 | 19 | 46 | 24660 | 19620 | 3600 | 20
53QDMT30-718 | 0.16 | Medium | 591 | 27 | 19 | 52 | 23020 | 18810 | 3730 | 20
53QDMT30-718 | 0.16 | Medium | 591 | 32 | 23 | 35 | 28480 | 24035 | 3545 | 20
53QDMT30-718 | 0.16 | Medium | 591 | 32 | 23 | 43 | 26290 | 23425 | 3675 | 20
53QDMT30-718 | 0.16 | Medium | 591 | 32 | 23 | 46 | 25470 | 23195 | 3715 | 20
53QDMT30-718 | 0.16 | Medium | 591 | 32 | 23 | 52 | 23830 | 22730 | 3795 | 20
53QDMT30-718 | 0.16 | Low | 495 | 21 | 15 | 35 | 24405 | 18055 | 3045 | 20
53QDMT30-718 | 0.16 | Low | 495 | 21 | 15 | 43 | 12710 | 18125 | 3135 | 20
53QDMT30-718 | 0.16 | Low | 495 | 21 | 15 | 46 | 22835 | 17935 | 3165 | 20
53QDMT30-718 | 0.16 | Low | 495 | 21 | 15 | 52 | 21535 | 17565 | 3225 | 20
53QDMT30-718 | 0.16 | Low | 495 | 24 | 17 | 35 | 25195 | 18860 | 3170 | 20
53QDMT30-718 | 0.16 | Low | 495 | 24 | 17 | 43 | 23620 | 18340 | 3335 | 20
53QDMT30-718 | 0.16 | Low | 495 | 24 | 17 | 46 | 23100 | 17350 | 3395 | 20
53QDMT30-718 | 0.16 | Low | 495 | 24 | 17 | 52 | 22055 | 17565 | 3515 | 20
53QDMT30-718 | 0.16 | Low | 495 | 27 | 19 | 35 | 26240 | 18915 | 3235 | 20
53QDMT30-718 | 0.16 | Low | 495 | 27 | 19 | 43 | 24420 | 18500 | 3400 | 20
53QDMT30-718 | 0.16 | Low | 495 | 27 | 19 | 46 | 23635 | 17395 | 3460 | 20
53QDMT30-718 | 0.16 | Low | 495 | 27 | 19 | 52 | 22060 | 17380 | 3580 | 20
53QDMT30-718 | 0.16 | Low | 495 | 21 | 23 | 35 | 27295 | 22205 | 3395 | 20
53QDMT30-718 | 0.16 | Low | 495 | 21 | 23 | 43 | 25200 | 21645 | 3530 | 20
53QDMT30-718 | 0.16 | Low | 495 | 21 | 23 | 46 | 24410 | 20565 | 3565 | 20
53QDMT30-718 | 0.16 | Low | 495 | 21 | 23 | 52 | 22835 | 21000 | 3635 | 20
53QDMT30-718 | 0.2 | High | 760 | 21 | 15 | 35 | 26180 | 20960 | 3260 | 21
53QDMT30-718 | 0.2 | High | 760 | 21 | 15 | 43 | 25055 | 21040 | 3370 | 21
53QDMT30-718 | 0.2 | High | 760 | 21 | 15 | 46 | 24495 | 20825 | 3405 | 21
53QDMT30-718 | 0.2 | High | 760 | 21 | 15 | 52 | 22815 | 20395 | 3475 | 21
53QDMT30-718 | 0.2 | High | 760 | 24 | 17 | 35 | 27025 | 21900 | 3400 | 21
53QDMT30-718 | 0.2 | High | 760 | 24 | 17 | 43 | 25340 | 21295 | 3575 | 21
53QDMT30-718 | 0.2 | High | 760 | 24 | 17 | 46 | 24780 | 21070 | 3640 | 21
53QDMT30-718 | 0.2 | High | 760 | 24 | 17 | 52 | 23660 | 20620 | 3770 | 21
53QDMT30-718 | 0.2 | High | 760 | 27 | 19 | 35 | 28150 | 21960 | 3465 | 21
53QDMT30-718 | 0.2 | High | 760 | 27 | 19 | 43 | 26195 | 21480 | 3640 | 21
53QDMT30-718 | 0.2 | High | 760 | 27 | 19 | 46 | 25350 | 21045 | 3705 | 21
53QDMT30-718 | 0.2 | High | 760 | 27 | 19 | 52 | 23660 | 20175 | 3835 | 21
53QDMT30-718 | 0.2 | High | 760 | 32 | 23 | 35 | 29280 | 25780 | 3645 | 21
53QDMT30-718 | 0.2 | High | 760 | 32 | 23 | 43 | 27030 | 25130 | 3785 | 21
53QDMT30-718 | 0.2 | High | 760 | 32 | 23 | 46 | 26185 | 24880 | 3825 | 21
53QDMT30-718 | 0.2 | High | 760 | 32 | 23 | 52 | 24495 | 24380 | 3905 | 21
53QDMT30-718 | 0.2 | Medium | 550 | 21 | 15 | 35 | 25135 | 19285 | 3160 | 21
53QDMT30-718 | 0.2 | Medium | 550 | 21 | 15 | 43 | 24055 | 19360 | 3260 | 21
53QDMT30-718 | 0.2 | Medium | 550 | 21 | 15 | 46 | 23515 | 21160 | 3295 | 21
53QDMT30-718 | 0.2 | Medium | 550 | 21 | 15 | 52 | 21905 | 18765 | 3365 | 21
53QDMT30-718 | 0.2 | Medium | 550 | 24 | 17 | 35 | 25945 | 20150 | 3295 | 21
53QDMT30-718 | 0.2 | Medium | 550 | 24 | 17 | 43 | 24330 | 19595 | 3470 | 21
53QDMT30-718 | 0.2 | Medium | 550 | 24 | 17 | 46 | 23790 | 19385 | 3535 | 21
53QDMT30-718 | 0.2 | Medium | 550 | 24 | 17 | 52 | 22715 | 18970 | 3665 | 21
53QDMT30-718 | 0.2 | Medium | 550 | 27 | 19 | 35 | 27025 | 20205 | 3360 | 21
53QDMT30-718 | 0.2 | Medium | 550 | 27 | 19 | 43 | 25150 | 19765 | 3525 | 21
53QDMT30-718 | 0.2 | Medium | 550 | 27 | 19 | 46 | 24340 | 19365 | 3590 | 21
53QDMT30-718 | 0.2 | Medium | 550 | 27 | 19 | 52 | 22715 | 18565 | 3720 | 21
53QDMT30-718 | 0.2 | Medium | 550 | 32 | 23 | 35 | 28110 | 23720 | 3535 | 21
53QDMT30-718 | 0.2 | Medium | 550 | 32 | 23 | 43 | 25950 | 23120 | 3665 | 21
53QDMT30-718 | 0.2 | Medium | 550 | 32 | 23 | 46 | 25140 | 22890 | 3705 | 21
53QDMT30-718 | 0.2 | Medium | 550 | 32 | 23 | 52 | 23515 | 22430 | 3785 | 21
53QDMT30-718 | 0.2 | Low | 453 | 21 | 15 | 35 | 24090 | 17820 | 3035 | 21
53QDMT30-718 | 0.2 | Low | 453 | 21 | 15 | 43 | 23055 | 17885 | 3135 | 21
53QDMT30-718 | 0.2 | Low | 453 | 21 | 15 | 46 | 22535 | 17705 | 3165 | 21
53QDMT30-718 | 0.2 | Low | 453 | 21 | 15 | 52 | 20990 | 17340 | 3225 | 21
53QDMT30-718 | 0.2 | Low | 453 | 24 | 17 | 35 | 24865 | 18615 | 3160 | 21
53QDMT30-718 | 0.2 | Low | 453 | 24 | 17 | 43 | 23315 | 18100 | 3325 | 21
53QDMT30-718 | 0.2 | Low | 453 | 24 | 17 | 46 | 22800 | 17910 | 3385 | 21
53QDMT30-718 | 0.2 | Low | 453 | 24 | 17 | 52 | 21770 | 17530 | 3505 | 21
53QDMT30-718 | 0.2 | Low | 453 | 27 | 19 | 35 | 25900 | 18670 | 3225 | 21
53QDMT30-718 | 0.2 | Low | 453 | 27 | 19 | 43 | 24100 | 18260 | 3390 | 21
53QDMT30-718 | 0.2 | Low | 453 | 27 | 19 | 46 | 23325 | 17890 | 3450 | 21
53QDMT30-718 | 0.2 | Low | 453 | 27 | 19 | 52 | 21770 | 17150 | 3570 | 21
53QDMT30-718 | 0.2 | Low | 453 | 21 | 23 | 35 | 26940 | 21915 | 3385 | 21
53QDMT30-718 | 0.2 | Low | 453 | 21 | 23 | 43 | 24870 | 21365 | 3520 | 21
53QDMT30-718 | 0.2 | Low | 453 | 21 | 23 | 46 | 24090 | 21150 | 3555 | 21
53QDMT30-718 | 0.2 | Low | 453 | 21 | 23 | 52 | 22535 | 20725 | 3625 | 21
53QDMT30-718 | 0.24 | High | 730 | 21 | 15 | 35 | 25835 | 20690 | 3250 | 21
53QDMT30-718 | 0.24 | High | 730 | 21 | 15 | 43 | 24725 | 20765 | 3360 | 21
53QDMT30-718 | 0.24 | High | 730 | 21 | 15 | 46 | 24175 | 20550 | 3395 | 21
53QDMT30-718 | 0.24 | High | 730 | 21 | 15 | 52 | 23075 | 21125 | 3465 | 21
53QDMT30-718 | 0.24 | High | 730 | 24 | 17 | 35 | 26670 | 21615 | 3390 | 21
53QDMT30-718 | 0.24 | High | 730 | 24 | 17 | 43 | 25020 | 21030 | 3565 | 21
53QDMT30-718 | 0.24 | High | 730 | 24 | 17 | 46 | 24470 | 20805 | 3630 | 21
53QDMT30-718 | 0.24 | High | 730 | 24 | 17 | 52 | 23370 | 20365 | 3760 | 21
53QDMT30-718 | 0.24 | High | 730 | 27 | 19 | 35 | 27780 | 21675 | 3455 | 21
53QDMT30-718 | 0.24 | High | 730 | 27 | 19 | 43 | 25850 | 21210 | 3630 | 21
53QDMT30-718 | 0.24 | High | 730 | 27 | 19 | 46 | 25015 | 20780 | 3700 | 21
53QDMT30-718 | 0.24 | High | 730 | 27 | 19 | 52 | 23345 | 19905 | 3840 | 21
53QDMT30-718 | 0.24 | High | 730 | 32 | 23 | 35 | 28895 | 25445 | 3635 | 21
53QDMT30-718 | 0.24 | High | 730 | 32 | 23 | 43 | 26680 | 24805 | 3775 | 21
53QDMT30-718 | 0.24 | High | 730 | 32 | 23 | 46 | 25845 | 24555 | 3815 | 21
53QDMT30-718 | 0.24 | High | 730 | 32 | 23 | 52 | 24175 | 24050 | 3895 | 21
53QDMT30-718 | 0.24 | Medium | 509 | 21 | 15 | 35 | 24805 | 19035 | 3155 | 21
53QDMT30-718 | 0.24 | Medium | 509 | 21 | 15 | 43 | 23740 | 19105 | 3260 | 21
53QDMT30-718 | 0.24 | Medium | 509 | 21 | 15 | 46 | 23210 | 18910 | 3295 | 21
53QDMT30-718 | 0.24 | Medium | 509 | 21 | 15 | 52 | 22155 | 18515 | 3360 | 21
53QDMT30-718 | 0.24 | Medium | 509 | 24 | 17 | 35 | 25605 | 19890 | 3290 | 21
53QDMT30-718 | 0.24 | Medium | 509 | 24 | 17 | 43 | 24020 | 19350 | 3460 | 21
53QDMT30-718 | 0.24 | Medium | 509 | 24 | 17 | 46 | 23495 | 19145 | 3520 | 21
53QDMT30-718 | 0.24 | Medium | 509 | 24 | 17 | 52 | 22435 | 18740 | 3650 | 21
53QDMT30-718 | 0.24 | Medium | 509 | 27 | 19 | 35 | 26670 | 19940 | 3355 | 21
53QDMT30-718 | 0.24 | Medium | 509 | 27 | 19 | 43 | 24820 | 19515 | 3520 | 21
53QDMT30-718 | 0.24 | Medium | 509 | 27 | 19 | 46 | 24015 | 19120 | 3590 | 21
53QDMT30-718 | 0.24 | Medium | 509 | 27 | 19 | 52 | 22415 | 18315 | 3725 | 21
53QDMT30-718 | 0.24 | Medium | 509 | 32 | 23 | 35 | 27740 | 23410 | 3525 | 21
53QDMT30-718 | 0.24 | Medium | 509 | 32 | 23 | 43 | 25615 | 22825 | 3660 | 21
53QDMT30-718 | 0.24 | Medium | 509 | 32 | 23 | 46 | 24815 | 22595 | 3700 | 21
53QDMT30-718 | 0.24 | Medium | 509 | 32 | 23 | 52 | 23210 | 22130 | 3780 | 21
53QDMT30-718 | 0.24 | Low | 411 | 21 | 15 | 35 | 23775 | 17590 | 3025 | 21
53QDMT30-718 | 0.24 | Low | 411 | 21 | 15 | 43 | 22750 | 17650 | 3125 | 21
53QDMT30-718 | 0.24 | Low | 411 | 21 | 15 | 46 | 22245 | 17470 | 3160 | 21
53QDMT30-718 | 0.24 | Low | 411 | 21 | 15 | 52 | 21230 | 17110 | 3225 | 21
53QDMT30-718 | 0.24 | Low | 411 | 24 | 17 | 35 | 24540 | 18375 | 3155 | 21
53QDMT30-718 | 0.24 | Low | 411 | 24 | 17 | 43 | 23020 | 17875 | 3315 | 21
53QDMT30-718 | 0.24 | Low | 411 | 24 | 17 | 46 | 22515 | 17685 | 3375 | 21
53QDMT30-718 | 0.24 | Low | 411 | 24 | 17 | 52 | 21500 | 17310 | 3500 | 21
53QDMT30-718 | 0.24 | Low | 411 | 27 | 19 | 35 | 25560 | 18425 | 3215 | 21
53QDMT30-718 | 0.24 | Low | 411 | 27 | 19 | 43 | 23785 | 18030 | 3375 | 21
53QDMT30-718 | 0.24 | Low | 411 | 27 | 19 | 46 | 23015 | 17665 | 3440 | 21
53QDMT30-718 | 0.24 | Low | 411 | 27 | 19 | 52 | 21505 | 16920 | 3570 | 21
53QDMT30-718 | 0.24 | Low | 411 | 21 | 23 | 35 | 26585 | 21630 | 3380 | 21
53QDMT30-718 | 0.24 | Low | 411 | 21 | 23 | 43 | 24550 | 21085 | 3510 | 21
53QDMT30-718 | 0.24 | Low | 411 | 21 | 23 | 46 | 23780 | 20875 | 3550 | 21
53QDMT30-718 | 0.24 | Low | 411 | 21 | 23 | 52 | 22245 | 20445 | 3625 | 21
53QDMT30-718 | 0.28 | High | 700 | 21 | 15 | 35 | 25490 | 20415 | 3240 | 21
53QDMT30-718 | 0.28 | High | 700 | 21 | 15 | 43 | 24395 | 20490 | 3350 | 21
53QDMT30-718 | 0.28 | High | 700 | 21 | 15 | 46 | 23855 | 20280 | 3385 | 21
53QDMT30-718 | 0.28 | High | 700 | 21 | 15 | 52 | 22775 | 19865 | 3455 | 21
53QDMT30-718 | 0.28 | High | 700 | 24 | 17 | 35 | 26315 | 21330 | 3380 | 21
53QDMT30-718 | 0.28 | High | 700 | 24 | 17 | 43 | 24685 | 20750 | 3555 | 21
53QDMT30-718 | 0.28 | High | 700 | 24 | 17 | 46 | 24145 | 20530 | 3620 | 21
53QDMT30-718 | 0.28 | High | 700 | 24 | 17 | 52 | 23065 | 20100 | 3750 | 21
53QDMT30-718 | 0.28 | High | 700 | 27 | 19 | 35 | 27410 | 21385 | 3445 | 21
53QDMT30-718 | 0.28 | High | 700 | 27 | 19 | 43 | 25505 | 20930 | 3620 | 21
53QDMT30-718 | 0.28 | High | 700 | 27 | 19 | 46 | 24680 | 20505 | 3690 | 21
53QDMT30-718 | 0.28 | High | 700 | 27 | 19 | 52 | 23030 | 19640 | 3830 | 21
53QDMT30-718 | 0.28 | High | 700 | 32 | 23 | 35 | 28510 | 25105 | 3625 | 21
53QDMT30-718 | 0.28 | High | 700 | 32 | 23 | 43 | 26320 | 24470 | 3765 | 21
53QDMT30-718 | 0.28 | High | 700 | 32 | 23 | 46 | 25495 | 24225 | 3805 | 21
53QDMT30-718 | 0.28 | High | 700 | 32 | 23 | 52 | 23845 | 23820 | 3885 | 21
53QDMT30-718 | 0.28 | Medium | 468 | 21 | 15 | 35 | 24470 | 18785 | 3145 | 21
53QDMT30-718 | 0.28 | Medium | 468 | 21 | 15 | 43 | 23420 | 18855 | 3250 | 21
53QDMT30-718 | 0.28 | Medium | 468 | 21 | 15 | 46 | 22905 | 18660 | 3285 | 21
53QDMT30-718 | 0.28 | Medium | 468 | 21 | 15 | 52 | 21865 | 18280 | 3350 | 21
53QDMT30-718 | 0.28 | Medium | 468 | 24 | 17 | 35 | 25265 | 19630 | 3280 | 21
53QDMT30-718 | 0.28 | Medium | 468 | 24 | 17 | 43 | 23700 | 19090 | 3450 | 21
53QDMT30-718 | 0.28 | Medium | 468 | 24 | 17 | 46 | 23180 | 18890 | 3510 | 21
53QDMT30-718 | 0.28 | Medium | 468 | 24 | 17 | 52 | 21145 | 18495 | 3640 | 21
53QDMT30-718 | 0.28 | Medium | 468 | 27 | 19 | 35 | 26315 | 19675 | 3345 | 21
53QDMT30-718 | 0.28 | Medium | 468 | 27 | 19 | 43 | 24485 | 19260 | 3510 | 21
53QDMT30-718 | 0.28 | Medium | 468 | 27 | 19 | 46 | 23695 | 18865 | 3580 | 21
53QDMT30-718 | 0.28 | Medium | 468 | 27 | 19 | 52 | 22110 | 18070 | 3715 | 21
53QDMT30-718 | 0.28 | Medium | 468 | 32 | 23 | 35 | 27370 | 23100 | 3515 | 21
53QDMT30-718 | 0.28 | Medium | 468 | 32 | 23 | 43 | 25270 | 22515 | 3655 | 21
53QDMT30-718 | 0.28 | Medium | 468 | 32 | 23 | 46 | 24475 | 22290 | 3690 | 21
53QDMT30-718 | 0.28 | Medium | 468 | 32 | 23 | 52 | 22895 | 21915 | 3770 | 21
53QDMT30-718 | 0.28 | Low | 369 | 21 | 15 | 35 | 23455 | 17355 | 3015 | 21
53QDMT30-718 | 0.28 | Low | 369 | 21 | 15 | 43 | 22445 | 17420 | 3115 | 21
53QDMT30-718 | 0.28 | Low | 369 | 21 | 15 | 46 | 21950 | 17240 | 3150 | 21
53QDMT30-718 | 0.28 | Low | 369 | 21 | 15 | 52 | 20955 | 16885 | 3215 | 21
53QDMT30-718 | 0.28 | Low | 369 | 24 | 17 | 35 | 24210 | 18135 | 3145 | 21
53QDMT30-718 | 0.28 | Low | 369 | 24 | 17 | 43 | 22710 | 17640 | 3305 | 21
53QDMT30-718 | 0.28 | Low | 369 | 24 | 17 | 46 | 22215 | 17455 | 3370 | 21
53QDMT30-718 | 0.28 | Low | 369 | 24 | 17 | 52 | 21220 | 15725 | 3490 | 21
53QDMT30-718 | 0.28 | Low | 369 | 27 | 19 | 35 | 25220 | 18180 | 3205 | 21
53QDMT30-718 | 0.28 | Low | 369 | 27 | 19 | 43 | 23465 | 17795 | 3365 | 21
53QDMT30-718 | 0.28 | Low | 369 | 27 | 19 | 46 | 22710 | 17430 | 3435 | 21
53QDMT30-718 | 0.28 | Low | 369 | 27 | 19 | 52 | 21190 | 16695 | 3560 | 21
53QDMT30-718 | 0.28 | Low | 369 | 21 | 23 | 35 | 26230 | 21340 | 3370 | 21
53QDMT30-718 | 0.28 | Low | 369 | 21 | 23 | 43 | 24215 | 20800 | 3500 | 21
53QDMT30-718 | 0.28 | Low | 369 | 21 | 23 | 46 | 23455 | 20595 | 3540 | 21
53QDMT30-718 | 0.28 | Low | 369 | 21 | 23 | 52 | 21940 | 20250 | 3615 | 21
53QDMT30-718 | 0.32 | High | 670 | 21 | 15 | 35 | 25145 | 20135 | 3230 | 21
53QDMT30-718 | 0.32 | High | 670 | 21 | 15 | 43 | 24065 | 20210 | 3340 | 21
53QDMT30-718 | 0.32 | High | 670 | 21 | 15 | 46 | 23530 | 20005 | 3375 | 21
53QDMT30-718 | 0.32 | High | 670 | 21 | 15 | 52 | 21055 | 18825 | 3445 | 21
53QDMT30-718 | 0.32 | High | 670 | 24 | 17 | 35 | 25960 | 21040 | 3370 | 21
53QDMT30-718 | 0.32 | High | 670 | 24 | 17 | 43 | 24350 | 20465 | 3535 | 21
53QDMT30-718 | 0.32 | High | 670 | 24 | 17 | 46 | 23815 | 20250 | 3610 | 21
53QDMT30-718 | 0.32 | High | 670 | 24 | 17 | 52 | 22740 | 19820 | 3740 | 21
53QDMT30-718 | 0.32 | High | 670 | 27 | 19 | 35 | 27040 | 21095 | 3435 | 21
53QDMT30-718 | 0.32 | High | 670 | 27 | 19 | 43 | 25160 | 20635 | 3610 | 21
53QDMT30-718 | 0.32 | High | 670 | 27 | 19 | 46 | 24345 | 20215 | 3675 | 21
53QDMT30-718 | 0.32 | High | 670 | 27 | 19 | 52 | 22740 | 19395 | 3805 | 21
53QDMT30-718 | 0.32 | High | 670 | 32 | 23 | 35 | 28125 | 24765 | 3615 | 21
53QDMT30-718 | 0.32 | High | 670 | 32 | 23 | 43 | 25965 | 24140 | 3755 | 21
53QDMT30-718 | 0.32 | High | 670 | 32 | 23 | 46 | 25150 | 23900 | 3795 | 21
53QDMT30-718 | 0.32 | High | 670 | 32 | 23 | 52 | 23520 | 23410 | 3875 | 21
53QDMT30-718 | 0.32 | Medium | 427 | 21 | 15 | 35 | 24140 | 18525 | 3130 | 21
53QDMT30-718 | 0.32 | Medium | 427 | 21 | 15 | 43 | 23105 | 18595 | 3240 | 21
53QDMT30-718 | 0.32 | Medium | 427 | 21 | 15 | 46 | 22590 | 18405 | 3275 | 21
53QDMT30-718 | 0.32 | Medium | 427 | 21 | 15 | 52 | 20215 | 17320 | 3345 | 21
53QDMT30-718 | 0.32 | Medium | 427 | 24 | 17 | 35 | 24925 | 19360 | 3265 | 21
53QDMT30-718 | 0.32 | Medium | 427 | 24 | 17 | 43 | 23380 | 18830 | 3440 | 21
53QDMT30-718 | 0.32 | Medium | 427 | 24 | 17 | 46 | 22865 | 18630 | 3505 | 21
53QDMT30-718 | 0.32 | Medium | 427 | 24 | 17 | 52 | 21830 | 18235 | 3630 | 21
53QDMT30-718 | 0.32 | Medium | 427 | 27 | 19 | 35 | 25960 | 19410 | 3330 | 21
53QDMT30-718 | 0.32 | Medium | 427 | 27 | 19 | 43 | 24155 | 18985 | 3505 | 21
53QDMT30-718 | 0.32 | Medium | 427 | 27 | 19 | 46 | 23375 | 18600 | 3565 | 21
53QDMT30-718 | 0.32 | Medium | 427 | 27 | 19 | 52 | 21830 | 17845 | 3690 | 21
53QDMT30-718 | 0.32 | Medium | 427 | 32 | 23 | 35 | 27000 | 22785 | 3505 | 21
53QDMT30-718 | 0.32 | Medium | 427 | 32 | 23 | 43 | 24930 | 22210 | 3645 | 21
53QDMT30-718 | 0.32 | Medium | 427 | 32 | 23 | 46 | 24145 | 21990 | 3680 | 21
53QDMT30-718 | 0.32 | Medium | 427 | 32 | 23 | 52 | 22580 | 21540 | 2760 | 21
53QDMT30-718 | 0.32 | Low | 327 | 21 | 15 | 35 | 23135 | 17115 | 3005 | 21
53QDMT30-718 | 0.32 | Low | 327 | 21 | 15 | 43 | 22140 | 17180 | 3105 | 21
53QDMT30-718 | 0.32 | Low | 327 | 21 | 15 | 46 | 21650 | 17005 | 3140 | 21
53QDMT30-718 | 0.32 | Low | 327 | 21 | 15 | 52 | 19375 | 16005 | 3205 | 21
53QDMT30-718 | 0.32 | Low | 327 | 24 | 17 | 35 | 23885 | 17885 | 3130 | 21
53QDMT30-718 | 0.32 | Low | 327 | 24 | 17 | 43 | 22405 | 17395 | 3300 | 21
53QDMT30-718 | 0.32 | Low | 327 | 24 | 17 | 46 | 21910 | 17215 | 3360 | 21
53QDMT30-718 | 0.32 | Low | 327 | 24 | 17 | 52 | 20925 | 16850 | 3480 | 21
53QDMT30-718 | 0.32 | Low | 327 | 27 | 19 | 35 | 24880 | 17935 | 3195 | 21
53QDMT30-718 | 0.32 | Low | 327 | 27 | 19 | 43 | 23150 | 17540 | 3360 | 21
53QDMT30-718 | 0.32 | Low | 327 | 27 | 19 | 46 | 22400 | 17185 | 3420 | 21
53QDMT30-718 | 0.32 | Low | 327 | 27 | 19 | 52 | 20925 | 16490 | 3540 | 21
53QDMT30-718 | 0.32 | Low | 327 | 21 | 23 | 35 | 25875 | 21050 | 3355 | 21
53QDMT30-718 | 0.32 | Low | 327 | 21 | 23 | 43 | 23890 | 20520 | 3495 | 21
53QDMT30-718 | 0.32 | Low | 327 | 21 | 23 | 46 | 23140 | 20315 | 3530 | 21
53QDMT30-718 | 0.32 | Low | 327 | 21 | 23 | 52 | 21640 | 19900 | 3605 | 21
53QDMT36-718 | 0 | High | 1080 | 21 | 15 | 35 | 34990 | 27970 | 3940 | 22
53QDMT36-718 | 0 | High | 1080 | 21 | 15 | 43 | 33490 | 28120 | 4065 | 22
53QDMT36-718 | 0 | High | 1080 | 21 | 15 | 46 | 32740 | 27835 | 4110 | 22
53QDMT36-718 | 0 | High | 1080 | 21 | 15 | 52 | 31240 | 27265 | 4200 | 22
53QDMT36-718 | 0 | High | 1080 | 24 | 17 | 35 | 36100 | 29225 | 4105 | 22
53QDMT36-718 | 0 | High | 1080 | 24 | 17 | 43 | 33845 | 28440 | 4320 | 22
53QDMT36-718 | 0 | High | 1080 | 24 | 17 | 46 | 33095 | 28130 | 4400 | 22
53QDMT36-718 | 0 | High | 1080 | 24 | 17 | 52 | 31595 | 27510 | 4560 | 22
53QDMT36-718 | 0 | High | 1080 | 27 | 19 | 35 | 37600 | 29330 | 4195 | 22
53QDMT36-718 | 0 | High | 1080 | 27 | 19 | 43 | 34990 | 28690 | 4400 | 22
53QDMT36-718 | 0 | High | 1080 | 27 | 19 | 46 | 33845 | 28095 | 4490 | 22
53QDMT36-718 | 0 | High | 1080 | 27 | 19 | 52 | 31555 | 26905 | 4670 | 22
53QDMT36-718 | 0 | High | 1080 | 32 | 23 | 35 | 39105 | 34415 | 4400 | 22
53QDMT36-718 | 0 | High | 1080 | 32 | 23 | 43 | 36100 | 33560 | 4570 | 22
53QDMT36-718 | 0 | High | 1080 | 32 | 23 | 46 | 35000 | 33260 | 4615 | 22
53QDMT36-718 | 0 | High | 1080 | 32 | 23 | 52 | 32800 | 32660 | 4705 | 22
53QDMT36-718 | 0 | Medium | 730 | 21 | 15 | 35 | 33590 | 25735 | 3825 | 22
53QDMT36-718 | 0 | Medium | 730 | 21 | 15 | 43 | 32150 | 25870 | 3945 | 22
53QDMT36-718 | 0 | Medium | 730 | 21 | 15 | 46 | 31430 | 25610 | 3990 | 22
53QDMT36-718 | 0 | Medium | 730 | 21 | 15 | 52 | 29990 | 25085 | 4075 | 22
53QDMT36-718 | 0 | Medium | 730 | 24 | 17 | 35 | 34660 | 26890 | 3985 | 22
53QDMT36-718 | 0 | Medium | 730 | 24 | 17 | 43 | 32495 | 26165 | 4190 | 22
53QDMT36-718 | 0 | Medium | 730 | 24 | 17 | 46 | 31775 | 25880 | 4270 | 22
53QDMT36-718 | 0 | Medium | 730 | 24 | 17 | 52 | 30335 | 25310 | 4425 | 22
53QDMT36-718 | 0 | Medium | 730 | 27 | 19 | 35 | 36100 | 26985 | 4070 | 22
53QDMT36-718 | 0 | Medium | 730 | 27 | 19 | 43 | 33590 | 26395 | 4270 | 22
53QDMT36-718 | 0 | Medium | 730 | 27 | 19 | 46 | 32495 | 25850 | 4355 | 22
53QDMT36-718 | 0 | Medium | 730 | 27 | 19 | 52 | 30295 | 24755 | 4530 | 22
53QDMT36-718 | 0 | Medium | 730 | 32 | 23 | 35 | 37545 | 31665 | 4270 | 22
53QDMT36-718 | 0 | Medium | 730 | 32 | 23 | 43 | 34660 | 30875 | 4435 | 22
53QDMT36-718 | 0 | Medium | 730 | 32 | 23 | 46 | 33600 | 30600 | 4480 | 22
53QDMT36-718 | 0 | Medium | 730 | 32 | 23 | 52 | 31490 | 30050 | 4565 | 22
53QDMT36-718 | 0 | Low | 645 | 21 | 15 | 35 | 32195 | 23775 | 3665 | 22
53QDMT36-718 | 0 | Low | 645 | 21 | 15 | 43 | 30815 | 23905 | 3780 | 22
53QDMT36-718 | 0 | Low | 645 | 21 | 15 | 46 | 30125 | 23670 | 3825 | 22
53QDMT36-718 | 0 | Low | 645 | 21 | 15 | 52 | 28745 | 23175 | 3905 | 22
53QDMT36-718 | 0 | Low | 645 | 24 | 17 | 35 | 33215 | 24840 | 3820 | 22
53QDMT36-718 | 0 | Low | 645 | 24 | 17 | 43 | 31140 | 24175 | 4020 | 22
53QDMT36-718 | 0 | Low | 645 | 24 | 17 | 46 | 30450 | 23915 | 4095 | 22
53QDMT36-718 | 0 | Low | 645 | 24 | 17 | 52 | 29070 | 23385 | 4240 | 22
53QDMT36-718 | 0 | Low | 645 | 27 | 19 | 35 | 34595 | 24930 | 3900 | 22
53QDMT36-718 | 0 | Low | 645 | 27 | 19 | 43 | 32195 | 24390 | 4095 | 22
53QDMT36-718 | 0 | Low | 645 | 27 | 19 | 46 | 31140 | 23885 | 4175 | 22
53QDMT36-718 | 0 | Low | 645 | 27 | 19 | 52 | 29035 | 22870 | 4345 | 22
53QDMT36-718 | 0 | Low | 645 | 21 | 23 | 35 | 35980 | 29255 | 4095 | 22
53QDMT36-718 | 0 | Low | 645 | 21 | 23 | 43 | 33215 | 28530 | 4250 | 22
53QDMT36-718 | 0 | Low | 645 | 21 | 23 | 46 | 32200 | 28275 | 4295 | 22
53QDMT36-718 | 0 | Low | 645 | 21 | 23 | 52 | 30180 | 27765 | 4375 | 22
53QDMT36-718 | 0.08 | High | 1005 | 21 | 15 | 35 | 34175 | 28320 | 3925 | 22
53QDMT36-718 | 0.08 | High | 1005 | 21 | 15 | 43 | 32715 | 27465 | 4050 | 22
53QDMT36-718 | 0.08 | High | 1005 | 21 | 15 | 46 | 31980 | 27190 | 4095 | 22
53QDMT36-718 | 0.08 | High | 1005 | 21 | 15 | 52 | 30510 | 26640 | 4185 | 22
53QDMT36-718 | 0.08 | High | 1005 | 24 | 17 | 35 | 35260 | 28545 | 4085 | 22
53QDMT36-718 | 0.08 | High | 1005 | 24 | 17 | 43 | 33055 | 27780 | 4300 | 22
53QDMT36-718 | 0.08 | High | 1005 | 24 | 17 | 46 | 32325 | 27475 | 4380 | 22
53QDMT36-718 | 0.08 | High | 1005 | 24 | 17 | 52 | 30865 | 26875 | 4540 | 22
53QDMT36-718 | 0.08 | High | 1005 | 27 | 19 | 35 | 36720 | 28645 | 4175 | 22
53QDMT36-718 | 0.08 | High | 1005 | 27 | 19 | 43 | 34175 | 28025 | 4380 | 22
53QDMT36-718 | 0.08 | High | 1005 | 27 | 19 | 46 | 33055 | 27445 | 4470 | 22
53QDMT36-718 | 0.08 | High | 1005 | 27 | 19 | 52 | 30820 | 26280 | 4650 | 22
53QDMT36-718 | 0.08 | High | 1005 | 32 | 23 | 35 | 38195 | 33615 | 4380 | 22
53QDMT36-718 | 0.08 | High | 1005 | 32 | 23 | 43 | 35260 | 32780 | 4550 | 22
53QDMT36-718 | 0.08 | High | 1005 | 32 | 23 | 46 | 34185 | 32485 | 4595 | 22
53QDMT36-718 | 0.08 | High | 1005 | 32 | 23 | 52 | 32035 | 31565 | 4685 | 22
53QDMT36-718 | 0.08 | Medium | 657 | 21 | 15 | 35 | 32810 | 26055 | 3810 | 22
53QDMT36-718 | 0.08 | Medium | 657 | 21 | 15 | 43 | 31405 | 25270 | 3930 | 22
53QDMT36-718 | 0.08 | Medium | 657 | 21 | 15 | 46 | 30700 | 25015 | 3975 | 22
53QDMT36-718 | 0.08 | Medium | 657 | 21 | 15 | 52 | 29290 | 24510 | 4060 | 22
53QDMT36-718 | 0.08 | Medium | 657 | 24 | 17 | 35 | 33850 | 26265 | 3965 | 22
53QDMT36-718 | 0.08 | Medium | 657 | 24 | 17 | 43 | 31735 | 25555 | 4175 | 22
53QDMT36-718 | 0.08 | Medium | 657 | 24 | 17 | 46 | 31035 | 25280 | 4250 | 22
53QDMT36-718 | 0.08 | Medium | 657 | 24 | 17 | 52 | 29630 | 24725 | 4405 | 22
53QDMT36-718 | 0.08 | Medium | 657 | 27 | 19 | 35 | 35255 | 26360 | 4050 | 22
53QDMT36-718 | 0.08 | Medium | 657 | 27 | 19 | 43 | 32740 | 25785 | 4250 | 22
53QDMT36-718 | 0.08 | Medium | 657 | 27 | 19 | 46 | 31735 | 25250 | 4335 | 22
53QDMT36-718 | 0.08 | Medium | 657 | 27 | 19 | 52 | 29590 | 24180 | 4510 | 22
53QDMT36-718 | 0.08 | Medium | 657 | 32 | 23 | 35 | 36670 | 30925 | 4250 | 22
53QDMT36-718 | 0.08 | Medium | 657 | 32 | 23 | 43 | 33850 | 30155 | 4335 | 22
53QDMT36-718 | 0.08 | Medium | 657 | 32 | 23 | 46 | 32820 | 29890 | 4460 | 22
53QDMT36-718 | 0.08 | Medium | 657 | 32 | 23 | 52 | 30755 | 29045 | 4545 | 22
53QDMT36-718 | 0.08 | Low | 562 | 21 | 15 | 35 | 31445 | 24070 | 3650 | 22
53QDMT36-718 | 0.08 | Low | 562 | 21 | 15 | 43 | 30100 | 23350 | 3770 | 22
53QDMT36-718 | 0.08 | Low | 562 | 21 | 15 | 46 | 29425 | 23120 | 3810 | 22
53QDMT36-718 | 0.08 | Low | 562 | 21 | 15 | 52 | 28075 | 22645 | 3895 | 22
53QDMT36-718 | 0.08 | Low | 562 | 24 | 17 | 35 | 32440 | 24265 | 3800 | 22
53QDMT36-718 | 0.08 | Low | 562 | 24 | 17 | 43 | 30415 | 23615 | 4000 | 22
53QDMT36-718 | 0.08 | Low | 562 | 24 | 17 | 46 | 29740 | 23360 | 4075 | 22
53QDMT36-718 | 0.08 | Low | 562 | 24 | 17 | 52 | 28395 | 22845 | 4225 | 22
53QDMT36-718 | 0.08 | Low | 562 | 27 | 19 | 35 | 33785 | 24350 | 3885 | 22
53QDMT36-718 | 0.08 | Low | 562 | 27 | 19 | 43 | 31445 | 23825 | 4075 | 22
53QDMT36-718 | 0.08 | Low | 562 | 27 | 19 | 46 | 30415 | 23330 | 4160 | 22
53QDMT36-718 | 0.08 | Low | 562 | 27 | 19 | 52 | 28665 | 22340 | 4325 | 22
53QDMT36-718 | 0.08 | Low | 562 | 21 | 23 | 35 | 35140 | 28575 | 4075 | 22
53QDMT36-718 | 0.08 | Low | 562 | 21 | 23 | 43 | 32440 | 27865 | 4235 | 22
53QDMT36-718 | 0.08 | Low | 562 | 21 | 23 | 46 | 31450 | 27615 | 4275 | 22
53QDMT36-718 | 0.08 | Low | 562 | 21 | 23 | 52 | 29490 | 26835 | 4360 | 22
53QDMT36-718 | 0.12 | High | 976 | 21 | 15 | 35 | 33765 | 30990 | 3915 | 22
53QDMT36-718 | 0.12 | High | 976 | 21 | 15 | 43 | 32330 | 27140 | 4040 | 22
53QDMT36-718 | 0.12 | High | 976 | 21 | 15 | 46 | 31600 | 26870 | 4085 | 22
53QDMT36-718 | 0.12 | High | 976 | 21 | 15 | 52 | 30140 | 26330 | 4175 | 22
53QDMT36-718 | 0.12 | High | 976 | 24 | 17 | 35 | 34835 | 28205 | 4075 | 22
53QDMT36-718 | 0.12 | High | 976 | 24 | 17 | 43 | 32660 | 27445 | 4290 | 22
53QDMT36-718 | 0.12 | High | 976 | 24 | 17 | 46 | 31940 | 27150 | 4370 | 22
53QDMT36-718 | 0.12 | High | 976 | 24 | 17 | 52 | 30500 | 26560 | 4530 | 22
53QDMT36-718 | 0.12 | High | 976 | 27 | 19 | 35 | 36280 | 28305 | 4165 | 22
53QDMT36-718 | 0.12 | High | 976 | 27 | 19 | 43 | 33765 | 27690 | 4370 | 22
53QDMT36-718 | 0.12 | High | 976 | 27 | 19 | 46 | 32660 | 27115 | 4460 | 22
53QDMT36-718 | 0.12 | High | 976 | 27 | 19 | 52 | 30450 | 25965 | 4640 | 22
53QDMT36-718 | 0.12 | High | 976 | 32 | 23 | 35 | 37735 | 33210 | 4370 | 22
53QDMT36-718 | 0.12 | High | 976 | 32 | 23 | 43 | 34835 | 32385 | 4540 | 22
53QDMT36-718 | 0.12 | High | 976 | 32 | 23 | 46 | 33775 | 32100 | 4585 | 22
53QDMT36-718 | 0.12 | High | 976 | 32 | 23 | 52 | 31655 | 30180 | 4675 | 22
53QDMT36-718 | 0.12 | Medium | 624 | 21 | 15 | 35 | 32415 | 28515 | 3800 | 22
53QDMT36-718 | 0.12 | Medium | 624 | 21 | 15 | 43 | 31040 | 24970 | 3920 | 22
53QDMT36-718 | 0.12 | Medium | 624 | 21 | 15 | 46 | 30340 | 24720 | 3965 | 22
53QDMT36-718 | 0.12 | Medium | 624 | 21 | 15 | 52 | 28935 | 24225 | 4050 | 22
53QDMT36-718 | 0.12 | Medium | 624 | 24 | 17 | 35 | 33445 | 25950 | 3955 | 22
53QDMT36-718 | 0.12 | Medium | 624 | 24 | 17 | 43 | 31355 | 25250 | 4160 | 22
53QDMT36-718 | 0.12 | Medium | 624 | 24 | 17 | 46 | 30665 | 24980 | 4240 | 22
53QDMT36-718 | 0.12 | Medium | 624 | 24 | 17 | 52 | 29280 | 24435 | 4395 | 22
53QDMT36-718 | 0.12 | Medium | 624 | 27 | 19 | 35 | 34830 | 26045 | 4040 | 22
53QDMT36-718 | 0.12 | Medium | 624 | 27 | 19 | 43 | 32415 | 25475 | 4240 | 22
53QDMT36-718 | 0.12 | Medium | 624 | 27 | 19 | 46 | 31355 | 24950 | 4325 | 22
53QDMT36-718 | 0.12 | Medium | 624 | 27 | 19 | 52 | 29235 | 23890 | 4500 | 22
53QDMT36-718 | 0.12 | Medium | 624 | 32 | 23 | 35 | 36230 | 30555 | 4240 | 22
53QDMT36-718 | 0.12 | Medium | 624 | 32 | 23 | 43 | 33445 | 29795 | 4405 | 22
53QDMT36-718 | 0.12 | Medium | 624 | 32 | 23 | 46 | 32425 | 29535 | 4450 | 22
53QDMT36-718 | 0.12 | Medium | 624 | 32 | 23 | 52 | 30390 | 27770 | 4535 | 22
53QDMT36-718 | 0.12 | Low | 525 | 21 | 15 | 35 | 31065 | 26345 | 3640 | 22
53QDMT36-718 | 0.12 | Low | 525 | 21 | 15 | 43 | 29745 | 23070 | 3760 | 22
53QDMT36-718 | 0.12 | Low | 525 | 21 | 15 | 46 | 29075 | 22840 | 3800 | 22
53QDMT36-718 | 0.12 | Low | 525 | 21 | 15 | 52 | 27730 | 22385 | 3885 | 22
53QDMT36-718 | 0.12 | Low | 525 | 24 | 17 | 35 | 32050 | 23975 | 3790 | 22
53QDMT36-718 | 0.12 | Low | 525 | 24 | 17 | 43 | 30050 | 23330 | 3990 | 22
53QDMT36-718 | 0.12 | Low | 525 | 24 | 17 | 46 | 29385 | 23080 | 4065 | 22
53QDMT36-718 | 0.12 | Low | 525 | 24 | 17 | 52 | 28060 | 22580 | 4215 | 22
53QDMT36-718 | 0.12 | Low | 525 | 27 | 19 | 35 | 33380 | 24060 | 3875 | 22
53QDMT36-718 | 0.12 | Low | 525 | 27 | 19 | 43 | 31065 | 23540 | 4065 | 22
53QDMT36-718 | 0.12 | Low | 525 | 27 | 19 | 46 | 30050 | 23050 | 4150 | 22
53QDMT36-718 | 0.12 | Low | 525 | 27 | 19 | 52 | 29235 | 22070 | 4315 | 22
53QDMT36-718 | 0.12 | Low | 525 | 21 | 23 | 35 | 34720 | 28230 | 4065 | 22
53QDMT36-718 | 0.12 | Low | 525 | 21 | 23 | 43 | 32050 | 27530 | 4225 | 22
53QDMT36-718 | 0.12 | Low | 525 | 21 | 23 | 46 | 31075 | 27285 | 4265 | 22
53QDMT36-718 | 0.12 | Low | 525 | 21 | 23 | 52 | 29175 | 25655 | 4350 | 22
53QDMT36-718 | 0.16 | High | 947 | 21 | 15 | 35 | 33355 | 28665 | 3910 | 22
53QDMT36-718 | 0.16 | High | 947 | 21 | 15 | 43 | 31935 | 26810 | 4035 | 22
53QDMT36-718 | 0.16 | High | 947 | 21 | 15 | 46 | 31215 | 26545 | 4080 | 22
53QDMT36-718 | 0.16 | High | 947 | 21 | 15 | 52 | 29780 | 26008 | 4170 | 22
53QDMT36-718 | 0.16 | High | 947 | 24 | 17 | 35 | 34415 | 27865 | 4065 | 22
53QDMT36-718 | 0.16 | High | 947 | 24 | 17 | 43 | 32265 | 27115 | 4280 | 22
53QDMT36-718 | 0.16 | High | 947 | 24 | 17 | 46 | 31555 | 26820 | 4360 | 22
53QDMT36-718 | 0.16 | High | 947 | 24 | 17 | 52 | 30128 | 26235 | 4520 | 22
53QDMT36-718 | 0.16 | High | 947 | 27 | 19 | 35 | 35840 | 27960 | 4155 | 22
53QDMT36-718 | 0.16 | High | 947 | 27 | 19 | 43 | 33355 | 27355 | 4360 | 22
53QDMT36-718 | 0.16 | High | 947 | 27 | 19 | 46 | 32265 | 26790 | 4450 | 22
53QDMT36-718 | 0.16 | High | 947 | 27 | 19 | 52 | 30085 | 25655 | 4630 | 22
53QDMT36-718 | 0.16 | High | 947 | 32 | 23 | 35 | 37280 | 32810 | 4360 | 22
53QDMT36-718 | 0.16 | High | 947 | 32 | 23 | 43 | 34415 | 31995 | 4530 | 22
53QDMT36-718 | 0.16 | High | 947 | 32 | 23 | 46 | 33365 | 31710 | 4575 | 22
53QDMT36-718 | 0.16 | High | 947 | 32 | 23 | 52 | 31270 | 30470 | 4665 | 22
53QDMT36-718 | 0.16 | Medium | 591 | 21 | 15 | 35 | 32025 | 26375 | 3795 | 22
53QDMT36-718 | 0.16 | Medium | 591 | 21 | 15 | 43 | 30660 | 24670 | 3915 | 22
53QDMT36-718 | 0.16 | Medium | 591 | 21 | 15 | 46 | 29970 | 24420 | 3960 | 22
53QDMT36-718 | 0.16 | Medium | 591 | 21 | 15 | 52 | 28590 | 23930 | 4045 | 22
53QDMT36-718 | 0.16 | Medium | 591 | 24 | 17 | 35 | 33040 | 25635 | 3945 | 22
53QDMT36-718 | 0.16 | Medium | 591 | 24 | 17 | 43 | 30975 | 24945 | 4155 | 22
53QDMT36-718 | 0.16 | Medium | 591 | 24 | 17 | 46 | 30295 | 24680 | 4230 | 22
53QDMT36-718 | 0.16 | Medium | 591 | 24 | 17 | 52 | 28925 | 24140 | 4385 | 22
53QDMT36-718 | 0.16 | Medium | 591 | 27 | 19 | 35 | 34410 | 25730 | 4030 | 22
53QDMT36-718 | 0.16 | Medium | 591 | 27 | 19 | 43 | 31890 | 25170 | 4230 | 22
53QDMT36-718 | 0.16 | Medium | 591 | 27 | 19 | 46 | 30975 | 24650 | 4315 | 22
53QDMT36-718 | 0.16 | Medium | 591 | 27 | 19 | 52 | 28885 | 23605 | 4490 | 22
53QDMT36-718 | 0.16 | Medium | 591 | 32 | 23 | 35 | 35790 | 30185 | 4230 | 22
53QDMT36-718 | 0.16 | Medium | 591 | 32 | 23 | 43 | 33040 | 29435 | 4230 | 22
53QDMT36-718 | 0.16 | Medium | 591 | 32 | 23 | 46 | 32035 | 29175 | 4440 | 22
53QDMT36-718 | 0.16 | Medium | 591 | 32 | 23 | 52 | 30020 | 28035 | 4525 | 22
53QDMT36-718 | 0.16 | Low | 495 | 21 | 15 | 35 | 30690 | 24365 | 3635 | 22
53QDMT36-718 | 0.16 | Low | 495 | 21 | 15 | 43 | 29380 | 22790 | 3755 | 22
53QDMT36-718 | 0.16 | Low | 495 | 21 | 15 | 46 | 28720 | 22565 | 3795 | 22
53QDMT36-718 | 0.16 | Low | 495 | 21 | 15 | 52 | 27400 | 22110 | 3880 | 22
53QDMT36-718 | 0.16 | Low | 495 | 24 | 17 | 35 | 31665 | 23685 | 3780 | 22
53QDMT36-718 | 0.16 | Low | 495 | 24 | 17 | 43 | 29685 | 23050 | 3980 | 22
53QDMT36-718 | 0.16 | Low | 495 | 24 | 17 | 46 | 29030 | 22800 | 4055 | 22
53QDMT36-718 | 0.16 | Low | 495 | 24 | 17 | 52 | 27720 | 22305 | 4205 | 22
53QDMT36-718 | 0.16 | Low | 495 | 27 | 19 | 35 | 32975 | 23770 | 3865 | 22
53QDMT36-718 | 0.16 | Low | 495 | 27 | 19 | 43 | 30690 | 23255 | 4055 | 22
53QDMT36-718 | 0.16 | Low | 495 | 27 | 19 | 46 | 29685 | 22775 | 4140 | 22
53QDMT36-718 | 0.16 | Low | 495 | 27 | 19 | 52 | 28290 | 21805 | 4305 | 22
53QDMT36-718 | 0.16 | Low | 495 | 21 | 23 | 35 | 34295 | 27890 | 4055 | 22
53QDMT36-718 | 0.16 | Low | 495 | 21 | 23 | 43 | 31665 | 27195 | 4215 | 22
53QDMT36-718 | 0.16 | Low | 495 | 21 | 23 | 46 | 30700 | 26955 | 4255 | 22
53QDMT36-718 | 0.16 | Low | 495 | 21 | 23 | 52 | 28795 | 25905 | 4340 | 22
53QDMT36-718 | 0.2 | High | 915 | 21 | 15 | 35 | 32945 | 26335 | 3900 | 23
53QDMT36-718 | 0.2 | High | 915 | 21 | 15 | 43 | 31535 | 26480 | 4025 | 23
53QDMT36-718 | 0.2 | High | 915 | 21 | 15 | 46 | 30830 | 26215 | 4070 | 23
53QDMT36-718 | 0.2 | High | 915 | 21 | 15 | 52 | 29420 | 25685 | 4160 | 23
53QDMT36-718 | 0.2 | High | 915 | 24 | 17 | 35 | 33990 | 27520 | 4055 | 23
53QDMT36-718 | 0.2 | High | 915 | 24 | 17 | 43 | 31870 | 26780 | 4270 | 23
53QDMT36-718 | 0.2 | High | 915 | 24 | 17 | 46 | 31165 | 26490 | 4350 | 23
53QDMT36-718 | 0.2 | High | 915 | 24 | 17 | 52 | 29755 | 25910 | 4510 | 23
53QDMT36-718 | 0.2 | High | 915 | 27 | 19 | 35 | 35400 | 27615 | 4145 | 23
53QDMT36-718 | 0.2 | High | 915 | 27 | 19 | 43 | 32945 | 27015 | 4350 | 23
53QDMT36-718 | 0.2 | High | 915 | 27 | 19 | 46 | 31870 | 26460 | 4440 | 23
53QDMT36-718 | 0.2 | High | 915 | 27 | 19 | 52 | 29720 | 25340 | 4620 | 23
53QDMT36-718 | 0.2 | High | 915 | 32 | 23 | 35 | 36820 | 32405 | 4350 | 23
53QDMT36-718 | 0.2 | High | 915 | 32 | 23 | 43 | 33990 | 31600 | 4520 | 23
53QDMT36-718 | 0.2 | High | 915 | 32 | 23 | 46 | 32955 | 31320 | 4565 | 23
53QDMT36-718 | 0.2 | High | 915 | 32 | 23 | 52 | 30885 | 30760 | 4655 | 23
53QDMT36-718 | 0.2 | Medium | 550 | 21 | 15 | 35 | 31630 | 24230 | 3785 | 23
53QDMT36-718 | 0.2 | Medium | 550 | 21 | 15 | 43 | 30275 | 24365 | 3905 | 23
53QDMT36-718 | 0.2 | Medium | 550 | 21 | 15 | 46 | 29600 | 24120 | 3950 | 23
53QDMT36-718 | 0.2 | Medium | 550 | 21 | 15 | 52 | 28245 | 23630 | 4035 | 23
53QDMT36-718 | 0.2 | Medium | 550 | 24 | 17 | 35 | 32630 | 25320 | 3935 | 23
53QDMT36-718 | 0.2 | Medium | 550 | 24 | 17 | 43 | 30595 | 24640 | 4140 | 23
53QDMT36-718 | 0.2 | Medium | 550 | 24 | 17 | 46 | 29920 | 24375 | 4220 | 23
53QDMT36-718 | 0.2 | Medium | 550 | 24 | 17 | 52 | 28565 | 23840 | 4375 | 23
53QDMT36-718 | 0.2 | Medium | 550 | 27 | 19 | 35 | 33985 | 25410 | 4020 | 23
53QDMT36-718 | 0.2 | Medium | 550 | 27 | 19 | 43 | 31360 | 24860 | 4220 | 23
53QDMT36-718 | 0.2 | Medium | 550 | 27 | 19 | 46 | 30595 | 24345 | 4310 | 23
53QDMT36-718 | 0.2 | Medium | 550 | 27 | 19 | 52 | 28535 | 23315 | 4480 | 23
53QDMT36-718 | 0.2 | Medium | 550 | 32 | 23 | 35 | 35350 | 29815 | 4220 | 23
53QDMT36-718 | 0.2 | Medium | 550 | 32 | 23 | 43 | 32630 | 29075 | 4385 | 23
53QDMT36-718 | 0.2 | Medium | 550 | 32 | 23 | 46 | 31640 | 28815 | 4430 | 23
53QDMT36-718 | 0.2 | Medium | 550 | 32 | 23 | 52 | 29650 | 28300 | 4515 | 23
53QDMT36-718 | 0.2 | Low | 453 | 21 | 15 | 35 | 30310 | 22385 | 3630 | 23
53QDMT36-718 | 0.2 | Low | 453 | 21 | 15 | 43 | 29015 | 22510 | 3745 | 23
53QDMT36-718 | 0.2 | Low | 453 | 21 | 15 | 46 | 28365 | 22285 | 3785 | 23
53QDMT36-718 | 0.2 | Low | 453 | 21 | 15 | 52 | 27070 | 21835 | 3870 | 23
53QDMT36-718 | 0.2 | Low | 453 | 24 | 17 | 35 | 31275 | 23395 | 3770 | 23
53QDMT36-718 | 0.2 | Low | 453 | 24 | 17 | 43 | 29320 | 22765 | 3850 | 23
53QDMT36-718 | 0.2 | Low | 453 | 24 | 17 | 46 | 28675 | 22520 | 4045 | 23
53QDMT36-718 | 0.2 | Low | 453 | 24 | 17 | 52 | 27375 | 22025 | 4195 | 23
53QDMT36-718 | 0.2 | Low | 453 | 27 | 19 | 35 | 32570 | 23475 | 3855 | 23
53QDMT36-718 | 0.2 | Low | 453 | 27 | 19 | 43 | 30310 | 22970 | 4045 | 23
53QDMT36-718 | 0.2 | Low | 453 | 27 | 19 | 46 | 29320 | 22495 | 4130 | 23
53QDMT36-718 | 0.2 | Low | 453 | 27 | 19 | 52 | 27345 | 21540 | 4300 | 23
53QDMT36-718 | 0.2 | Low | 453 | 21 | 23 | 35 | 33875 | 27545 | 4045 | 23
53QDMT36-718 | 0.2 | Low | 453 | 21 | 23 | 43 | 31275 | 26860 | 4205 | 23
53QDMT36-718 | 0.2 | Low | 453 | 21 | 23 | 46 | 30320 | 26625 | 4245 | 23
53QDMT36-718 | 0.2 | Low | 453 | 21 | 23 | 52 | 28415 | 26150 | 4330 | 23
53QDMT36-718 | 0.24 | High | 883 | 21 | 15 | 35 | 32535 | 26010 | 3890 | 23
53QDMT36-718 | 0.24 | High | 883 | 21 | 15 | 43 | 31140 | 26150 | 4015 | 23
53QDMT36-718 | 0.24 | High | 883 | 21 | 15 | 46 | 30445 | 25885 | 4060 | 23
53QDMT36-718 | 0.24 | High | 883 | 21 | 15 | 52 | 29055 | 25360 | 4150 | 23
53QDMT36-718 | 0.24 | High | 883 | 24 | 17 | 35 | 33570 | 27180 | 4045 | 23
53QDMT36-718 | 0.24 | High | 883 | 24 | 17 | 43 | 31475 | 26450 | 4260 | 23
53QDMT36-718 | 0.24 | High | 883 | 24 | 17 | 46 | 30780 | 26165 | 4340 | 23
53QDMT36-718 | 0.24 | High | 883 | 24 | 17 | 52 | 29390 | 25590 | 4500 | 23
53QDMT36-718 | 0.24 | High | 883 | 27 | 19 | 35 | 34960 | 27275 | 4135 | 23
53QDMT36-718 | 0.24 | High | 883 | 27 | 19 | 43 | 32535 | 26680 | 4340 | 23
53QDMT36-718 | 0.24 | High | 883 | 27 | 19 | 46 | 31470 | 26125 | 4430 | 23
53QDMT36-718 | 0.24 | High | 883 | 27 | 19 | 52 | 29340 | 25020 | 4610 | 23
53QDMT36-718 | 0.24 | High | 883 | 32 | 23 | 35 | 36365 | 32005 | 4340 | 23
53QDMT36-718 | 0.24 | High | 883 | 32 | 23 | 43 | 33570 | 31210 | 4510 | 23
53QDMT36-718 | 0.24 | High | 883 | 32 | 23 | 46 | 32550 | 30935 | 4555 | 23
53QDMT36-718 | 0.24 | High | 883 | 32 | 23 | 52 | 30510 | 30380 | 4645 | 23
53QDMT36-718 | 0.24 | Medium | 509 | 21 | 15 | 35 | 31235 | 23930 | 3775 | 23
53QDMT36-718 | 0.24 | Medium | 509 | 21 | 15 | 43 | 29895 | 24060 | 3895 | 23
53QDMT36-718 | 0.24 | Medium | 509 | 21 | 15 | 46 | 29230 | 23815 | 3940 | 23
53QDMT36-718 | 0.24 | Medium | 509 | 21 | 15 | 52 | 27895 | 23335 | 4025 | 23
53QDMT36-718 | 0.24 | Medium | 509 | 24 | 17 | 35 | 32230 | 25010 | 3925 | 23
53QDMT36-718 | 0.24 | Medium | 509 | 24 | 17 | 43 | 30220 | 24335 | 4135 | 23
53QDMT36-718 | 0.24 | Medium | 509 | 24 | 17 | 46 | 29550 | 24075 | 4210 | 23
53QDMT36-718 | 0.24 | Medium | 509 | 24 | 17 | 52 | 28215 | 23545 | 4365 | 23
53QDMT36-718 | 0.24 | Medium | 509 | 27 | 19 | 35 | 33565 | 25095 | 4010 | 23
53QDMT36-718 | 0.24 | Medium | 509 | 27 | 19 | 43 | 31235 | 24550 | 4210 | 23
53QDMT36-718 | 0.24 | Medium | 509 | 27 | 19 | 46 | 30215 | 24035 | 4300 | 23
53QDMT36-718 | 0.24 | Medium | 509 | 27 | 19 | 52 | 28170 | 23020 | 4475 | 23
53QDMT36-718 | 0.24 | Medium | 509 | 32 | 23 | 35 | 34910 | 29445 | 4210 | 23
53QDMT36-718 | 0.24 | Medium | 509 | 32 | 23 | 43 | 32230 | 28715 | 4375 | 23
53QDMT36-718 | 0.24 | Medium | 509 | 32 | 23 | 46 | 31250 | 28460 | 4420 | 23
53QDMT36-718 | 0.24 | Medium | 509 | 32 | 23 | 52 | 29290 | 27950 | 4505 | 23
53QDMT36-718 | 0.24 | Low | 411 | 21 | 15 | 35 | 29935 | 22100 | 3620 | 23
53QDMT36-718 | 0.24 | Low | 411 | 21 | 15 | 43 | 28650 | 22230 | 3735 | 23
53QDMT36-718 | 0.24 | Low | 411 | 21 | 15 | 46 | 28010 | 22005 | 3775 | 23
53QDMT36-718 | 0.24 | Low | 411 | 21 | 15 | 52 | 26735 | 21560 | 3860 | 23
53QDMT36-718 | 0.24 | Low | 411 | 24 | 17 | 35 | 30885 | 23105 | 3765 | 23
53QDMT36-718 | 0.24 | Low | 411 | 24 | 17 | 43 | 28960 | 22485 | 3965 | 23
53QDMT36-718 | 0.24 | Low | 411 | 24 | 17 | 46 | 28320 | 22240 | 4035 | 23
53QDMT36-718 | 0.24 | Low | 411 | 24 | 17 | 52 | 27040 | 21755 | 4185 | 23
53QDMT36-718 | 0.24 | Low | 411 | 27 | 19 | 35 | 32165 | 23185 | 3845 | 23
53QDMT36-718 | 0.24 | Low | 411 | 27 | 19 | 43 | 29935 | 22680 | 4035 | 23
53QDMT36-718 | 0.24 | Low | 411 | 27 | 19 | 46 | 28955 | 22210 | 4120 | 23
53QDMT36-718 | 0.24 | Low | 411 | 27 | 19 | 52 | 26995 | 21270 | 3920 | 23
53QDMT36-718 | 0.24 | Low | 411 | 21 | 23 | 35 | 33460 | 27205 | 4035 | 23
53QDMT36-718 | 0.24 | Low | 411 | 21 | 23 | 43 | 30885 | 26530 | 4195 | 23
53QDMT36-718 | 0.24 | Low | 411 | 21 | 23 | 46 | 29950 | 26295 | 4235 | 23
53QDMT36-718 | 0.24 | Low | 411 | 21 | 23 | 52 | 28070 | 25825 | 4320 | 23
53QDMT36-718 | 0.28 | High | 851 | 21 | 15 | 35 | 32125 | 25685 | 3880 | 23
53QDMT36-718 | 0.28 | High | 851 | 21 | 15 | 43 | 30745 | 25820 | 4005 | 23
53QDMT36-718 | 0.28 | High | 851 | 21 | 15 | 46 | 30060 | 25560 | 4050 | 23
53QDMT36-718 | 0.28 | High | 851 | 21 | 15 | 52 | 28690 | 25045 | 4140 | 23
53QDMT36-718 | 0.28 | High | 851 | 24 | 17 | 35 | 33150 | 26840 | 4035 | 23
53QDMT36-718 | 0.28 | High | 851 | 24 | 17 | 43 | 31080 | 26120 | 4250 | 23
53QDMT36-718 | 0.28 | High | 851 | 24 | 17 | 46 | 30395 | 25840 | 4330 | 23
53QDMT36-718 | 0.28 | High | 851 | 24 | 17 | 52 | 29025 | 25275 | 4490 | 23
53QDMT36-718 | 0.28 | High | 851 | 27 | 19 | 35 | 34520 | 26935 | 4125 | 23
53QDMT36-718 | 0.28 | High | 851 | 27 | 19 | 43 | 32125 | 26345 | 4330 | 23
53QDMT36-718 | 0.28 | High | 851 | 27 | 19 | 46 | 31075 | 25800 | 4420 | 23
53QDMT36-718 | 0.28 | High | 851 | 27 | 19 | 52 | 28975 | 24710 | 4600 | 23
53QDMT36-718 | 0.28 | High | 851 | 32 | 23 | 35 | 35910 | 31605 | 4330 | 23
53QDMT36-718 | 0.28 | High | 851 | 32 | 23 | 43 | 33150 | 30820 | 4500 | 23
53QDMT36-718 | 0.28 | High | 851 | 32 | 23 | 46 | 32145 | 30550 | 4545 | 23
53QDMT36-718 | 0.28 | High | 851 | 32 | 23 | 52 | 30135 | 30010 | 4635 | 23
53QDMT36-718 | 0.28 | Medium | 468 | 21 | 15 | 35 | 30845 | 23630 | 3765 | 23
53QDMT36-718 | 0.28 | Medium | 468 | 21 | 15 | 43 | 29515 | 23755 | 3885 | 23
53QDMT36-718 | 0.28 | Medium | 468 | 21 | 15 | 46 | 28860 | 23515 | 3930 | 23
53QDMT36-718 | 0.28 | Medium | 468 | 21 | 15 | 52 | 27545 | 23045 | 4015 | 23
53QDMT36-718 | 0.28 | Medium | 468 | 24 | 17 | 35 | 31825 | 24695 | 3915 | 23
53QDMT36-718 | 0.28 | Medium | 468 | 24 | 17 | 43 | 29840 | 24030 | 4125 | 23
53QDMT36-718 | 0.28 | Medium | 468 | 24 | 17 | 46 | 29180 | 23775 | 4200 | 23
53QDMT36-718 | 0.28 | Medium | 468 | 24 | 17 | 52 | 27865 | 23255 | 4355 | 23
53QDMT36-718 | 0.28 | Medium | 468 | 27 | 19 | 35 | 33145 | 24780 | 4000 | 23
53QDMT36-718 | 0.28 | Medium | 468 | 27 | 19 | 43 | 30840 | 24240 | 4200 | 23
53QDMT36-718 | 0.28 | Medium | 468 | 27 | 19 | 46 | 29835 | 23740 | 4290 | 23
53QDMT36-718 | 0.28 | Medium | 468 | 27 | 19 | 52 | 27820 | 22735 | 4462 | 23
53QDMT36-718 | 0.28 | Medium | 468 | 32 | 23 | 35 | 34475 | 29080 | 4200 | 23
53QDMT36-718 | 0.28 | Medium | 468 | 32 | 23 | 43 | 31825 | 28355 | 4365 | 23
53QDMT36-718 | 0.28 | Medium | 468 | 32 | 23 | 46 | 30860 | 28110 | 4410 | 23
53QDMT36-718 | 0.28 | Medium | 468 | 32 | 23 | 52 | 28930 | 27610 | 4495 | 23
53QDMT36-718 | 0.28 | Low | 369 | 21 | 15 | 35 | 29560 | 21835 | 3610 | 23
53QDMT36-718 | 0.28 | Low | 369 | 21 | 15 | 43 | 28285 | 21950 | 3725 | 23
53QDMT36-718 | 0.28 | Low | 369 | 21 | 15 | 46 | 27655 | 21730 | 3765 | 23
53QDMT36-718 | 0.28 | Low | 369 | 21 | 15 | 52 | 26395 | 21290 | 3850 | 23
53QDMT36-718 | 0.28 | Low | 369 | 24 | 17 | 35 | 30500 | 22815 | 3755 | 23
53QDMT36-718 | 0.28 | Low | 369 | 24 | 17 | 43 | 28595 | 22205 | 3955 | 23
53QDMT36-718 | 0.28 | Low | 369 | 24 | 17 | 46 | 27965 | 21965 | 4030 | 23
53QDMT36-718 | 0.28 | Low | 369 | 24 | 17 | 52 | 26705 | 21485 | 4175 | 23
53QDMT36-718 | 0.28 | Low | 369 | 27 | 19 | 35 | 31760 | 22895 | 3835 | 23
53QDMT36-718 | 0.28 | Low | 369 | 27 | 19 | 43 | 29555 | 22395 | 4030 | 23
53QDMT36-718 | 0.28 | Low | 369 | 27 | 19 | 46 | 28590 | 21930 | 4110 | 23
53QDMT36-718 | 0.28 | Low | 369 | 27 | 19 | 52 | 26660 | 21010 | 4280 | 23
53QDMT36-718 | 0.28 | Low | 369 | 21 | 23 | 35 | 33040 | 26865 | 4030 | 23
53QDMT36-718 | 0.28 | Low | 369 | 21 | 23 | 43 | 30500 | 26200 | 4185 | 23
53QDMT36-718 | 0.28 | Low | 369 | 21 | 23 | 46 | 29575 | 25970 | 4230 | 23
53QDMT36-718 | 0.28 | Low | 369 | 21 | 23 | 52 | 27725 | 25510 | 4310 | 23
53QDMT36-718 | 0.32 | High | 819 | 21 | 15 | 35 | 31715 | 25355 | 3870 | 23
53QDMT36-718 | 0.32 | High | 819 | 21 | 15 | 43 | 30345 | 25785 | 3995 | 23
53QDMT36-718 | 0.32 | High | 819 | 21 | 15 | 46 | 26975 | 22940 | 4040 | 23
53QDMT36-718 | 0.32 | High | 819 | 21 | 15 | 52 | 28340 | 24745 | 4130 | 23
53QDMT36-718 | 0.32 | High | 819 | 24 | 17 | 35 | 32725 | 26500 | 4025 | 23
53QDMT36-718 | 0.32 | High | 819 | 24 | 17 | 43 | 30685 | 25785 | 4240 | 23
53QDMT36-718 | 0.32 | High | 819 | 24 | 17 | 46 | 28730 | 24420 | 4320 | 23
53QDMT36-718 | 0.32 | High | 819 | 24 | 17 | 52 | 28640 | 24940 | 4480 | 23
53QDMT36-718 | 0.32 | High | 819 | 27 | 19 | 35 | 34080 | 26585 | 4115 | 23
53QDMT36-718 | 0.32 | High | 819 | 27 | 19 | 43 | 31715 | 26015 | 4320 | 23
53QDMT36-718 | 0.32 | High | 819 | 27 | 19 | 46 | 30685 | 25480 | 4410 | 23
53QDMT36-718 | 0.32 | High | 819 | 27 | 19 | 52 | 28625 | 24410 | 4590 | 23
53QDMT36-718 | 0.32 | High | 819 | 32 | 23 | 35 | 35450 | 31200 | 4320 | 23
53QDMT36-718 | 0.32 | High | 819 | 32 | 23 | 43 | 32725 | 30425 | 4490 | 23
53QDMT36-718 | 0.32 | High | 819 | 32 | 23 | 46 | 31725 | 30155 | 4535 | 23
53QDMT36-718 | 0.32 | High | 819 | 32 | 23 | 52 | 29730 | 29610 | 4625 | 23
53QDMT36-718 | 0.32 | Medium | 427 | 21 | 15 | 35 | 30450 | 23330 | 3755 | 23
53QDMT36-718 | 0.32 | Medium | 427 | 21 | 15 | 43 | 29135 | 23450 | 3875 | 23
53QDMT36-718 | 0.32 | Medium | 427 | 21 | 15 | 46 | 28490 | 21105 | 3920 | 23
53QDMT36-718 | 0.32 | Medium | 427 | 21 | 15 | 52 | 27210 | 22765 | 4005 | 23
53QDMT36-718 | 0.32 | Medium | 427 | 24 | 17 | 35 | 31420 | 24380 | 3905 | 23
53QDMT36-718 | 0.32 | Medium | 427 | 24 | 17 | 43 | 29460 | 23725 | 4115 | 23
53QDMT36-718 | 0.32 | Medium | 427 | 24 | 17 | 46 | 27585 | 22470 | 4190 | 23
53QDMT36-718 | 0.32 | Medium | 427 | 24 | 17 | 52 | 27495 | 22945 | 4345 | 23
53QDMT36-718 | 0.32 | Medium | 427 | 27 | 19 | 35 | 32720 | 24460 | 3990 | 23
53QDMT36-718 | 0.32 | Medium | 427 | 27 | 19 | 43 | 30450 | 23935 | 4190 | 23
53QDMT36-718 | 0.32 | Medium | 427 | 27 | 19 | 46 | 29460 | 23445 | 4280 | 23
53QDMT36-718 | 0.32 | Medium | 427 | 27 | 19 | 52 | 27480 | 22460 | 4455 | 23
53QDMT36-718 | 0.32 | Medium | 427 | 32 | 23 | 35 | 34035 | 28705 | 4190 | 23
53QDMT36-718 | 0.32 | Medium | 427 | 32 | 23 | 43 | 31420 | 27995 | 4355 | 23
53QDMT36-718 | 0.32 | Medium | 427 | 32 | 23 | 46 | 30460 | 27745 | 4400 | 23
53QDMT36-718 | 0.32 | Medium | 427 | 32 | 23 | 52 | 28545 | 27245 | 4485 | 23
53QDMT36-718 | 0.32 | Low | 327 | 21 | 15 | 35 | 29180 | 21555 | 3600 | 23
53QDMT36-718 | 0.32 | Low | 327 | 21 | 15 | 43 | 27920 | 21665 | 3715 | 23
53QDMT36-718 | 0.32 | Low | 327 | 21 | 15 | 46 | 27305 | 19500 | 3760 | 23
53QDMT36-718 | 0.32 | Low | 327 | 21 | 15 | 52 | 26075 | 21035 | 3840 | 23
53QDMT36-718 | 0.32 | Low | 327 | 24 | 17 | 35 | 30110 | 22525 | 3745 | 23
53QDMT36-718 | 0.32 | Low | 327 | 24 | 17 | 43 | 28230 | 21920 | 3945 | 23
53QDMT36-718 | 0.32 | Low | 327 | 24 | 17 | 46 | 26435 | 20760 | 4020 | 23
53QDMT36-718 | 0.32 | Low | 327 | 24 | 17 | 52 | 26350 | 21200 | 4165 | 23
53QDMT36-718 | 0.32 | Low | 327 | 27 | 19 | 35 | 31355 | 22600 | 3830 | 23
53QDMT36-718 | 0.32 | Low | 327 | 27 | 19 | 43 | 29180 | 22115 | 4020 | 23
53QDMT36-718 | 0.32 | Low | 327 | 27 | 19 | 46 | 28230 | 21660 | 4100 | 23
53QDMT36-718 | 0.32 | Low | 327 | 27 | 19 | 52 | 26335 | 20750 | 4270 | 23
53QDMT36-718 | 0.32 | Low | 327 | 21 | 23 | 35 | 32615 | 26520 | 4020 | 23
53QDMT36-718 | 0.32 | Low | 327 | 21 | 23 | 43 | 30110 | 25865 | 4175 | 23
53QDMT36-718 | 0.32 | Low | 327 | 21 | 23 | 46 | 29190 | 25635 | 4220 | 23
53QDMT36-718 | 0.32 | Low | 327 | 21 | 23 | 52 | 27355 | 25170 | 4300 | 23
53QDMT42-718 | 0 | High | 1370 | 21 | 15 | 35 | 37200 | 29775 | 4280 | 24
53QDMT42-718 | 0 | High | 1370 | 21 | 15 | 43 | 35600 | 30000 | 4410 | 24
53QDMT42-718 | 0 | High | 1370 | 21 | 15 | 46 | 34800 | 29585 | 4455 | 24
53QDMT42-718 | 0 | High | 1370 | 21 | 15 | 52 | 33200 | 28755 | 4545 | 24
53QDMT42-718 | 0 | High | 1370 | 24 | 17 | 35 | 38400 | 31115 | 4465 | 24
53QDMT42-718 | 0 | High | 1370 | 24 | 17 | 43 | 36000 | 30230 | 4695 | 24
53QDMT42-718 | 0 | High | 1370 | 24 | 17 | 46 | 35200 | 29920 | 4780 | 24
53QDMT42-718 | 0 | High | 1370 | 24 | 17 | 52 | 33600 | 29300 | 4950 | 24
53QDMT42-718 | 0 | High | 1370 | 27 | 19 | 35 | 40000 | 31200 | 4555 | 24
53QDMT42-718 | 0 | High | 1370 | 27 | 19 | 43 | 37200 | 30515 | 4785 | 24
53QDMT42-718 | 0 | High | 1370 | 27 | 19 | 46 | 36000 | 29880 | 4870 | 24
53QDMT42-718 | 0 | High | 1370 | 27 | 19 | 52 | 33600 | 28610 | 5040 | 24
53QDMT42-718 | 0 | High | 1370 | 32 | 23 | 35 | 41600 | 36600 | 4780 | 24
53QDMT42-718 | 0 | High | 1370 | 32 | 23 | 43 | 38400 | 35715 | 4965 | 24
53QDMT42-718 | 0 | High | 1370 | 32 | 23 | 46 | 37200 | 35335 | 5015 | 24
53QDMT42-718 | 0 | High | 1370 | 32 | 23 | 52 | 34800 | 34575 | 5115 | 24
53QDMT42-718 | 0 | Medium | 880 | 21 | 15 | 35 | 35715 | 27395 | 4150 | 24
53QDMT42-718 | 0 | Medium | 880 | 21 | 15 | 43 | 34180 | 27600 | 4270 | 24
53QDMT42-718 | 0 | Medium | 880 | 21 | 15 | 46 | 33410 | 27220 | 4315 | 24
53QDMT42-718 | 0 | Medium | 880 | 21 | 15 | 52 | 31875 | 26455 | 4405 | 24
53QDMT42-718 | 0 | Medium | 880 | 24 | 17 | 35 | 36865 | 28630 | 4330 | 24
53QDMT42-718 | 0 | Medium | 880 | 24 | 17 | 43 | 34560 | 27815 | 4540 | 24
53QDMT42-718 | 0 | Medium | 880 | 24 | 17 | 46 | 33795 | 27530 | 4625 | 24
53QDMT42-718 | 0 | Medium | 880 | 24 | 17 | 52 | 32260 | 26960 | 4795 | 24
53QDMT42-718 | 0 | Medium | 880 | 27 | 19 | 35 | 38400 | 28705 | 4420 | 24
53QDMT42-718 | 0 | Medium | 880 | 27 | 19 | 43 | 35715 | 28075 | 4630 | 24
53QDMT42-718 | 0 | Medium | 880 | 27 | 19 | 46 | 34560 | 27490 | 4715 | 24
53QDMT42-718 | 0 | Medium | 880 | 27 | 19 | 52 | 32260 | 26325 | 4885 | 24
53QDMT42-718 | 0 | Medium | 880 | 32 | 23 | 35 | 39940 | 33675 | 4640 | 24
53QDMT42-718 | 0 | Medium | 880 | 32 | 23 | 43 | 36865 | 32860 | 4800 | 24
53QDMT42-718 | 0 | Medium | 880 | 32 | 23 | 46 | 35715 | 32510 | 4850 | 24
53QDMT42-718 | 0 | Medium | 880 | 32 | 23 | 52 | 33410 | 31810 | 4950 | 24
53QDMT42-718 | 0 | Low | 715 | 21 | 15 | 35 | 34225 | 25310 | 3980 | 24
53QDMT42-718 | 0 | Low | 715 | 21 | 15 | 43 | 32755 | 25500 | 4105 | 24
53QDMT42-718 | 0 | Low | 715 | 21 | 15 | 46 | 32020 | 25150 | 4145 | 24
53QDMT42-718 | 0 | Low | 715 | 21 | 15 | 52 | 30545 | 24445 | 4225 | 24
53QDMT42-718 | 0 | Low | 715 | 24 | 17 | 35 | 35330 | 26450 | 4155 | 24
53QDMT42-718 | 0 | Low | 715 | 24 | 17 | 43 | 33120 | 25700 | 4370 | 24
53QDMT42-718 | 0 | Low | 715 | 24 | 17 | 46 | 32385 | 25435 | 4450 | 24
53QDMT42-718 | 0 | Low | 715 | 24 | 17 | 52 | 30915 | 24905 | 4610 | 24
53QDMT42-718 | 0 | Low | 715 | 27 | 19 | 35 | 36800 | 26520 | 4235 | 24
53QDMT42-718 | 0 | Low | 715 | 27 | 19 | 43 | 34225 | 25940 | 4455 | 24
53QDMT42-718 | 0 | Low | 715 | 27 | 19 | 46 | 33120 | 25400 | 4535 | 24
53QDMT42-718 | 0 | Low | 715 | 27 | 19 | 52 | 30915 | 24320 | 4695 | 24
53QDMT42-718 | 0 | Low | 715 | 21 | 23 | 35 | 38275 | 31110 | 4445 | 24
53QDMT42-718 | 0 | Low | 715 | 21 | 23 | 43 | 35330 | 30360 | 4625 | 24
53QDMT42-718 | 0 | Low | 715 | 21 | 23 | 46 | 34225 | 30035 | 4670 | 24
53QDMT42-718 | 0 | Low | 715 | 21 | 23 | 52 | 32020 | 29390 | 4760 | 24
53QDMT42-718 | 0.08 | High | 1300 | 21 | 15 | 35 | 36395 | 29135 | 4260 | 24
53QDMT42-718 | 0.08 | High | 1300 | 21 | 15 | 43 | 34830 | 29355 | 4390 | 24
53QDMT42-718 | 0.08 | High | 1300 | 21 | 15 | 46 | 34050 | 28950 | 4435 | 24
53QDMT42-718 | 0.08 | High | 1300 | 21 | 15 | 52 | 32490 | 28140 | 4525 | 24
53QDMT42-718 | 0.08 | High | 1300 | 24 | 17 | 35 | 37570 | 30445 | 4445 | 24
53QDMT42-718 | 0.08 | High | 1300 | 24 | 17 | 43 | 35225 | 29580 | 4670 | 24
53QDMT42-718 | 0.08 | High | 1300 | 24 | 17 | 46 | 34440 | 29275 | 4755 | 24
53QDMT42-718 | 0.08 | High | 1300 | 24 | 17 | 52 | 32880 | 28670 | 4925 | 24
53QDMT42-718 | 0.08 | High | 1300 | 27 | 19 | 35 | 39135 | 30525 | 4530 | 24
53QDMT42-718 | 0.08 | High | 1300 | 27 | 19 | 43 | 36395 | 29860 | 4760 | 24
53QDMT42-718 | 0.08 | High | 1300 | 27 | 19 | 46 | 35225 | 29235 | 4845 | 24
53QDMT42-718 | 0.08 | High | 1300 | 27 | 19 | 52 | 32875 | 27995 | 5015 | 24
53QDMT42-718 | 0.08 | High | 1300 | 32 | 23 | 35 | 40700 | 35810 | 4755 | 24
53QDMT42-718 | 0.08 | High | 1300 | 32 | 23 | 43 | 37570 | 34945 | 4940 | 24
53QDMT42-718 | 0.08 | High | 1300 | 32 | 23 | 46 | 36395 | 34575 | 4990 | 24
53QDMT42-718 | 0.08 | High | 1300 | 32 | 23 | 52 | 34050 | 33695 | 5090 | 24
53QDMT42-718 | 0.08 | Medium | 803 | 21 | 15 | 35 | 34945 | 26805 | 4130 | 24
53QDMT42-718 | 0.08 | Medium | 803 | 21 | 15 | 43 | 33440 | 27005 | 4250 | 24
53QDMT42-718 | 0.08 | Medium | 803 | 21 | 15 | 46 | 32690 | 26635 | 4295 | 24
53QDMT42-718 | 0.08 | Medium | 803 | 21 | 15 | 52 | 31190 | 25890 | 4385 | 24
53QDMT42-718 | 0.08 | Medium | 803 | 24 | 17 | 35 | 36070 | 28010 | 4310 | 24
53QDMT42-718 | 0.08 | Medium | 803 | 24 | 17 | 43 | 33815 | 27215 | 4518 | 24
53QDMT42-718 | 0.08 | Medium | 803 | 24 | 17 | 46 | 33065 | 26935 | 4600 | 24
53QDMT42-718 | 0.08 | Medium | 803 | 24 | 17 | 52 | 31565 | 26380 | 4765 | 24
53QDMT42-718 | 0.08 | Medium | 803 | 27 | 19 | 35 | 37570 | 28085 | 4395 | 24
53QDMT42-718 | 0.08 | Medium | 803 | 27 | 19 | 43 | 34945 | 27470 | 4605 | 24
53QDMT42-718 | 0.08 | Medium | 803 | 27 | 19 | 46 | 33815 | 26900 | 4690 | 24
53QDMT42-718 | 0.08 | Medium | 803 | 27 | 19 | 52 | 31565 | 25755 | 4857 | 24
53QDMT42-718 | 0.08 | Medium | 803 | 32 | 23 | 35 | 39075 | 32950 | 4615 | 24
53QDMT42-718 | 0.08 | Medium | 803 | 32 | 23 | 43 | 36070 | 32150 | 4780 | 24
53QDMT42-718 | 0.08 | Medium | 803 | 32 | 23 | 46 | 34945 | 31810 | 4830 | 24
53QDMT42-718 | 0.08 | Medium | 803 | 32 | 23 | 52 | 32690 | 31000 | 4930 | 24
53QDMT42-718 | 0.08 | Low | 636 | 21 | 15 | 35 | 33485 | 24765 | 3960 | 24
53QDMT42-718 | 0.08 | Low | 636 | 21 | 15 | 43 | 32050 | 24955 | 4085 | 24
53QDMT42-718 | 0.08 | Low | 636 | 21 | 15 | 46 | 31330 | 24610 | 4125 | 24
53QDMT42-718 | 0.08 | Low | 636 | 21 | 15 | 52 | 29890 | 23920 | 4205 | 24
53QDMT42-718 | 0.08 | Low | 636 | 24 | 17 | 35 | 34565 | 25880 | 4135 | 24
53QDMT42-718 | 0.08 | Low | 636 | 24 | 17 | 43 | 32405 | 25145 | 4345 | 24
53QDMT42-718 | 0.08 | Low | 636 | 24 | 17 | 46 | 31395 | 24885 | 4425 | 24
53QDMT42-718 | 0.08 | Low | 636 | 24 | 17 | 52 | 30250 | 24370 | 4585 | 24
53QDMT42-718 | 0.08 | Low | 636 | 27 | 19 | 35 | 36005 | 25950 | 4215 | 24
53QDMT42-718 | 0.08 | Low | 636 | 27 | 19 | 43 | 33485 | 25380 | 4435 | 24
53QDMT42-718 | 0.08 | Low | 636 | 27 | 19 | 46 | 32405 | 24855 | 4515 | 24
53QDMT42-718 | 0.08 | Low | 636 | 27 | 19 | 52 | 30250 | 23795 | 4675 | 24
53QDMT42-718 | 0.08 | Low | 636 | 21 | 23 | 35 | 37445 | 30440 | 4425 | 24
53QDMT42-718 | 0.08 | Low | 636 | 21 | 23 | 43 | 34565 | 29705 | 4600 | 24
53QDMT42-718 | 0.08 | Low | 636 | 21 | 23 | 46 | 33485 | 29390 | 4645 | 24
53QDMT42-718 | 0.08 | Low | 636 | 21 | 23 | 52 | 31100 | 28645 | 4735 | 24
53QDMT42-718 | 0.12 | High | 1255 | 21 | 15 | 35 | 35995 | 28810 | 4250 | 24
53QDMT42-718 | 0.12 | High | 1255 | 21 | 15 | 43 | 34445 | 29030 | 4380 | 24
53QDMT42-718 | 0.12 | High | 1255 | 21 | 15 | 46 | 33675 | 28630 | 4425 | 24
53QDMT42-718 | 0.12 | High | 1255 | 21 | 15 | 52 | 32135 | 27830 | 4515 | 24
53QDMT42-718 | 0.12 | High | 1255 | 24 | 17 | 35 | 37155 | 30105 | 4435 | 24
53QDMT42-718 | 0.12 | High | 1255 | 24 | 17 | 43 | 34835 | 29255 | 4660 | 24
53QDMT42-718 | 0.12 | High | 1255 | 24 | 17 | 46 | 34065 | 28955 | 4745 | 24
53QDMT42-718 | 0.12 | High | 1255 | 24 | 17 | 52 | 32525 | 28355 | 4915 | 24
53QDMT42-718 | 0.12 | High | 1255 | 27 | 19 | 35 | 38700 | 30190 | 4515 | 24
53QDMT42-718 | 0.12 | High | 1255 | 27 | 19 | 43 | 35995 | 29530 | 4745 | 24
53QDMT42-718 | 0.12 | High | 1255 | 27 | 19 | 46 | 34835 | 28915 | 4830 | 24
53QDMT42-718 | 0.12 | High | 1255 | 27 | 19 | 52 | 32515 | 27685 | 5000 | 24
53QDMT42-718 | 0.12 | High | 1255 | 32 | 23 | 35 | 40250 | 35415 | 4745 | 24
53QDMT42-718 | 0.12 | High | 1255 | 32 | 23 | 43 | 37155 | 34560 | 4930 | 24
53QDMT42-718 | 0.12 | High | 1255 | 32 | 23 | 46 | 35995 | 34190 | 4980 | 24
53QDMT42-718 | 0.12 | High | 1255 | 32 | 23 | 52 | 33675 | 33450 | 5080 | 24
53QDMT42-718 | 0.12 | Medium | 770 | 21 | 15 | 35 | 34555 | 26510 | 4125 | 24
53QDMT42-718 | 0.12 | Medium | 770 | 21 | 15 | 43 | 33070 | 26710 | 4240 | 24
53QDMT42-718 | 0.12 | Medium | 770 | 21 | 15 | 46 | 32330 | 26340 | 4285 | 24
53QDMT42-718 | 0.12 | Medium | 770 | 21 | 15 | 52 | 30850 | 25605 | 4375 | 24
53QDMT42-718 | 0.12 | Medium | 770 | 24 | 17 | 35 | 35670 | 27700 | 4305 | 24
53QDMT42-718 | 0.12 | Medium | 770 | 24 | 17 | 43 | 33445 | 26915 | 4510 | 24
53QDMT42-718 | 0.12 | Medium | 770 | 24 | 17 | 46 | 32705 | 26640 | 4590 | 24
53QDMT42-718 | 0.12 | Medium | 770 | 24 | 17 | 52 | 31225 | 26090 | 4750 | 24
53QDMT42-718 | 0.12 | Medium | 770 | 27 | 19 | 35 | 37155 | 27775 | 4380 | 24
53QDMT42-718 | 0.12 | Medium | 770 | 27 | 19 | 43 | 34555 | 27170 | 4590 | 24
53QDMT42-718 | 0.12 | Medium | 770 | 27 | 19 | 46 | 33445 | 26605 | 4675 | 24
53QDMT42-718 | 0.12 | Medium | 770 | 27 | 19 | 52 | 31215 | 25470 | 4845 | 24
53QDMT42-718 | 0.12 | Medium | 770 | 32 | 23 | 35 | 38645 | 32585 | 4605 | 24
53QDMT42-718 | 0.12 | Medium | 770 | 32 | 23 | 43 | 35670 | 31795 | 4770 | 24
53QDMT42-718 | 0.12 | Medium | 770 | 32 | 23 | 46 | 34555 | 31455 | 4820 | 24
53QDMT42-718 | 0.12 | Medium | 770 | 32 | 23 | 52 | 32330 | 30775 | 4920 | 24
53QDMT42-718 | 0.12 | Low | 594 | 21 | 15 | 35 | 33115 | 24490 | 3950 | 24
53QDMT42-718 | 0.12 | Low | 594 | 21 | 15 | 43 | 31690 | 24680 | 4070 | 24
53QDMT42-718 | 0.12 | Low | 594 | 21 | 15 | 46 | 30985 | 24340 | 4110 | 24
53QDMT42-718 | 0.12 | Low | 594 | 21 | 15 | 52 | 29565 | 23660 | 4190 | 24
53QDMT42-718 | 0.12 | Low | 594 | 24 | 17 | 35 | 34185 | 25590 | 4125 | 24
53QDMT42-718 | 0.12 | Low | 594 | 24 | 17 | 43 | 32050 | 24870 | 4325 | 24
53QDMT42-718 | 0.12 | Low | 594 | 24 | 17 | 46 | 31340 | 24615 | 4405 | 24
53QDMT42-718 | 0.12 | Low | 594 | 24 | 17 | 52 | 29925 | 24105 | 4565 | 24
53QDMT42-718 | 0.12 | Low | 594 | 27 | 19 | 35 | 35605 | 25665 | 4205 | 24
53QDMT42-718 | 0.12 | Low | 594 | 27 | 19 | 43 | 33115 | 25105 | 4425 | 24
53QDMT42-718 | 0.12 | Low | 594 | 27 | 19 | 46 | 32050 | 24580 | 4505 | 24
53QDMT42-718 | 0.12 | Low | 594 | 27 | 19 | 52 | 29915 | 23535 | 4665 | 24
53QDMT42-718 | 0.12 | Low | 594 | 21 | 23 | 35 | 37030 | 30105 | 4415 | 24
53QDMT42-718 | 0.12 | Low | 594 | 21 | 23 | 43 | 34185 | 29380 | 4585 | 24
53QDMT42-718 | 0.12 | Low | 594 | 21 | 23 | 46 | 33115 | 29065 | 4630 | 24
53QDMT42-718 | 0.12 | Low | 594 | 21 | 23 | 52 | 30985 | 28435 | 4720 | 24
53QDMT42-718 | 0.16 | High | 1223 | 21 | 15 | 35 | 35590 | 28488 | 4235 | 24
53QDMT42-718 | 0.16 | High | 1223 | 21 | 15 | 43 | 34060 | 28705 | 4365 | 24
53QDMT42-718 | 0.16 | High | 1223 | 21 | 15 | 46 | 33300 | 28310 | 4410 | 24
53QDMT42-718 | 0.16 | High | 1223 | 21 | 15 | 52 | 31775 | 27520 | 4500 | 24
53QDMT42-718 | 0.16 | High | 1223 | 24 | 17 | 35 | 36740 | 29770 | 4420 | 24
53QDMT42-718 | 0.16 | High | 1223 | 24 | 17 | 43 | 34445 | 28925 | 4645 | 24
53QDMT42-718 | 0.16 | High | 1223 | 24 | 17 | 46 | 33680 | 28630 | 4730 | 24
53QDMT42-718 | 0.16 | High | 1223 | 24 | 17 | 52 | 32155 | 28035 | 4900 | 24
53QDMT42-718 | 0.16 | High | 1223 | 27 | 19 | 35 | 38265 | 29850 | 4500 | 24
53QDMT42-718 | 0.16 | High | 1223 | 27 | 19 | 43 | 35590 | 29200 | 4730 | 24
53QDMT42-718 | 0.16 | High | 1223 | 27 | 19 | 46 | 34445 | 28590 | 4815 | 24
53QDMT42-718 | 0.16 | High | 1223 | 27 | 19 | 52 | 32150 | 27375 | 4985 | 24
53QDMT42-718 | 0.16 | High | 1223 | 32 | 23 | 35 | 39800 | 35020 | 4730 | 24
53QDMT42-718 | 0.16 | High | 1223 | 32 | 23 | 43 | 36740 | 34170 | 4915 | 24
53QDMT42-718 | 0.16 | High | 1223 | 32 | 23 | 46 | 35590 | 33810 | 4965 | 24
53QDMT42-718 | 0.16 | High | 1223 | 32 | 23 | 52 | 33300 | 32815 | 5065 | 24
53QDMT42-718 | 0.16 | Medium | 733 | 21 | 15 | 35 | 34170 | 26215 | 4110 | 24
53QDMT42-718 | 0.16 | Medium | 733 | 21 | 15 | 43 | 32700 | 26410 | 4225 | 24
53QDMT42-718 | 0.16 | Medium | 733 | 21 | 15 | 46 | 31970 | 26050 | 4270 | 24
53QDMT42-718 | 0.16 | Medium | 733 | 21 | 15 | 52 | 30505 | 25320 | 4360 | 24
53QDMT42-718 | 0.16 | Medium | 733 | 24 | 17 | 35 | 35270 | 27390 | 4290 | 24
53QDMT42-718 | 0.16 | Medium | 733 | 24 | 17 | 43 | 33070 | 26615 | 4495 | 24
53QDMT42-718 | 0.16 | Medium | 733 | 24 | 17 | 46 | 32335 | 26340 | 4575 | 24
53QDMT42-718 | 0.16 | Medium | 733 | 24 | 17 | 52 | 30870 | 25800 | 4735 | 24
53QDMT42-718 | 0.16 | Medium | 733 | 27 | 19 | 35 | 36740 | 27465 | 4365 | 24
53QDMT42-718 | 0.16 | Medium | 733 | 27 | 19 | 43 | 34170 | 26865 | 4575 | 24
53QDMT42-718 | 0.16 | Medium | 733 | 27 | 19 | 46 | 33070 | 26305 | 4660 | 24
53QDMT42-718 | 0.16 | Medium | 733 | 27 | 19 | 52 | 30865 | 25185 | 4828 | 24
53QDMT42-718 | 0.16 | Medium | 733 | 32 | 23 | 35 | 38210 | 32220 | 4590 | 24
53QDMT42-718 | 0.16 | Medium | 733 | 32 | 23 | 43 | 35270 | 31440 | 4755 | 24
53QDMT42-718 | 0.16 | Medium | 733 | 32 | 23 | 46 | 34170 | 31105 | 4805 | 24
53QDMT42-718 | 0.16 | Medium | 733 | 32 | 23 | 52 | 31965 | 30190 | 4905 | 24
53QDMT42-718 | 0.16 | Low | 548 | 21 | 15 | 35 | 32745 | 24215 | 3940 | 24
53QDMT42-718 | 0.16 | Low | 548 | 21 | 15 | 43 | 31340 | 24405 | 4060 | 24
53QDMT42-718 | 0.16 | Low | 548 | 21 | 15 | 46 | 30640 | 24070 | 4100 | 24
53QDMT42-718 | 0.16 | Low | 548 | 21 | 15 | 52 | 29235 | 23395 | 4180 | 24
53QDMT42-718 | 0.16 | Low | 548 | 24 | 17 | 35 | 33800 | 25305 | 4115 | 24
53QDMT42-718 | 0.16 | Low | 548 | 24 | 17 | 43 | 31690 | 24590 | 4315 | 24
53QDMT42-718 | 0.16 | Low | 548 | 24 | 17 | 46 | 30400 | 24335 | 4395 | 24
53QDMT42-718 | 0.16 | Low | 548 | 24 | 17 | 52 | 29585 | 23830 | 4555 | 24
53QDMT42-718 | 0.16 | Low | 548 | 27 | 19 | 35 | 35205 | 25375 | 4190 | 24
53QDMT42-718 | 0.16 | Low | 548 | 27 | 19 | 43 | 32745 | 24820 | 4410 | 24
53QDMT42-718 | 0.16 | Low | 548 | 27 | 19 | 46 | 31690 | 24305 | 4490 | 24
53QDMT42-718 | 0.16 | Low | 548 | 27 | 19 | 52 | 29580 | 23270 | 4650 | 24
53QDMT42-718 | 0.16 | Low | 548 | 21 | 23 | 35 | 36615 | 29770 | 4400 | 24
53QDMT42-718 | 0.16 | Low | 548 | 21 | 23 | 43 | 33800 | 29050 | 4570 | 24
53QDMT42-718 | 0.16 | Low | 548 | 21 | 23 | 46 | 32745 | 28740 | 4615 | 24
53QDMT42-718 | 0.16 | Low | 548 | 21 | 23 | 52 | 30175 | 27895 | 4705 | 24
53QDMT42-718 | 0.2 | High | 1187 | 21 | 15 | 35 | 35185 | 28165 | 4220 | 24
53QDMT42-718 | 0.2 | High | 1187 | 21 | 15 | 43 | 33675 | 28380 | 4350 | 24
53QDMT42-718 | 0.2 | High | 1187 | 21 | 15 | 46 | 32920 | 27990 | 4395 | 24
53QDMT42-718 | 0.2 | High | 1187 | 21 | 15 | 52 | 31410 | 27210 | 4485 | 24
53QDMT42-718 | 0.2 | High | 1187 | 24 | 17 | 35 | 36320 | 29430 | 4405 | 24
53QDMT42-718 | 0.2 | High | 1187 | 24 | 17 | 43 | 34050 | 28595 | 4630 | 24
53QDMT42-718 | 0.2 | High | 1187 | 24 | 17 | 46 | 33295 | 28300 | 4715 | 24
53QDMT42-718 | 0.2 | High | 1187 | 24 | 17 | 52 | 31785 | 27710 | 4885 | 24
53QDMT42-718 | 0.2 | High | 1187 | 27 | 19 | 35 | 37830 | 29510 | 4485 | 24
53QDMT42-718 | 0.2 | High | 1187 | 27 | 19 | 43 | 35185 | 28865 | 4715 | 24
53QDMT42-718 | 0.2 | High | 1187 | 27 | 19 | 46 | 34050 | 28265 | 4800 | 24
53QDMT42-718 | 0.2 | High | 1187 | 27 | 19 | 52 | 31780 | 27065 | 4970 | 24
53QDMT42-718 | 0.2 | High | 1187 | 32 | 23 | 35 | 39345 | 34620 | 4715 | 24
53QDMT42-718 | 0.2 | High | 1187 | 32 | 23 | 43 | 36320 | 33780 | 4900 | 24
53QDMT42-718 | 0.2 | High | 1187 | 32 | 23 | 46 | 35185 | 33425 | 4950 | 24
53QDMT42-718 | 0.2 | High | 1187 | 32 | 23 | 52 | 32915 | 32175 | 5050 | 24
53QDMT42-718 | 0.2 | Medium | 693 | 21 | 15 | 35 | 33780 | 25915 | 4095 | 24
53QDMT42-718 | 0.2 | Medium | 693 | 21 | 15 | 43 | 32330 | 26110 | 4210 | 24
53QDMT42-718 | 0.2 | Medium | 693 | 21 | 15 | 46 | 31605 | 25755 | 4255 | 24
53QDMT42-718 | 0.2 | Medium | 693 | 21 | 15 | 52 | 30155 | 25035 | 4345 | 24
53QDMT42-718 | 0.2 | Medium | 693 | 24 | 17 | 35 | 34870 | 27080 | 4275 | 24
53QDMT42-718 | 0.2 | Medium | 693 | 24 | 17 | 43 | 32690 | 26310 | 4475 | 24
53QDMT42-718 | 0.2 | Medium | 693 | 24 | 17 | 46 | 31965 | 26040 | 4555 | 24
53QDMT42-718 | 0.2 | Medium | 693 | 24 | 17 | 52 | 30515 | 25495 | 4715 | 24
53QDMT42-718 | 0.2 | Medium | 693 | 27 | 19 | 35 | 36320 | 27150 | 4350 | 24
53QDMT42-718 | 0.2 | Medium | 693 | 27 | 19 | 43 | 33780 | 26560 | 4555 | 24
53QDMT42-718 | 0.2 | Medium | 693 | 27 | 19 | 46 | 32690 | 26005 | 4640 | 24
53QDMT42-718 | 0.2 | Medium | 693 | 27 | 19 | 52 | 30510 | 24900 | 4810 | 24
53QDMT42-718 | 0.2 | Medium | 693 | 32 | 23 | 35 | 37775 | 31855 | 4575 | 24
53QDMT42-718 | 0.2 | Medium | 693 | 32 | 23 | 43 | 34870 | 31080 | 4740 | 24
53QDMT42-718 | 0.2 | Medium | 693 | 32 | 23 | 46 | 33780 | 30755 | 4790 | 24
53QDMT42-718 | 0.2 | Medium | 693 | 32 | 23 | 52 | 31600 | 29605 | 4890 | 24
53QDMT42-718 | 0.2 | Low | 491 | 21 | 15 | 35 | 32370 | 23940 | 3925 | 24
53QDMT42-718 | 0.2 | Low | 491 | 21 | 15 | 43 | 30985 | 24125 | 4045 | 24
53QDMT42-718 | 0.2 | Low | 491 | 21 | 15 | 46 | 30290 | 23795 | 4085 | 24
53QDMT42-718 | 0.2 | Low | 491 | 21 | 15 | 52 | 28900 | 23130 | 4165 | 24
53QDMT42-718 | 0.2 | Low | 491 | 24 | 17 | 35 | 33415 | 25015 | 4100 | 24
53QDMT42-718 | 0.2 | Low | 491 | 24 | 17 | 43 | 31330 | 24310 | 4300 | 24
53QDMT42-718 | 0.2 | Low | 491 | 24 | 17 | 46 | 30635 | 24055 | 4380 | 24
53QDMT42-718 | 0.2 | Low | 491 | 24 | 17 | 52 | 29245 | 23555 | 4540 | 24
53QDMT42-718 | 0.2 | Low | 491 | 27 | 19 | 35 | 34805 | 25085 | 4175 | 24
53QDMT42-718 | 0.2 | Low | 491 | 27 | 19 | 43 | 32370 | 24535 | 4395 | 24
53QDMT42-718 | 0.2 | Low | 491 | 27 | 19 | 46 | 31330 | 24025 | 4475 | 24
53QDMT42-718 | 0.2 | Low | 491 | 27 | 19 | 52 | 29240 | 23005 | 4635 | 24
53QDMT42-718 | 0.2 | Low | 491 | 21 | 23 | 35 | 36200 | 29430 | 4385 | 24
53QDMT42-718 | 0.2 | Low | 491 | 21 | 23 | 43 | 33415 | 28715 | 4550 | 24
53QDMT42-718 | 0.2 | Low | 491 | 21 | 23 | 46 | 32370 | 28415 | 4595 | 24
53QDMT42-718 | 0.2 | Low | 491 | 21 | 23 | 52 | 29365 | 27350 | 4685 | 24
53QDMT42-718 | 0.24 | High | 1151 | 21 | 15 | 35 | 34780 | 27845 | 4205 | 25
53QDMT42-718 | 0.24 | High | 1151 | 21 | 15 | 43 | 33295 | 28060 | 4335 | 25
53QDMT42-718 | 0.24 | High | 1151 | 21 | 15 | 46 | 31570 | 26840 | 4380 | 25
53QDMT42-718 | 0.24 | High | 1151 | 21 | 15 | 52 | 28120 | 24355 | 4470 | 25
53QDMT42-718 | 0.24 | High | 1151 | 24 | 17 | 35 | 35905 | 29095 | 4390 | 25
53QDMT42-718 | 0.24 | High | 1151 | 24 | 17 | 43 | 33660 | 28270 | 4620 | 25
53QDMT42-718 | 0.24 | High | 1151 | 24 | 17 | 46 | 32910 | 27975 | 4705 | 25
53QDMT42-718 | 0.24 | High | 1151 | 24 | 17 | 52 | 31410 | 27390 | 4875 | 25
53QDMT42-718 | 0.24 | High | 1151 | 27 | 19 | 35 | 32395 | 29175 | 4470 | 25
53QDMT42-718 | 0.24 | High | 1151 | 27 | 19 | 43 | 34780 | 28535 | 4695 | 25
53QDMT42-718 | 0.24 | High | 1151 | 27 | 19 | 46 | 33610 | 27900 | 4780 | 25
53QDMT42-718 | 0.24 | High | 1151 | 27 | 19 | 52 | 31270 | 26630 | 4950 | 25
53QDMT42-718 | 0.24 | High | 1151 | 32 | 23 | 35 | 38895 | 34250 | 4700 | 25
53QDMT42-718 | 0.24 | High | 1151 | 32 | 23 | 43 | 35905 | 33400 | 4885 | 25
53QDMT42-718 | 0.24 | High | 1151 | 32 | 23 | 46 | 34780 | 33040 | 4935 | 25
53QDMT42-718 | 0.24 | High | 1151 | 32 | 23 | 52 | 32530 | 32320 | 5035 | 25
53QDMT42-718 | 0.24 | Medium | 653 | 21 | 15 | 35 | 33390 | 25620 | 4080 | 25
53QDMT42-718 | 0.24 | Medium | 653 | 21 | 15 | 43 | 31965 | 25820 | 4205 | 25
53QDMT42-718 | 0.24 | Medium | 653 | 21 | 15 | 46 | 30310 | 24695 | 4250 | 25
53QDMT42-718 | 0.24 | Medium | 653 | 21 | 15 | 52 | 26995 | 22410 | 4335 | 25
53QDMT42-718 | 0.24 | Medium | 653 | 24 | 17 | 35 | 34470 | 26770 | 4260 | 25
53QDMT42-718 | 0.24 | Medium | 653 | 24 | 17 | 43 | 32315 | 26010 | 4480 | 25
53QDMT42-718 | 0.24 | Medium | 653 | 24 | 17 | 46 | 31595 | 25740 | 4565 | 25
53QDMT42-718 | 0.24 | Medium | 653 | 24 | 17 | 52 | 30155 | 25200 | 4730 | 25
53QDMT42-718 | 0.24 | Medium | 653 | 27 | 19 | 35 | 35903 | 26840 | 4335 | 25
53QDMT42-718 | 0.24 | Medium | 653 | 27 | 19 | 43 | 33390 | 26255 | 4555 | 25
53QDMT42-718 | 0.24 | Medium | 653 | 27 | 19 | 46 | 32315 | 25670 | 4640 | 25
53QDMT42-718 | 0.24 | Medium | 653 | 27 | 19 | 52 | 30020 | 24500 | 4800 | 25
53QDMT42-718 | 0.24 | Medium | 653 | 32 | 23 | 35 | 37340 | 31490 | 4560 | 25
53QDMT42-718 | 0.24 | Medium | 653 | 32 | 23 | 43 | 34475 | 30730 | 4740 | 25
53QDMT42-718 | 0.24 | Medium | 653 | 32 | 23 | 46 | 33390 | 31720 | 4790 | 25
53QDMT42-718 | 0.24 | Medium | 653 | 32 | 23 | 52 | 31230 | 29735 | 4885 | 25
53QDMT42-718 | 0.24 | Low | 434 | 21 | 15 | 35 | 32000 | 23670 | 3915 | 25
53QDMT42-718 | 0.24 | Low | 434 | 21 | 15 | 43 | 30635 | 23855 | 4030 | 25
53QDMT42-718 | 0.24 | Low | 434 | 21 | 15 | 46 | 29045 | 22815 | 4075 | 25
53QDMT42-718 | 0.24 | Low | 434 | 21 | 15 | 52 | 25870 | 20705 | 4160 | 25
53QDMT42-718 | 0.24 | Low | 434 | 24 | 17 | 35 | 33035 | 24735 | 4085 | 25
53QDMT42-718 | 0.24 | Low | 434 | 24 | 17 | 43 | 30970 | 24030 | 4300 | 25
53QDMT42-718 | 0.24 | Low | 434 | 24 | 17 | 46 | 30280 | 23780 | 4375 | 25
53QDMT42-718 | 0.24 | Low | 434 | 24 | 17 | 52 | 28900 | 23285 | 4535 | 25
53QDMT42-718 | 0.24 | Low | 434 | 27 | 19 | 35 | 34405 | 24800 | 4160 | 25
53QDMT42-718 | 0.24 | Low | 434 | 27 | 19 | 43 | 32000 | 24255 | 4370 | 25
53QDMT42-718 | 0.24 | Low | 434 | 27 | 19 | 46 | 30970 | 23715 | 4445 | 25
53QDMT42-718 | 0.24 | Low | 434 | 27 | 19 | 52 | 28770 | 22640 | 4605 | 25
53QDMT42-718 | 0.24 | Low | 434 | 21 | 23 | 35 | 35785 | 29095 | 4375 | 25
53QDMT42-718 | 0.24 | Low | 434 | 21 | 23 | 43 | 33035 | 28390 | 4545 | 25
53QDMT42-718 | 0.24 | Low | 434 | 21 | 23 | 46 | 32000 | 30730 | 4590 | 25
53QDMT42-718 | 0.24 | Low | 434 | 21 | 23 | 52 | 29930 | 27475 | 4685 | 25
53QDMT42-718 | 0.28 | High | 1115 | 21 | 15 | 35 | 34375 | 27520 | 4190 | 25
53QDMT42-718 | 0.28 | High | 1115 | 21 | 15 | 43 | 32910 | 27740 | 4320 | 25
53QDMT42-718 | 0.28 | High | 1115 | 21 | 15 | 46 | 32175 | 27355 | 4365 | 25
53QDMT42-718 | 0.28 | High | 1115 | 21 | 15 | 52 | 30705 | 26595 | 4455 | 25
53QDMT42-718 | 0.28 | High | 1115 | 24 | 17 | 35 | 35485 | 28760 | 4375 | 25
53QDMT42-718 | 0.28 | High | 1115 | 24 | 17 | 43 | 33265 | 27940 | 4605 | 25
53QDMT42-718 | 0.28 | High | 1115 | 24 | 17 | 46 | 32525 | 27650 | 4690 | 25
53QDMT42-718 | 0.28 | High | 1115 | 24 | 17 | 52 | 31045 | 27075 | 4860 | 25
53QDMT42-718 | 0.28 | High | 1115 | 27 | 19 | 35 | 26960 | 28835 | 4455 | 25
53QDMT42-718 | 0.28 | High | 1115 | 27 | 19 | 43 | 34375 | 28205 | 4680 | 25
53QDMT42-718 | 0.28 | High | 1115 | 27 | 19 | 46 | 33270 | 27620 | 4765 | 25
53QDMT42-718 | 0.28 | High | 1115 | 27 | 19 | 52 | 31060 | 26455 | 4935 | 25
53QDMT42-718 | 0.28 | High | 1115 | 32 | 23 | 35 | 38440 | 33880 | 4685 | 25
53QDMT42-718 | 0.28 | High | 1115 | 32 | 23 | 43 | 35490 | 33015 | 4870 | 25
53QDMT42-718 | 0.28 | High | 1115 | 32 | 23 | 46 | 34380 | 32660 | 4920 | 25
53QDMT42-718 | 0.28 | High | 1115 | 32 | 23 | 52 | 32160 | 31955 | 5020 | 25
53QDMT42-718 | 0.28 | Medium | 613 | 21 | 15 | 35 | 33000 | 25320 | 4065 | 25
53QDMT42-718 | 0.28 | Medium | 613 | 21 | 15 | 43 | 31595 | 25525 | 4190 | 25
53QDMT42-718 | 0.28 | Medium | 613 | 21 | 15 | 46 | 30890 | 25170 | 4235 | 25
53QDMT42-718 | 0.28 | Medium | 613 | 21 | 15 | 52 | 29480 | 24470 | 4320 | 25
53QDMT42-718 | 0.28 | Medium | 613 | 24 | 17 | 35 | 34070 | 26460 | 4245 | 25
53QDMT42-718 | 0.28 | Medium | 613 | 24 | 17 | 43 | 31935 | 25705 | 4470 | 25
53QDMT42-718 | 0.28 | Medium | 613 | 24 | 17 | 46 | 31225 | 25440 | 4550 | 25
53QDMT42-718 | 0.28 | Medium | 613 | 24 | 17 | 52 | 29805 | 24910 | 4715 | 25
53QDMT42-718 | 0.28 | Medium | 613 | 27 | 19 | 35 | 35485 | 26530 | 4320 | 25
53QDMT42-718 | 0.28 | Medium | 613 | 27 | 19 | 43 | 33000 | 25950 | 4540 | 25
53QDMT42-718 | 0.28 | Medium | 613 | 27 | 19 | 46 | 31940 | 25410 | 4625 | 25
53QDMT42-718 | 0.28 | Medium | 613 | 27 | 19 | 52 | 29820 | 24340 | 4790 | 25
53QDMT42-718 | 0.28 | Medium | 613 | 32 | 23 | 35 | 36905 | 31125 | 4545 | 25
53QDMT42-718 | 0.28 | Medium | 613 | 32 | 23 | 43 | 34075 | 30375 | 4725 | 25
53QDMT42-718 | 0.28 | Medium | 613 | 32 | 23 | 46 | 33005 | 30050 | 4775 | 25
53QDMT42-718 | 0.28 | Medium | 613 | 32 | 23 | 52 | 30875 | 29400 | 4870 | 25
53QDMT42-718 | 0.28 | Low | 377 | 21 | 15 | 35 | 31625 | 23395 | 3900 | 25
53QDMT42-718 | 0.28 | Low | 377 | 21 | 15 | 43 | 30280 | 23580 | 4020 | 25
53QDMT42-718 | 0.28 | Low | 377 | 21 | 15 | 46 | 29605 | 23255 | 4060 | 25
53QDMT42-718 | 0.28 | Low | 377 | 21 | 15 | 52 | 28250 | 22610 | 4145 | 25
53QDMT42-718 | 0.28 | Low | 377 | 24 | 17 | 35 | 32650 | 24450 | 4070 | 25
53QDMT42-718 | 0.28 | Low | 377 | 24 | 17 | 43 | 30605 | 23750 | 4285 | 25
53QDMT42-718 | 0.28 | Low | 377 | 24 | 17 | 46 | 29925 | 23505 | 4360 | 25
53QDMT42-718 | 0.28 | Low | 377 | 24 | 17 | 52 | 28565 | 23015 | 4520 | 25
53QDMT42-718 | 0.28 | Low | 377 | 27 | 19 | 35 | 34005 | 24510 | 4145 | 25
53QDMT42-718 | 0.28 | Low | 377 | 27 | 19 | 43 | 31625 | 23975 | 4355 | 25
53QDMT42-718 | 0.28 | Low | 377 | 27 | 19 | 46 | 30610 | 23480 | 4430 | 25
53QDMT42-718 | 0.28 | Low | 377 | 27 | 19 | 52 | 28575 | 22490 | 4590 | 25
53QDMT42-718 | 0.28 | Low | 377 | 21 | 23 | 35 | 35365 | 28760 | 4360 | 25
53QDMT42-718 | 0.28 | Low | 377 | 21 | 23 | 43 | 32655 | 28065 | 4530 | 25
53QDMT42-718 | 0.28 | Low | 377 | 21 | 23 | 46 | 31630 | 27765 | 4575 | 25
53QDMT42-718 | 0.28 | Low | 377 | 21 | 23 | 52 | 29590 | 27165 | 4670 | 25
53QDMT42-718 | 0.32 | High | 1079 | 21 | 15 | 35 | 33970 | 27195 | 4175 | 25
53QDMT42-718 | 0.32 | High | 1079 | 21 | 15 | 43 | 32520 | 27410 | 4305 | 25
53QDMT42-718 | 0.32 | High | 1079 | 21 | 15 | 46 | 31790 | 27030 | 4350 | 25
53QDMT42-718 | 0.32 | High | 1079 | 21 | 15 | 52 | 30325 | 26270 | 4440 | 25
53QDMT42-718 | 0.32 | High | 1079 | 24 | 17 | 35 | 35070 | 28420 | 4360 | 25
53QDMT42-718 | 0.32 | High | 1079 | 24 | 17 | 43 | 32875 | 27610 | 4585 | 25
53QDMT42-718 | 0.32 | High | 1079 | 24 | 17 | 46 | 32140 | 27320 | 4670 | 25
53QDMT42-718 | 0.32 | High | 1079 | 24 | 17 | 52 | 30675 | 26745 | 4840 | 25
53QDMT42-718 | 0.32 | High | 1079 | 27 | 19 | 35 | 36525 | 28495 | 4440 | 25
53QDMT42-718 | 0.32 | High | 1079 | 27 | 19 | 43 | 33970 | 27870 | 4670 | 25
53QDMT42-718 | 0.32 | High | 1079 | 27 | 19 | 46 | 32875 | 27290 | 4755 | 25
53QDMT42-718 | 0.32 | High | 1079 | 27 | 19 | 52 | 30680 | 26130 | 4925 | 25
53QDMT42-718 | 0.32 | High | 1079 | 32 | 23 | 35 | 37990 | 33430 | 4670 | 25
53QDMT42-718 | 0.32 | High | 1079 | 32 | 23 | 43 | 35070 | 32620 | 4855 | 25
53QDMT42-718 | 0.32 | High | 1079 | 32 | 23 | 46 | 33970 | 32275 | 4905 | 25
53QDMT42-718 | 0.32 | High | 1079 | 32 | 23 | 52 | 31775 | 31065 | 5005 | 25
53QDMT42-718 | 0.32 | Medium | 573 | 21 | 15 | 35 | 32615 | 25020 | 4050 | 25
53QDMT42-718 | 0.32 | Medium | 573 | 21 | 15 | 43 | 31220 | 25220 | 4175 | 25
53QDMT42-718 | 0.32 | Medium | 573 | 21 | 15 | 46 | 30520 | 24870 | 4220 | 25
53QDMT42-718 | 0.32 | Medium | 573 | 21 | 15 | 52 | 29115 | 24170 | 4310 | 25
53QDMT42-718 | 0.32 | Medium | 573 | 24 | 17 | 35 | 33670 | 26150 | 4230 | 25
53QDMT42-718 | 0.32 | Medium | 573 | 24 | 17 | 43 | 31560 | 25405 | 4405 | 25
53QDMT42-718 | 0.32 | Medium | 573 | 24 | 17 | 46 | 30855 | 25153 | 4530 | 25
53QDMT42-718 | 0.32 | Medium | 573 | 24 | 17 | 52 | 29450 | 24605 | 4695 | 25
53QDMT42-718 | 0.32 | Medium | 573 | 27 | 19 | 35 | 35065 | 26215 | 4310 | 25
53QDMT42-718 | 0.32 | Medium | 573 | 27 | 19 | 43 | 32615 | 25640 | 4530 | 25
53QDMT42-718 | 0.32 | Medium | 573 | 27 | 19 | 46 | 31560 | 25110 | 4615 | 25
53QDMT42-718 | 0.32 | Medium | 573 | 27 | 19 | 52 | 29455 | 24040 | 4780 | 25
53QDMT42-718 | 0.32 | Medium | 573 | 32 | 23 | 35 | 36470 | 30760 | 4530 | 25
53QDMT42-718 | 0.32 | Medium | 573 | 32 | 23 | 43 | 33670 | 30010 | 4710 | 25
53QDMT42-718 | 0.32 | Medium | 573 | 32 | 23 | 46 | 32615 | 29695 | 4760 | 25
53QDMT42-718 | 0.32 | Medium | 573 | 32 | 23 | 52 | 30505 | 28580 | 4855 | 25
53QDMT42-718 | 0.32 | Low | 320 | 21 | 15 | 35 | 31255 | 23120 | 3885 | 25
53QDMT42-718 | 0.32 | Low | 320 | 21 | 15 | 43 | 29920 | 23300 | 4005 | 25
53QDMT42-718 | 0.32 | Low | 320 | 21 | 15 | 46 | 29250 | 22980 | 4045 | 25
53QDMT42-718 | 0.32 | Low | 320 | 21 | 15 | 52 | 27900 | 22330 | 4130 | 25
53QDMT42-718 | 0.32 | Low | 320 | 24 | 17 | 35 | 32265 | 24160 | 4055 | 25
53QDMT42-718 | 0.32 | Low | 320 | 24 | 17 | 43 | 30245 | 23470 | 4265 | 25
53QDMT42-718 | 0.32 | Low | 320 | 24 | 17 | 46 | 29570 | 23225 | 4345 | 25
53QDMT42-718 | 0.32 | Low | 320 | 24 | 17 | 52 | 28225 | 22735 | 4500 | 25
53QDMT42-718 | 0.32 | Low | 320 | 27 | 19 | 35 | 33605 | 24225 | 4130 | 25
53QDMT42-718 | 0.32 | Low | 320 | 27 | 19 | 43 | 31255 | 23670 | 4345 | 25
53QDMT42-718 | 0.32 | Low | 320 | 27 | 19 | 46 | 30245 | 23200 | 4425 | 25
53QDMT42-718 | 0.32 | Low | 320 | 27 | 19 | 52 | 28230 | 22215 | 4580 | 25
53QDMT42-718 | 0.32 | Low | 320 | 21 | 23 | 35 | 34955 | 28420 | 4345 | 25
53QDMT42-718 | 0.32 | Low | 320 | 21 | 23 | 43 | 32265 | 27730 | 4515 | 25
53QDMT42-718 | 0.32 | Low | 320 | 21 | 23 | 46 | 31255 | 27435 | 4565 | 25
53QDMT42-718 | 0.32 | Low | 320 | 21 | 23 | 52 | 29235 | 26405 | 4655 | 25
53QDMT42-718 | 0.36 | High | 1043 | 21 | 15 | 35 | 33565 | 26873 | 4160 | 25
53QDMT42-718 | 0.36 | High | 1043 | 21 | 15 | 43 | 32133 | 27085 | 4290 | 25
53QDMT42-718 | 0.36 | High | 1043 | 21 | 15 | 46 | 31413 | 26710 | 4335 | 25
53QDMT42-718 | 0.36 | High | 1043 | 21 | 15 | 52 | 29965 | 25960 | 4425 | 25
53QDMT42-718 | 0.36 | High | 1043 | 24 | 17 | 35 | 34655 | 28085 | 4345 | 25
53QDMT42-718 | 0.36 | High | 1043 | 24 | 17 | 43 | 32488 | 27285 | 4570 | 25
53QDMT42-718 | 0.36 | High | 1043 | 24 | 17 | 46 | 31763 | 27000 | 4655 | 25
53QDMT42-718 | 0.36 | High | 1043 | 24 | 17 | 52 | 30305 | 26423 | 4825 | 25
53QDMT42-718 | 0.36 | High | 1043 | 27 | 19 | 35 | 36090 | 28158 | 4425 | 25
53QDMT42-718 | 0.36 | High | 1043 | 27 | 19 | 43 | 33568 | 27540 | 4655 | 25
53QDMT42-718 | 0.36 | High | 1043 | 27 | 19 | 46 | 32488 | 26970 | 4740 | 25
53QDMT42-718 | 0.36 | High | 1043 | 27 | 19 | 52 | 30315 | 25820 | 4910 | 25
53QDMT42-718 | 0.36 | High | 1043 | 32 | 23 | 35 | 37540 | 33035 | 4655 | 25
53QDMT42-718 | 0.36 | High | 1043 | 32 | 23 | 43 | 34655 | 32235 | 4840 | 25
53QDMT42-718 | 0.36 | High | 1043 | 32 | 23 | 46 | 33570 | 31895 | 4890 | 25
53QDMT42-718 | 0.36 | High | 1043 | 32 | 23 | 52 | 31395 | 30695 | 4990 | 25
53QDMT42-718 | 0.36 | Medium | 533 | 21 | 15 | 35 | 32225 | 24725 | 4035 | 25
53QDMT42-718 | 0.36 | Medium | 533 | 21 | 15 | 43 | 30850 | 24920 | 4163 | 25
53QDMT42-718 | 0.36 | Medium | 533 | 21 | 15 | 46 | 30158 | 24575 | 4205 | 25
53QDMT42-718 | 0.36 | Medium | 533 | 21 | 15 | 52 | 28770 | 23885 | 4295 | 25
53QDMT42-718 | 0.36 | Medium | 533 | 24 | 17 | 35 | 33270 | 25840 | 4215 | 25
53QDMT42-718 | 0.36 | Medium | 533 | 24 | 17 | 43 | 31190 | 25105 | 4413 | 25
53QDMT42-718 | 0.36 | Medium | 533 | 24 | 17 | 46 | 30493 | 24852 | 4515 | 25
53QDMT42-718 | 0.36 | Medium | 533 | 24 | 17 | 52 | 29095 | 24310 | 3180 | 25
53QDMT42-718 | 0.36 | Medium | 533 | 27 | 19 | 35 | 34648 | 25905 | 4295 | 25
53QDMT42-718 | 0.36 | Medium | 533 | 27 | 19 | 43 | 32228 | 25338 | 4515 | 25
53QDMT42-718 | 0.36 | Medium | 533 | 27 | 19 | 46 | 31190 | 24815 | 4600 | 25
53QDMT42-718 | 0.36 | Medium | 533 | 27 | 19 | 52 | 29105 | 23890 | 4765 | 25
53QDMT42-718 | 0.36 | Medium | 533 | 32 | 23 | 35 | 36040 | 30395 | 4515 | 25
53QDMT42-718 | 0.36 | Medium | 533 | 32 | 23 | 43 | 33270 | 29658 | 4695 | 25
53QDMT42-718 | 0.36 | Medium | 533 | 32 | 23 | 46 | 32230 | 29345 | 4745 | 25
53QDMT42-718 | 0.36 | Medium | 533 | 32 | 23 | 52 | 30140 | 28240 | 4840 | 25
53QDMT42-718 | 0.36 | Low | 263 | 21 | 15 | 35 | 30883 | 22845 | 3870 | 25
53QDMT42-718 | 0.36 | Low | 263 | 21 | 15 | 43 | 29563 | 23025 | 3990 | 25
53QDMT42-718 | 0.36 | Low | 263 | 21 | 15 | 46 | 28903 | 22708 | 4033 | 25
53QDMT42-718 | 0.36 | Low | 263 | 21 | 15 | 52 | 27570 | 22090 | 4115 | 25
53QDMT42-718 | 0.36 | Low | 263 | 24 | 17 | 35 | 31885 | 23875 | 4043 | 25
53QDMT42-718 | 0.36 | Low | 263 | 24 | 17 | 43 | 29890 | 23195 | 4250 | 25
53QDMT42-718 | 0.36 | Low | 263 | 24 | 17 | 46 | 29223 | 22953 | 4330 | 25
53QDMT42-718 | 0.36 | Low | 263 | 24 | 17 | 52 | 27883 | 22460 | 4488 | 25
53QDMT42-718 | 0.36 | Low | 263 | 27 | 19 | 35 | 33205 | 23938 | 4115 | 25
53QDMT42-718 | 0.36 | Low | 263 | 27 | 19 | 43 | 30885 | 23400 | 4330 | 25
53QDMT42-718 | 0.36 | Low | 263 | 27 | 19 | 46 | 29890 | 22928 | 4410 | 25
53QDMT42-718 | 0.36 | Low | 263 | 27 | 19 | 52 | 27893 | 21950 | 4568 | 25
53QDMT42-718 | 0.36 | Low | 263 | 21 | 23 | 35 | 34540 | 28083 | 4330 | 25
53QDMT42-718 | 0.36 | Low | 263 | 21 | 23 | 43 | 31885 | 27403 | 4483 | 25
53QDMT42-718 | 0.36 | Low | 263 | 21 | 23 | 46 | 30888 | 27113 | 4550 | 25
53QDMT42-718 | 0.36 | Low | 263 | 21 | 23 | 52 | 28885 | 26093 | 4643 | 25
53QDMT42-718 | 0.4 | High | 1007 | 21 | 15 | 35 | 33160 | 26550 | 4145 | 25
53QDMT42-718 | 0.4 | High | 1007 | 21 | 15 | 43 | 31745 | 26760 | 4275 | 25
53QDMT42-718 | 0.4 | High | 1007 | 21 | 15 | 46 | 31035 | 26390 | 4320 | 25
53QDMT42-718 | 0.4 | High | 1007 | 21 | 15 | 52 | 29605 | 25650 | 4410 | 25
53QDMT42-718 | 0.4 | High | 1007 | 24 | 17 | 35 | 34240 | 27750 | 4330 | 25
53QDMT42-718 | 0.4 | High | 1007 | 24 | 17 | 43 | 32100 | 26960 | 4555 | 25
53QDMT42-718 | 0.4 | High | 1007 | 24 | 17 | 46 | 31385 | 26680 | 4640 | 25
53QDMT42-718 | 0.4 | High | 1007 | 24 | 17 | 52 | 29935 | 26100 | 4810 | 25
53QDMT42-718 | 0.4 | High | 1007 | 27 | 19 | 35 | 35655 | 27820 | 4410 | 25
53QDMT42-718 | 0.4 | High | 1007 | 27 | 19 | 43 | 33165 | 27210 | 4640 | 25
53QDMT42-718 | 0.4 | High | 1007 | 27 | 19 | 46 | 32100 | 26650 | 4725 | 25
53QDMT42-718 | 0.4 | High | 1007 | 27 | 19 | 52 | 29950 | 25510 | 4895 | 25
53QDMT42-718 | 0.4 | High | 1007 | 32 | 23 | 35 | 37090 | 32640 | 4640 | 25
53QDMT42-718 | 0.4 | High | 1007 | 32 | 23 | 43 | 34240 | 31850 | 4825 | 25
53QDMT42-718 | 0.4 | High | 1007 | 32 | 23 | 46 | 33170 | 31515 | 4875 | 25
53QDMT42-718 | 0.4 | High | 1007 | 32 | 23 | 52 | 31015 | 30325 | 4975 | 25
53QDMT42-718 | 0.4 | Medium | 493 | 21 | 15 | 35 | 31835 | 24430 | 4020 | 25
53QDMT42-718 | 0.4 | Medium | 493 | 21 | 15 | 43 | 30480 | 24620 | 4150 | 25
53QDMT42-718 | 0.4 | Medium | 493 | 21 | 15 | 46 | 29795 | 24280 | 4190 | 25
53QDMT42-718 | 0.4 | Medium | 493 | 21 | 15 | 52 | 28425 | 23600 | 4280 | 25
53QDMT42-718 | 0.4 | Medium | 493 | 24 | 17 | 35 | 32870 | 25530 | 4200 | 25
53QDMT42-718 | 0.4 | Medium | 493 | 24 | 17 | 43 | 30820 | 24805 | 4420 | 25
53QDMT42-718 | 0.4 | Medium | 493 | 24 | 17 | 46 | 30130 | 24550 | 4500 | 25
53QDMT42-718 | 0.4 | Medium | 493 | 24 | 17 | 52 | 28740 | 24015 | 1665 | 25
53QDMT42-718 | 0.4 | Medium | 493 | 27 | 19 | 35 | 34230 | 25595 | 4280 | 25
53QDMT42-718 | 0.4 | Medium | 493 | 27 | 19 | 43 | 31840 | 25035 | 4500 | 25
53QDMT42-718 | 0.4 | Medium | 493 | 27 | 19 | 46 | 30820 | 24520 | 4585 | 25
53QDMT42-718 | 0.4 | Medium | 493 | 27 | 19 | 52 | 28755 | 23740 | 4750 | 25
53QDMT42-718 | 0.4 | Medium | 493 | 32 | 23 | 35 | 35610 | 30030 | 4500 | 25
53QDMT42-718 | 0.4 | Medium | 493 | 32 | 23 | 43 | 32870 | 29305 | 4680 | 25
53QDMT42-718 | 0.4 | Medium | 493 | 32 | 23 | 46 | 31845 | 28995 | 4730 | 25
53QDMT42-718 | 0.4 | Medium | 493 | 32 | 23 | 52 | 29775 | 27900 | 4825 | 25
53QDMT42-718 | 0.4 | Low | 206 | 21 | 15 | 35 | 30510 | 22570 | 3855 | 25
53QDMT42-718 | 0.4 | Low | 206 | 21 | 15 | 43 | 29205 | 22750 | 3975 | 25
53QDMT42-718 | 0.4 | Low | 206 | 21 | 15 | 46 | 28555 | 22435 | 4020 | 25
53QDMT42-718 | 0.4 | Low | 206 | 21 | 15 | 52 | 27240 | 21850 | 4100 | 25
53QDMT42-718 | 0.4 | Low | 206 | 24 | 17 | 35 | 31505 | 23590 | 4030 | 25
53QDMT42-718 | 0.4 | Low | 206 | 24 | 17 | 43 | 29535 | 22920 | 4235 | 25
53QDMT42-718 | 0.4 | Low | 206 | 24 | 17 | 46 | 28875 | 22680 | 4315 | 25
53QDMT42-718 | 0.4 | Low | 206 | 24 | 17 | 52 | 27540 | 22185 | 4475 | 25
53QDMT42-718 | 0.4 | Low | 206 | 27 | 19 | 35 | 32805 | 23650 | 4100 | 25
53QDMT42-718 | 0.4 | Low | 206 | 27 | 19 | 43 | 30515 | 23130 | 4315 | 25
53QDMT42-718 | 0.4 | Low | 206 | 27 | 19 | 46 | 29535 | 22655 | 4395 | 25
53QDMT42-718 | 0.4 | Low | 206 | 27 | 19 | 52 | 27555 | 21685 | 4555 | 25
53QDMT42-718 | 0.4 | Low | 206 | 21 | 23 | 35 | 34125 | 27745 | 4315 | 25
53QDMT42-718 | 0.4 | Low | 206 | 21 | 23 | 43 | 31505 | 27075 | 4450 | 25
53QDMT42-718 | 0.4 | Low | 206 | 21 | 23 | 46 | 30520 | 26790 | 4535 | 25
53QDMT42-718 | 0.4 | Low | 206 | 21 | 23 | 52 | 28535 | 25780 | 4630 | 25
53QDMT48-518 | 0 | High | 1370 | 21 | 15 | 35 | 41385 | 33120 | 3945 | 26
53QDMT48-518 | 0 | High | 1370 | 21 | 15 | 43 | 39605 | 33370 | 4065 | 26
53QDMT48-518 | 0 | High | 1370 | 21 | 15 | 46 | 38715 | 32915 | 4105 | 26
53QDMT48-518 | 0 | High | 1370 | 21 | 15 | 52 | 36935 | 32005 | 4190 | 26
53QDMT48-518 | 0 | High | 1370 | 24 | 17 | 35 | 42720 | 34620 | 4115 | 26
53QDMT48-518 | 0 | High | 1370 | 24 | 17 | 43 | 40050 | 33630 | 4325 | 26
53QDMT48-518 | 0 | High | 1370 | 24 | 17 | 46 | 39160 | 33285 | 4400 | 26
53QDMT48-518 | 0 | High | 1370 | 24 | 17 | 52 | 37380 | 32590 | 4560 | 26
53QDMT48-518 | 0 | High | 1370 | 27 | 19 | 35 | 44500 | 34710 | 4200 | 26
53QDMT48-518 | 0 | High | 1370 | 27 | 19 | 43 | 41385 | 33950 | 4415 | 26
53QDMT48-518 | 0 | High | 1370 | 27 | 19 | 46 | 40050 | 33245 | 4490 | 26
53QDMT48-518 | 0 | High | 1370 | 27 | 19 | 52 | 37380 | 31835 | 4645 | 26
53QDMT48-518 | 0 | High | 1370 | 32 | 23 | 35 | 46280 | 40720 | 4405 | 26
53QDMT48-518 | 0 | High | 1370 | 32 | 23 | 43 | 42720 | 39735 | 4580 | 26
53QDMT48-518 | 0 | High | 1370 | 32 | 23 | 46 | 41385 | 39315 | 4625 | 26
53QDMT48-518 | 0 | High | 1370 | 32 | 23 | 52 | 38715 | 38470 | 4720 | 26
53QDMT48-518 | 0 | Medium | 880 | 21 | 15 | 35 | 39735 | 30475 | 3825 | 26
53QDMT48-518 | 0 | Medium | 880 | 21 | 15 | 43 | 38020 | 30700 | 3935 | 26
53QDMT48-518 | 0 | Medium | 880 | 21 | 15 | 46 | 37170 | 30285 | 3975 | 26
53QDMT48-518 | 0 | Medium | 880 | 21 | 15 | 52 | 35460 | 29450 | 4060 | 26
53QDMT48-518 | 0 | Medium | 880 | 24 | 17 | 35 | 41015 | 31850 | 3990 | 26
53QDMT48-518 | 0 | Medium | 880 | 24 | 17 | 43 | 38450 | 30940 | 4180 | 26
53QDMT48-518 | 0 | Medium | 880 | 24 | 17 | 46 | 37595 | 30625 | 4255 | 26
53QDMT48-518 | 0 | Medium | 880 | 24 | 17 | 52 | 36185 | 29985 | 4415 | 26
53QDMT48-518 | 0 | Medium | 880 | 27 | 19 | 35 | 42720 | 31940 | 4075 | 26
53QDMT48-518 | 0 | Medium | 880 | 27 | 19 | 43 | 39735 | 31235 | 4265 | 26
53QDMT48-518 | 0 | Medium | 880 | 27 | 19 | 46 | 38450 | 30590 | 4345 | 26
53QDMT48-518 | 0 | Medium | 880 | 27 | 19 | 52 | 36185 | 29295 | 4500 | 26
53QDMT48-518 | 0 | Medium | 880 | 32 | 23 | 35 | 44435 | 37465 | 4275 | 26
53QDMT48-518 | 0 | Medium | 880 | 32 | 23 | 43 | 41015 | 36555 | 4430 | 26
53QDMT48-518 | 0 | Medium | 880 | 32 | 23 | 46 | 39735 | 36170 | 4474 | 26
53QDMT48-518 | 0 | Medium | 880 | 32 | 23 | 52 | 37170 | 35395 | 4570 | 26
53QDMT48-518 | 0 | Low | 715 | 21 | 15 | 35 | 38075 | 28155 | 3670 | 26
53QDMT48-518 | 0 | Low | 715 | 21 | 15 | 43 | 36435 | 28370 | 3785 | 26
53QDMT48-518 | 0 | Low | 715 | 21 | 15 | 46 | 35620 | 27985 | 3820 | 26
53QDMT48-518 | 0 | Low | 715 | 21 | 15 | 52 | 33985 | 27210 | 3895 | 26
53QDMT48-518 | 0 | Low | 715 | 24 | 17 | 35 | 39310 | 29430 | 3830 | 26
53QDMT48-518 | 0 | Low | 715 | 24 | 17 | 43 | 36850 | 28590 | 4020 | 26
53QDMT48-518 | 0 | Low | 715 | 24 | 17 | 46 | 36030 | 28295 | 4090 | 26
53QDMT48-518 | 0 | Low | 715 | 24 | 17 | 52 | 34395 | 27705 | 4235 | 26
53QDMT48-518 | 0 | Low | 715 | 27 | 19 | 35 | 40940 | 29510 | 3910 | 26
53QDMT48-518 | 0 | Low | 715 | 27 | 19 | 43 | 38075 | 28860 | 4105 | 26
53QDMT48-518 | 0 | Low | 715 | 27 | 19 | 46 | 36850 | 28260 | 4180 | 26
53QDMT48-518 | 0 | Low | 715 | 27 | 19 | 52 | 34395 | 27065 | 4325 | 26
53QDMT48-518 | 0 | Low | 715 | 21 | 23 | 35 | 42580 | 34615 | 4100 | 26
53QDMT48-518 | 0 | Low | 715 | 21 | 23 | 43 | 39310 | 33775 | 4260 | 26
53QDMT48-518 | 0 | Low | 715 | 21 | 23 | 46 | 38075 | 33420 | 4305 | 26
53QDMT48-518 | 0 | Low | 715 | 21 | 23 | 52 | 35620 | 32700 | 4385 | 26
53QDMT48-518 | 0.08 | High | 1300 | 21 | 15 | 35 | 40700 | 32575 | 3920 | 26
53QDMT48-518 | 0.08 | High | 1300 | 21 | 15 | 43 | 38950 | 32820 | 4040 | 26
53QDMT48-518 | 0.08 | High | 1300 | 21 | 15 | 46 | 38075 | 32375 | 4080 | 26
53QDMT48-518 | 0.08 | High | 1300 | 21 | 15 | 52 | 36325 | 31485 | 4165 | 26
53QDMT48-518 | 0.08 | High | 1300 | 24 | 17 | 35 | 42010 | 34045 | 4090 | 26
53QDMT48-518 | 0.08 | High | 1300 | 24 | 17 | 43 | 39385 | 33075 | 4300 | 26
53QDMT48-518 | 0.08 | High | 1300 | 24 | 17 | 46 | 38510 | 32730 | 4375 | 26
53QDMT48-518 | 0.08 | High | 1300 | 24 | 17 | 52 | 36765 | 32050 | 4530 | 26
53QDMT48-518 | 0.08 | High | 1300 | 27 | 19 | 35 | 43760 | 34135 | 4170 | 26
53QDMT48-518 | 0.08 | High | 1300 | 27 | 19 | 43 | 40695 | 33385 | 4380 | 26
53QDMT48-518 | 0.08 | High | 1300 | 27 | 19 | 46 | 39385 | 32690 | 4470 | 26
53QDMT48-518 | 0.08 | High | 1300 | 27 | 19 | 52 | 36760 | 31310 | 3475 | 26
53QDMT48-518 | 0.08 | High | 1300 | 32 | 23 | 35 | 45510 | 40045 | 4380 | 26
53QDMT48-518 | 0.08 | High | 1300 | 32 | 23 | 43 | 41765 | 39075 | 4555 | 26
53QDMT48-518 | 0.08 | High | 1300 | 32 | 23 | 46 | 40700 | 38660 | 4600 | 26
53QDMT48-518 | 0.08 | High | 1300 | 32 | 23 | 52 | 38565 | 37835 | 4695 | 26
53QDMT48-518 | 0.08 | Medium | 803 | 21 | 15 | 35 | 39075 | 29975 | 3805 | 26
53QDMT48-518 | 0.08 | Medium | 803 | 21 | 15 | 43 | 37390 | 30195 | 3910 | 26
53QDMT48-518 | 0.08 | Medium | 803 | 21 | 15 | 46 | 36555 | 29785 | 3950 | 26
53QDMT48-518 | 0.08 | Medium | 803 | 21 | 15 | 52 | 34875 | 28965 | 4035 | 26
53QDMT48-518 | 0.08 | Medium | 803 | 24 | 17 | 35 | 40335 | 31320 | 3970 | 26
53QDMT48-518 | 0.08 | Medium | 803 | 24 | 17 | 43 | 37810 | 30430 | 4160 | 26
53QDMT48-518 | 0.08 | Medium | 803 | 24 | 17 | 46 | 36975 | 30115 | 4230 | 26
53QDMT48-518 | 0.08 | Medium | 803 | 24 | 17 | 52 | 35445 | 29490 | 4385 | 26
53QDMT48-518 | 0.08 | Medium | 803 | 27 | 19 | 35 | 42010 | 31410 | 4050 | 26
53QDMT48-518 | 0.08 | Medium | 803 | 27 | 19 | 43 | 39075 | 30715 | 4240 | 26
53QDMT48-518 | 0.08 | Medium | 803 | 27 | 19 | 46 | 37810 | 30080 | 4320 | 26
53QDMT48-518 | 0.08 | Medium | 803 | 27 | 19 | 52 | 35440 | 28805 | 4475 | 26
53QDMT48-518 | 0.08 | Medium | 803 | 32 | 23 | 35 | 43695 | 36845 | 4250 | 26
53QDMT48-518 | 0.08 | Medium | 803 | 32 | 23 | 43 | 40100 | 35950 | 4400 | 26
53QDMT48-518 | 0.08 | Medium | 803 | 32 | 23 | 46 | 39072 | 35570 | 4450 | 26
53QDMT48-518 | 0.08 | Medium | 803 | 32 | 23 | 52 | 37025 | 34810 | 4540 | 26
53QDMT48-518 | 0.08 | Low | 636 | 21 | 15 | 35 | 37445 | 27690 | 3650 | 26
53QDMT48-518 | 0.08 | Low | 636 | 21 | 15 | 43 | 35835 | 27900 | 3760 | 26
53QDMT48-518 | 0.08 | Low | 636 | 21 | 15 | 46 | 35030 | 27525 | 3795 | 26
53QDMT48-518 | 0.08 | Low | 636 | 21 | 15 | 52 | 32795 | 26765 | 3865 | 26
53QDMT48-518 | 0.08 | Low | 636 | 24 | 17 | 35 | 38655 | 28940 | 3810 | 26
53QDMT48-518 | 0.08 | Low | 636 | 24 | 17 | 43 | 36235 | 28115 | 3995 | 26
53QDMT48-518 | 0.08 | Low | 636 | 24 | 17 | 46 | 35435 | 27825 | 4070 | 26
53QDMT48-518 | 0.08 | Low | 636 | 24 | 17 | 52 | 33185 | 27245 | 4215 | 26
53QDMT48-518 | 0.08 | Low | 636 | 27 | 19 | 35 | 40260 | 29020 | 3885 | 26
53QDMT48-518 | 0.08 | Low | 636 | 27 | 19 | 43 | 37445 | 28380 | 4080 | 26
53QDMT48-518 | 0.08 | Low | 636 | 27 | 19 | 46 | 36235 | 27790 | 4155 | 26
53QDMT48-518 | 0.08 | Low | 636 | 27 | 19 | 52 | 33090 | 26615 | 4300 | 26
53QDMT48-518 | 0.08 | Low | 636 | 21 | 23 | 35 | 41875 | 34040 | 4075 | 26
53QDMT48-518 | 0.08 | Low | 636 | 21 | 23 | 43 | 38430 | 33215 | 4235 | 26
53QDMT48-518 | 0.08 | Low | 636 | 21 | 23 | 46 | 37445 | 32870 | 4275 | 26
53QDMT48-518 | 0.08 | Low | 636 | 21 | 23 | 52 | 34820 | 32165 | 4360 | 26
53QDMT48-518 | 0.12 | High | 1255 | 21 | 15 | 35 | 40355 | 32300 | 3910 | 26
53QDMT48-518 | 0.12 | High | 1255 | 21 | 15 | 43 | 38620 | 32540 | 4030 | 26
53QDMT48-518 | 0.12 | High | 1255 | 21 | 15 | 46 | 37755 | 32100 | 4070 | 26
53QDMT48-518 | 0.12 | High | 1255 | 21 | 15 | 52 | 36020 | 31220 | 4155 | 26
53QDMT48-518 | 0.12 | High | 1255 | 24 | 17 | 35 | 41655 | 33755 | 4075 | 26
53QDMT48-518 | 0.12 | High | 1255 | 24 | 17 | 43 | 39055 | 32795 | 4285 | 26
53QDMT48-518 | 0.12 | High | 1255 | 24 | 17 | 46 | 38190 | 32455 | 4360 | 26
53QDMT48-518 | 0.12 | High | 1255 | 24 | 17 | 52 | 36455 | 31780 | 4515 | 26
53QDMT48-518 | 0.12 | High | 1255 | 27 | 19 | 35 | 43385 | 33845 | 4155 | 26
53QDMT48-518 | 0.12 | High | 1255 | 27 | 19 | 43 | 40350 | 33100 | 4365 | 26
53QDMT48-518 | 0.12 | High | 1255 | 27 | 19 | 46 | 39050 | 32415 | 4445 | 26
53QDMT48-518 | 0.12 | High | 1255 | 27 | 19 | 52 | 36445 | 31035 | 4600 | 26
53QDMT48-518 | 0.12 | High | 1255 | 32 | 23 | 35 | 45120 | 39705 | 4365 | 26
53QDMT48-518 | 0.12 | High | 1255 | 32 | 23 | 43 | 41655 | 38745 | 4535 | 26
53QDMT48-518 | 0.12 | High | 1255 | 32 | 23 | 46 | 40355 | 38335 | 4585 | 26
53QDMT48-518 | 0.12 | High | 1255 | 32 | 23 | 52 | 37755 | 37515 | 4680 | 26
53QDMT48-518 | 0.12 | Medium | 770 | 21 | 15 | 35 | 38740 | 29720 | 3790 | 26
53QDMT48-518 | 0.12 | Medium | 770 | 21 | 15 | 43 | 37080 | 29940 | 3895 | 26
53QDMT48-518 | 0.12 | Medium | 770 | 21 | 15 | 46 | 36245 | 29535 | 3935 | 26
53QDMT48-518 | 0.12 | Medium | 770 | 21 | 15 | 52 | 34585 | 28725 | 4020 | 26
53QDMT48-518 | 0.12 | Medium | 770 | 24 | 17 | 35 | 39990 | 31055 | 3955 | 26
53QDMT48-518 | 0.12 | Medium | 770 | 24 | 17 | 43 | 37495 | 30175 | 4140 | 26
53QDMT48-518 | 0.12 | Medium | 770 | 24 | 17 | 46 | 36660 | 29860 | 4220 | 26
53QDMT48-518 | 0.12 | Medium | 770 | 24 | 17 | 52 | 35005 | 29240 | 4375 | 26
53QDMT48-518 | 0.12 | Medium | 770 | 27 | 19 | 35 | 41655 | 31140 | 4035 | 26
53QDMT48-518 | 0.12 | Medium | 770 | 27 | 19 | 43 | 38735 | 30455 | 4225 | 26
53QDMT48-518 | 0.12 | Medium | 770 | 27 | 19 | 46 | 37490 | 29820 | 4305 | 26
53QDMT48-518 | 0.12 | Medium | 770 | 27 | 19 | 52 | 34995 | 28555 | 4460 | 26
53QDMT48-518 | 0.12 | Medium | 770 | 32 | 23 | 35 | 43320 | 36530 | 4235 | 26
53QDMT48-518 | 0.12 | Medium | 770 | 32 | 23 | 43 | 39990 | 35650 | 4385 | 26
53QDMT48-518 | 0.12 | Medium | 770 | 32 | 23 | 46 | 38740 | 35268 | 4435 | 26
53QDMT48-518 | 0.12 | Medium | 770 | 32 | 23 | 52 | 36245 | 34515 | 4525 | 26
53QDMT48-518 | 0.12 | Low | 594 | 21 | 15 | 35 | 37125 | 27460 | 3635 | 26
53QDMT48-518 | 0.12 | Low | 594 | 21 | 15 | 43 | 35535 | 27660 | 3740 | 26
53QDMT48-518 | 0.12 | Low | 594 | 21 | 15 | 46 | 34735 | 27290 | 3780 | 26
53QDMT48-518 | 0.12 | Low | 594 | 21 | 15 | 52 | 30620 | 26540 | 3850 | 26
53QDMT48-518 | 0.12 | Low | 594 | 24 | 17 | 35 | 38325 | 28690 | 3795 | 26
53QDMT48-518 | 0.12 | Low | 594 | 24 | 17 | 43 | 35935 | 27880 | 3980 | 26
53QDMT48-518 | 0.12 | Low | 594 | 24 | 17 | 46 | 35135 | 27590 | 4055 | 26
53QDMT48-518 | 0.12 | Low | 594 | 24 | 17 | 52 | 30990 | 27020 | 4200 | 26
53QDMT48-518 | 0.12 | Low | 594 | 27 | 19 | 35 | 39920 | 28770 | 3860 | 26
53QDMT48-518 | 0.12 | Low | 594 | 27 | 19 | 43 | 37120 | 28140 | 4065 | 26
53QDMT48-518 | 0.12 | Low | 594 | 27 | 19 | 46 | 35930 | 27550 | 4135 | 26
53QDMT48-518 | 0.12 | Low | 594 | 27 | 19 | 52 | 30985 | 26385 | 4285 | 26
53QDMT48-518 | 0.12 | Low | 594 | 21 | 23 | 35 | 41515 | 33755 | 4065 | 26
53QDMT48-518 | 0.12 | Low | 594 | 21 | 23 | 43 | 38325 | 32935 | 4220 | 26
53QDMT48-518 | 0.12 | Low | 594 | 21 | 23 | 46 | 37125 | 32590 | 4260 | 26
53QDMT48-518 | 0.12 | Low | 594 | 21 | 23 | 52 | 32090 | 31890 | 4345 | 26
53QDMT48-518 | 0.16 | High | 1233 | 21 | 15 | 35 | 40010 | 32025 | 3895 | 26
53QDMT48-518 | 0.16 | High | 1233 | 21 | 15 | 43 | 38290 | 32260 | 4015 | 26
53QDMT48-518 | 0.16 | High | 1233 | 21 | 15 | 46 | 37430 | 31825 | 4055 | 26
53QDMT48-518 | 0.16 | High | 1233 | 21 | 15 | 52 | 35715 | 30955 | 4135 | 26
53QDMT48-518 | 0.16 | High | 1233 | 24 | 17 | 35 | 41300 | 33465 | 4065 | 26
53QDMT48-518 | 0.16 | High | 1233 | 24 | 17 | 43 | 38720 | 32515 | 4270 | 26
53QDMT48-518 | 0.16 | High | 1233 | 24 | 17 | 46 | 37860 | 32180 | 4350 | 26
53QDMT48-518 | 0.16 | High | 1233 | 24 | 17 | 52 | 36145 | 31510 | 4505 | 26
53QDMT48-518 | 0.16 | High | 1233 | 27 | 19 | 35 | 43015 | 33555 | 4135 | 26
53QDMT48-518 | 0.16 | High | 1233 | 27 | 19 | 43 | 40005 | 32820 | 4348 | 26
53QDMT48-518 | 0.16 | High | 1233 | 27 | 19 | 46 | 38720 | 32140 | 4445 | 26
53QDMT48-518 | 0.16 | High | 1233 | 27 | 19 | 52 | 36140 | 30775 | 2305 | 26
53QDMT48-518 | 0.16 | High | 1233 | 32 | 23 | 35 | 44735 | 39365 | 4350 | 26
53QDMT48-518 | 0.16 | High | 1233 | 32 | 23 | 43 | 40810 | 38415 | 4520 | 26
53QDMT48-518 | 0.16 | High | 1233 | 32 | 23 | 46 | 40010 | 38005 | 4570 | 26
53QDMT48-518 | 0.16 | High | 1233 | 32 | 23 | 52 | 38415 | 37195 | 4660 | 26
53QDMT48-518 | 0.16 | Medium | 733 | 21 | 15 | 35 | 38415 | 29465 | 3780 | 26
53QDMT48-518 | 0.16 | Medium | 733 | 21 | 15 | 43 | 36760 | 29685 | 3885 | 26
53QDMT48-518 | 0.16 | Medium | 733 | 21 | 15 | 46 | 35940 | 29285 | 3925 | 26
53QDMT48-518 | 0.16 | Medium | 733 | 21 | 15 | 52 | 34290 | 28480 | 4005 | 26
53QDMT48-518 | 0.16 | Medium | 733 | 24 | 17 | 35 | 39650 | 30795 | 3945 | 26
53QDMT48-518 | 0.16 | Medium | 733 | 24 | 17 | 43 | 37170 | 29915 | 4130 | 26
53QDMT48-518 | 0.16 | Medium | 733 | 24 | 17 | 46 | 36350 | 29605 | 4205 | 26
53QDMT48-518 | 0.16 | Medium | 733 | 24 | 17 | 52 | 34700 | 28990 | 4355 | 26
53QDMT48-518 | 0.16 | Medium | 733 | 27 | 19 | 35 | 41300 | 30875 | 4020 | 26
53QDMT48-518 | 0.16 | Medium | 733 | 27 | 19 | 43 | 38410 | 30200 | 4210 | 26
53QDMT48-518 | 0.16 | Medium | 733 | 27 | 19 | 46 | 37170 | 29565 | 4290 | 26
53QDMT48-518 | 0.16 | Medium | 733 | 27 | 19 | 52 | 34695 | 28315 | 4445 | 26
53QDMT48-518 | 0.16 | Medium | 733 | 32 | 23 | 35 | 42950 | 36215 | 4220 | 26
53QDMT48-518 | 0.16 | Medium | 733 | 32 | 23 | 43 | 39180 | 35340 | 4369 | 26
53QDMT48-518 | 0.16 | Medium | 733 | 32 | 23 | 46 | 38415 | 34975 | 4420 | 26
53QDMT48-518 | 0.16 | Medium | 733 | 32 | 23 | 52 | 36875 | 34220 | 4510 | 26
53QDMT48-518 | 0.16 | Low | 548 | 21 | 15 | 35 | 36810 | 27225 | 3625 | 26
53QDMT48-518 | 0.16 | Low | 548 | 21 | 15 | 43 | 35230 | 27425 | 3730 | 26
53QDMT48-518 | 0.16 | Low | 548 | 21 | 15 | 46 | 34435 | 27060 | 3770 | 26
53QDMT48-518 | 0.16 | Low | 548 | 21 | 15 | 52 | 31600 | 26315 | 3840 | 26
53QDMT48-518 | 0.16 | Low | 548 | 24 | 17 | 35 | 38000 | 28450 | 3780 | 26
53QDMT48-518 | 0.16 | Low | 548 | 24 | 17 | 43 | 35625 | 27640 | 3970 | 26
53QDMT48-518 | 0.16 | Low | 548 | 24 | 17 | 46 | 34835 | 27355 | 4045 | 26
53QDMT48-518 | 0.16 | Low | 548 | 24 | 17 | 52 | 31980 | 26785 | 4190 | 26
53QDMT48-518 | 0.16 | Low | 548 | 27 | 19 | 35 | 39575 | 28525 | 3850 | 26
53QDMT48-518 | 0.16 | Low | 548 | 27 | 19 | 43 | 36810 | 27900 | 4055 | 26
53QDMT48-518 | 0.16 | Low | 548 | 27 | 19 | 46 | 35620 | 27320 | 4125 | 26
53QDMT48-518 | 0.16 | Low | 548 | 27 | 19 | 52 | 31780 | 26165 | 4270 | 26
53QDMT48-518 | 0.16 | Low | 548 | 21 | 23 | 35 | 41165 | 33465 | 4050 | 26
53QDMT48-518 | 0.16 | Low | 548 | 21 | 23 | 43 | 37545 | 32655 | 4205 | 26
53QDMT48-518 | 0.16 | Low | 548 | 21 | 23 | 46 | 36815 | 32310 | 4245 | 26
53QDMT48-518 | 0.16 | Low | 548 | 21 | 23 | 52 | 34015 | 31620 | 4330 | 26
53QDMT48-518 | 0.2 | High | 1187 | 21 | 15 | 35 | 39670 | 31755 | 3875 | 26
53QDMT48-518 | 0.2 | High | 1187 | 21 | 15 | 43 | 37970 | 31985 | 3995 | 26
53QDMT48-518 | 0.2 | High | 1187 | 21 | 15 | 46 | 37105 | 31550 | 4040 | 26
53QDMT48-518 | 0.2 | High | 1187 | 21 | 15 | 52 | 35405 | 30690 | 4120 | 26
53QDMT48-518 | 0.2 | High | 1187 | 24 | 17 | 35 | 40945 | 33180 | 4050 | 26
53QDMT48-518 | 0.2 | High | 1187 | 24 | 17 | 43 | 38385 | 32230 | 4255 | 26
53QDMT48-518 | 0.2 | High | 1187 | 24 | 17 | 46 | 37535 | 31900 | 4335 | 26
53QDMT48-518 | 0.2 | High | 1187 | 24 | 17 | 52 | 35830 | 31235 | 4490 | 26
53QDMT48-518 | 0.2 | High | 1187 | 27 | 19 | 35 | 42645 | 33270 | 4120 | 26
53QDMT48-518 | 0.2 | High | 1187 | 27 | 19 | 43 | 39660 | 32535 | 4327 | 26
53QDMT48-518 | 0.2 | High | 1187 | 27 | 19 | 46 | 38385 | 31860 | 4440 | 26
53QDMT48-518 | 0.2 | High | 1187 | 27 | 19 | 52 | 35830 | 30510 | 4585 | 26
53QDMT48-518 | 0.2 | High | 1187 | 32 | 23 | 35 | 44350 | 39025 | 4335 | 26
53QDMT48-518 | 0.2 | High | 1187 | 32 | 23 | 43 | 39965 | 38080 | 4505 | 26
53QDMT48-518 | 0.2 | High | 1187 | 32 | 23 | 46 | 39665 | 37680 | 4555 | 26
53QDMT48-518 | 0.2 | High | 1187 | 32 | 23 | 52 | 39070 | 36875 | 4645 | 26
53QDMT48-518 | 0.2 | Medium | 693 | 21 | 15 | 35 | 38085 | 29215 | 3765 | 26
53QDMT48-518 | 0.2 | Medium | 693 | 21 | 15 | 43 | 36440 | 29425 | 3865 | 26
53QDMT48-518 | 0.2 | Medium | 693 | 21 | 15 | 46 | 35630 | 29030 | 3910 | 26
53QDMT48-518 | 0.2 | Medium | 693 | 21 | 15 | 52 | 33990 | 28235 | 3990 | 26
53QDMT48-518 | 0.2 | Medium | 693 | 24 | 17 | 35 | 39310 | 30530 | 3930 | 26
53QDMT48-518 | 0.2 | Medium | 693 | 24 | 17 | 43 | 36850 | 29655 | 4115 | 26
53QDMT48-518 | 0.2 | Medium | 693 | 24 | 17 | 46 | 36030 | 29350 | 4190 | 26
53QDMT48-518 | 0.2 | Medium | 693 | 24 | 17 | 52 | 34400 | 28735 | 4335 | 26
53QDMT48-518 | 0.2 | Medium | 693 | 27 | 19 | 35 | 40940 | 30610 | 4000 | 26
53QDMT48-518 | 0.2 | Medium | 693 | 27 | 19 | 43 | 38075 | 29935 | 4195 | 26
53QDMT48-518 | 0.2 | Medium | 693 | 27 | 19 | 46 | 36850 | 29312 | 4270 | 26
53QDMT48-518 | 0.2 | Medium | 693 | 27 | 19 | 52 | 34400 | 28070 | 4430 | 26
53QDMT48-518 | 0.2 | Medium | 693 | 32 | 23 | 35 | 42580 | 35905 | 4205 | 26
53QDMT48-518 | 0.2 | Medium | 693 | 32 | 23 | 43 | 38370 | 35035 | 4355 | 26
53QDMT48-518 | 0.2 | Medium | 693 | 32 | 23 | 46 | 38080 | 34665 | 4400 | 26
53QDMT48-518 | 0.2 | Medium | 693 | 32 | 23 | 52 | 37510 | 33930 | 4495 | 26
53QDMT48-518 | 0.2 | Low | 491 | 21 | 15 | 35 | 36495 | 26990 | 3605 | 26
53QDMT48-518 | 0.2 | Low | 491 | 21 | 15 | 43 | 34920 | 27185 | 3715 | 26
53QDMT48-518 | 0.2 | Low | 491 | 21 | 15 | 46 | 34140 | 26825 | 3755 | 26
53QDMT48-518 | 0.2 | Low | 491 | 21 | 15 | 52 | 32575 | 26090 | 3825 | 26
53QDMT48-518 | 0.2 | Low | 491 | 24 | 17 | 35 | 37675 | 28210 | 3770 | 26
53QDMT48-518 | 0.2 | Low | 491 | 24 | 17 | 43 | 35315 | 27400 | 3955 | 26
53QDMT48-518 | 0.2 | Low | 491 | 24 | 17 | 46 | 34530 | 27115 | 4030 | 26
53QDMT48-518 | 0.2 | Low | 491 | 24 | 17 | 52 | 32965 | 26550 | 4175 | 26
53QDMT48-518 | 0.2 | Low | 491 | 27 | 19 | 35 | 39235 | 28280 | 3835 | 26
53QDMT48-518 | 0.2 | Low | 491 | 27 | 19 | 43 | 36490 | 27655 | 4040 | 26
53QDMT48-518 | 0.2 | Low | 491 | 27 | 19 | 46 | 35315 | 27085 | 4110 | 26
53QDMT48-518 | 0.2 | Low | 491 | 27 | 19 | 52 | 32575 | 25940 | 4255 | 26
53QDMT48-518 | 0.2 | Low | 491 | 21 | 23 | 35 | 40805 | 33170 | 4035 | 26
53QDMT48-518 | 0.2 | Low | 491 | 21 | 23 | 43 | 36770 | 32370 | 4190 | 26
53QDMT48-518 | 0.2 | Low | 491 | 21 | 23 | 46 | 36495 | 32030 | 4230 | 26
53QDMT48-518 | 0.2 | Low | 491 | 21 | 23 | 52 | 35945 | 31345 | 4315 | 26
53QDMT48-518 | 0.24 | High | 1151 | 21 | 15 | 35 | 39325 | 31480 | 3860 | 27
53QDMT48-518 | 0.24 | High | 1151 | 21 | 15 | 43 | 33910 | 28575 | 3980 | 27
53QDMT48-518 | 0.24 | High | 1151 | 21 | 15 | 46 | 33150 | 28190 | 4025 | 27
53QDMT48-518 | 0.24 | High | 1151 | 21 | 15 | 52 | 31635 | 27415 | 4105 | 27
53QDMT48-518 | 0.24 | High | 1151 | 24 | 17 | 35 | 40595 | 32895 | 4040 | 27
53QDMT48-518 | 0.24 | High | 1151 | 24 | 17 | 43 | 34480 | 28955 | 4245 | 27
53QDMT48-518 | 0.24 | High | 1151 | 24 | 17 | 46 | 33720 | 28655 | 4325 | 27
53QDMT48-518 | 0.24 | High | 1151 | 24 | 17 | 52 | 32195 | 28070 | 4480 | 27
53QDMT48-518 | 0.24 | High | 1151 | 27 | 19 | 35 | 42270 | 32985 | 4105 | 27
53QDMT48-518 | 0.24 | High | 1151 | 27 | 19 | 43 | 35040 | 28745 | 4315 | 27
53QDMT48-518 | 0.24 | High | 1151 | 27 | 19 | 46 | 33915 | 28155 | 4390 | 27
53QDMT48-518 | 0.24 | High | 1151 | 27 | 19 | 52 | 31665 | 26970 | 4540 | 27
53QDMT48-518 | 0.24 | High | 1151 | 32 | 23 | 35 | 43965 | 38685 | 4320 | 27
53QDMT48-518 | 0.24 | High | 1151 | 32 | 23 | 43 | 37265 | 35510 | 4490 | 27
53QDMT48-518 | 0.24 | High | 1151 | 32 | 23 | 46 | 36990 | 25355 | 4535 | 27
53QDMT48-518 | 0.24 | High | 1151 | 32 | 23 | 52 | 36440 | 36210 | 4630 | 27
53QDMT48-518 | 0.24 | Medium | 653 | 21 | 15 | 35 | 37335 | 28965 | 3750 | 27
53QDMT48-518 | 0.24 | Medium | 653 | 21 | 15 | 43 | 32555 | 26290 | 3855 | 27
53QDMT48-518 | 0.24 | Medium | 653 | 21 | 15 | 46 | 31825 | 25935 | 3905 | 27
53QDMT48-518 | 0.24 | Medium | 653 | 21 | 15 | 52 | 30375 | 25225 | 3980 | 27
53QDMT48-518 | 0.24 | Medium | 653 | 24 | 17 | 35 | 38970 | 30270 | 3920 | 27
53QDMT48-518 | 0.24 | Medium | 653 | 24 | 17 | 43 | 33100 | 26645 | 4110 | 27
53QDMT48-518 | 0.24 | Medium | 653 | 24 | 17 | 46 | 32375 | 26370 | 4195 | 27
53QDMT48-518 | 0.24 | Medium | 653 | 24 | 17 | 52 | 30905 | 25825 | 4345 | 27
53QDMT48-518 | 0.24 | Medium | 653 | 27 | 19 | 35 | 40585 | 30345 | 3985 | 27
53QDMT48-518 | 0.24 | Medium | 653 | 27 | 19 | 43 | 33640 | 26445 | 4185 | 27
53QDMT48-518 | 0.24 | Medium | 653 | 27 | 19 | 46 | 32560 | 25905 | 4260 | 27
53QDMT48-518 | 0.24 | Medium | 653 | 27 | 19 | 52 | 30400 | 24815 | 4405 | 27
53QDMT48-518 | 0.24 | Medium | 653 | 32 | 23 | 35 | 42210 | 35595 | 4190 | 27
53QDMT48-518 | 0.24 | Medium | 653 | 32 | 23 | 43 | 35775 | 32670 | 4350 | 27
53QDMT48-518 | 0.24 | Medium | 653 | 32 | 23 | 46 | 35515 | 32330 | 4400 | 27
53QDMT48-518 | 0.24 | Medium | 653 | 32 | 23 | 52 | 34985 | 33320 | 4490 | 27
53QDMT48-518 | 0.24 | Low | 434 | 21 | 15 | 35 | 36185 | 26760 | 3590 | 27
53QDMT48-518 | 0.24 | Low | 434 | 21 | 15 | 43 | 31200 | 24290 | 3705 | 27
53QDMT48-518 | 0.24 | Low | 434 | 21 | 15 | 46 | 30500 | 23965 | 3740 | 27
53QDMT48-518 | 0.24 | Low | 434 | 21 | 15 | 52 | 29105 | 23310 | 3820 | 27
53QDMT48-518 | 0.24 | Low | 434 | 24 | 17 | 35 | 37345 | 27970 | 3760 | 27
53QDMT48-518 | 0.24 | Low | 434 | 24 | 17 | 43 | 31725 | 24620 | 3945 | 27
53QDMT48-518 | 0.24 | Low | 434 | 24 | 17 | 46 | 31025 | 24360 | 4025 | 27
53QDMT48-518 | 0.24 | Low | 434 | 24 | 17 | 52 | 29620 | 23860 | 4170 | 27
53QDMT48-518 | 0.24 | Low | 434 | 27 | 19 | 35 | 38890 | 28040 | 3820 | 27
53QDMT48-518 | 0.24 | Low | 434 | 27 | 19 | 43 | 32235 | 24430 | 4020 | 27
53QDMT48-518 | 0.24 | Low | 434 | 27 | 19 | 46 | 31205 | 23935 | 4085 | 27
53QDMT48-518 | 0.24 | Low | 434 | 27 | 19 | 52 | 29130 | 22925 | 4225 | 27
53QDMT48-518 | 0.24 | Low | 434 | 21 | 23 | 35 | 40450 | 32885 | 4020 | 27
53QDMT48-518 | 0.24 | Low | 434 | 21 | 23 | 43 | 34285 | 30185 | 4180 | 27
53QDMT48-518 | 0.24 | Low | 434 | 21 | 23 | 46 | 34030 | 29870 | 4220 | 27
53QDMT48-518 | 0.24 | Low | 434 | 21 | 23 | 52 | 33530 | 30785 | 4310 | 27
53QDMT48-518 | 0.28 | High | 1115 | 21 | 15 | 35 | 38985 | 31205 | 3845 | 27
53QDMT48-518 | 0.28 | High | 1115 | 21 | 15 | 43 | 35445 | 25160 | 3965 | 27
53QDMT48-518 | 0.28 | High | 1115 | 21 | 15 | 46 | 34655 | 29465 | 4005 | 27
53QDMT48-518 | 0.28 | High | 1115 | 21 | 15 | 52 | 33070 | 28655 | 4090 | 27
53QDMT48-518 | 0.28 | High | 1115 | 24 | 17 | 35 | 40235 | 32615 | 4025 | 27
53QDMT48-518 | 0.28 | High | 1115 | 24 | 17 | 43 | 35940 | 25680 | 4230 | 27
53QDMT48-518 | 0.28 | High | 1115 | 24 | 17 | 46 | 35140 | 29870 | 4310 | 27
53QDMT48-518 | 0.28 | High | 1115 | 24 | 17 | 52 | 33545 | 29255 | 4465 | 27
53QDMT48-518 | 0.28 | High | 1115 | 27 | 19 | 35 | 41900 | 32695 | 4090 | 27
53QDMT48-518 | 0.28 | High | 1115 | 27 | 19 | 43 | 36835 | 24950 | 4300 | 27
53QDMT48-518 | 0.28 | High | 1115 | 27 | 19 | 46 | 35650 | 29595 | 4375 | 27
53QDMT48-518 | 0.28 | High | 1115 | 27 | 19 | 52 | 33285 | 28350 | 4525 | 27
53QDMT48-518 | 0.28 | High | 1115 | 32 | 23 | 35 | 43575 | 38350 | 4305 | 27
53QDMT48-518 | 0.28 | High | 1115 | 32 | 23 | 43 | 38095 | 32935 | 4475 | 27
53QDMT48-518 | 0.28 | High | 1115 | 32 | 23 | 46 | 37810 | 35920 | 4520 | 27
53QDMT48-518 | 0.28 | High | 1115 | 32 | 23 | 52 | 37245 | 37010 | 4615 | 27
53QDMT48-518 | 0.28 | Medium | 613 | 21 | 15 | 35 | 36585 | 28710 | 3730 | 27
53QDMT48-518 | 0.28 | Medium | 613 | 21 | 15 | 43 | 34025 | 23150 | 3845 | 27
53QDMT48-518 | 0.28 | Medium | 613 | 21 | 15 | 46 | 33270 | 36885 | 3890 | 27
53QDMT48-518 | 0.28 | Medium | 613 | 21 | 15 | 52 | 31750 | 26370 | 3970 | 27
53QDMT48-518 | 0.28 | Medium | 613 | 24 | 17 | 35 | 38630 | 30005 | 3905 | 27
53QDMT48-518 | 0.28 | Medium | 613 | 24 | 17 | 43 | 34500 | 23625 | 4105 | 27
53QDMT48-518 | 0.28 | Medium | 613 | 24 | 17 | 46 | 33740 | 27485 | 4180 | 27
53QDMT48-518 | 0.28 | Medium | 613 | 24 | 17 | 52 | 32210 | 26915 | 4328 | 27
53QDMT48-518 | 0.28 | Medium | 613 | 27 | 19 | 35 | 40225 | 30085 | 3970 | 27
53QDMT48-518 | 0.28 | Medium | 613 | 27 | 19 | 43 | 35360 | 22955 | 4170 | 27
53QDMT48-518 | 0.28 | Medium | 613 | 27 | 19 | 46 | 34225 | 27230 | 4245 | 27
53QDMT48-518 | 0.28 | Medium | 613 | 27 | 19 | 52 | 31955 | 26085 | 4390 | 27
53QDMT48-518 | 0.28 | Medium | 613 | 32 | 23 | 35 | 41835 | 35285 | 4175 | 27
53QDMT48-518 | 0.28 | Medium | 613 | 32 | 23 | 43 | 36575 | 30305 | 4340 | 27
53QDMT48-518 | 0.28 | Medium | 613 | 32 | 23 | 46 | 36300 | 33050 | 4385 | 27
53QDMT48-518 | 0.28 | Medium | 613 | 32 | 23 | 52 | 35760 | 34050 | 4480 | 27
53QDMT48-518 | 0.28 | Low | 377 | 21 | 15 | 35 | 35870 | 26525 | 3575 | 27
53QDMT48-518 | 0.28 | Low | 377 | 21 | 15 | 43 | 32615 | 21390 | 3690 | 27
53QDMT48-518 | 0.28 | Low | 377 | 21 | 15 | 46 | 31885 | 25050 | 3725 | 27
53QDMT48-518 | 0.28 | Low | 377 | 21 | 15 | 52 | 30425 | 24360 | 3805 | 27
53QDMT48-518 | 0.28 | Low | 377 | 24 | 17 | 35 | 37020 | 27725 | 3740 | 27
53QDMT48-518 | 0.28 | Low | 377 | 24 | 17 | 43 | 33065 | 21830 | 3935 | 27
53QDMT48-518 | 0.28 | Low | 377 | 24 | 17 | 46 | 32335 | 25390 | 4005 | 27
53QDMT48-518 | 0.28 | Low | 377 | 24 | 17 | 52 | 30870 | 24870 | 4155 | 27
53QDMT48-518 | 0.28 | Low | 377 | 27 | 19 | 35 | 38550 | 27795 | 3805 | 27
53QDMT48-518 | 0.28 | Low | 377 | 27 | 19 | 43 | 33890 | 21210 | 3995 | 27
53QDMT48-518 | 0.28 | Low | 377 | 27 | 19 | 46 | 32800 | 25160 | 3720 | 27
53QDMT48-518 | 0.28 | Low | 377 | 27 | 19 | 52 | 30625 | 24100 | 4210 | 27
53QDMT48-518 | 0.28 | Low | 377 | 21 | 23 | 35 | 40095 | 32600 | 4000 | 27
53QDMT48-518 | 0.28 | Low | 377 | 21 | 23 | 43 | 35050 | 27995 | 4165 | 27
53QDMT48-518 | 0.28 | Low | 377 | 21 | 23 | 46 | 34790 | 30535 | 4205 | 27
53QDMT48-518 | 0.28 | Low | 377 | 21 | 23 | 52 | 34265 | 31460 | 4295 | 27
53QDMT48-518 | 0.32 | High | 1079 | 21 | 15 | 35 | 38645 | 30930 | 3830 | 27
53QDMT48-518 | 0.32 | High | 1079 | 21 | 15 | 43 | 36975 | 31155 | 3950 | 27
53QDMT48-518 | 0.32 | High | 1079 | 21 | 15 | 46 | 36150 | 30740 | 3990 | 27
53QDMT48-518 | 0.32 | High | 1079 | 21 | 15 | 52 | 34500 | 29895 | 4075 | 27
53QDMT48-518 | 0.32 | High | 1079 | 24 | 17 | 35 | 39885 | 32325 | 4015 | 27
53QDMT48-518 | 0.32 | High | 1079 | 24 | 17 | 43 | 37400 | 31400 | 4220 | 27
53QDMT48-518 | 0.32 | High | 1079 | 24 | 17 | 46 | 36565 | 31080 | 4300 | 27
53QDMT48-518 | 0.32 | High | 1079 | 24 | 17 | 52 | 34910 | 30435 | 4455 | 27
53QDMT48-518 | 0.32 | High | 1079 | 27 | 19 | 35 | 41530 | 32405 | 4075 | 27
53QDMT48-518 | 0.32 | High | 1079 | 27 | 19 | 43 | 38625 | 31682 | 4275 | 27
53QDMT48-518 | 0.32 | High | 1079 | 27 | 19 | 46 | 37380 | 31030 | 4355 | 27
53QDMT48-518 | 0.32 | High | 1079 | 27 | 19 | 52 | 34895 | 29725 | 4505 | 27
53QDMT48-518 | 0.32 | High | 1079 | 32 | 23 | 35 | 43190 | 38005 | 4290 | 27
53QDMT48-518 | 0.32 | High | 1079 | 32 | 23 | 43 | 38920 | 37090 | 4460 | 27
53QDMT48-518 | 0.32 | High | 1079 | 32 | 23 | 46 | 38635 | 36700 | 4505 | 27
53QDMT48-518 | 0.32 | High | 1079 | 32 | 23 | 52 | 38055 | 37815 | 4600 | 27
53QDMT48-518 | 0.32 | Medium | 573 | 21 | 15 | 35 | 37100 | 28455 | 3715 | 27
53QDMT48-518 | 0.32 | Medium | 573 | 21 | 15 | 43 | 35500 | 28665 | 3830 | 27
53QDMT48-518 | 0.32 | Medium | 573 | 21 | 15 | 46 | 34705 | 28285 | 3870 | 27
53QDMT48-518 | 0.32 | Medium | 573 | 21 | 15 | 52 | 33115 | 27505 | 3955 | 27
53QDMT48-518 | 0.32 | Medium | 573 | 24 | 17 | 35 | 38290 | 29745 | 3895 | 27
53QDMT48-518 | 0.32 | Medium | 573 | 24 | 17 | 43 | 35900 | 28890 | 4095 | 27
53QDMT48-518 | 0.32 | Medium | 573 | 24 | 17 | 46 | 35100 | 28595 | 4170 | 27
53QDMT48-518 | 0.32 | Medium | 573 | 24 | 17 | 52 | 33520 | 28000 | 4320 | 27
53QDMT48-518 | 0.32 | Medium | 573 | 27 | 19 | 35 | 39870 | 29810 | 3955 | 27
53QDMT48-518 | 0.32 | Medium | 573 | 27 | 19 | 43 | 37080 | 29150 | 4150 | 27
53QDMT48-518 | 0.32 | Medium | 573 | 27 | 19 | 46 | 35890 | 28550 | 4225 | 27
53QDMT48-518 | 0.32 | Medium | 573 | 27 | 19 | 52 | 33505 | 27345 | 4370 | 27
53QDMT48-518 | 0.32 | Medium | 573 | 32 | 23 | 35 | 41465 | 34970 | 4160 | 27
53QDMT48-518 | 0.32 | Medium | 573 | 32 | 23 | 43 | 37365 | 34125 | 4325 | 27
53QDMT48-518 | 0.32 | Medium | 573 | 32 | 23 | 46 | 37090 | 33765 | 4370 | 27
53QDMT48-518 | 0.32 | Medium | 573 | 32 | 23 | 52 | 36535 | 34795 | 4465 | 27
53QDMT48-518 | 0.32 | Low | 320 | 21 | 15 | 35 | 35550 | 26295 | 3565 | 27
53QDMT48-518 | 0.32 | Low | 320 | 21 | 15 | 43 | 34020 | 26485 | 3675 | 27
53QDMT48-518 | 0.32 | Low | 320 | 21 | 15 | 46 | 33260 | 26135 | 3710 | 27
53QDMT48-518 | 0.32 | Low | 320 | 21 | 15 | 52 | 31740 | 25410 | 3790 | 27
53QDMT48-518 | 0.32 | Low | 320 | 24 | 17 | 35 | 36695 | 27480 | 3730 | 27
53QDMT48-518 | 0.32 | Low | 320 | 24 | 17 | 43 | 34405 | 26690 | 3925 | 27
53QDMT48-518 | 0.32 | Low | 320 | 24 | 17 | 46 | 33640 | 26420 | 3995 | 27
53QDMT48-518 | 0.32 | Low | 320 | 24 | 17 | 52 | 32120 | 25875 | 4140 | 27
53QDMT48-518 | 0.32 | Low | 320 | 27 | 19 | 35 | 38210 | 27545 | 3790 | 27
53QDMT48-518 | 0.32 | Low | 320 | 27 | 19 | 43 | 35540 | 26935 | 3980 | 27
53QDMT48-518 | 0.32 | Low | 320 | 27 | 19 | 46 | 34395 | 26380 | 4055 | 27
53QDMT48-518 | 0.32 | Low | 320 | 27 | 19 | 52 | 32110 | 25270 | 4190 | 27
53QDMT48-518 | 0.32 | Low | 320 | 21 | 23 | 35 | 39740 | 32310 | 3985 | 27
53QDMT48-518 | 0.32 | Low | 320 | 21 | 23 | 43 | 35810 | 31530 | 4150 | 27
53QDMT48-518 | 0.32 | Low | 320 | 21 | 23 | 46 | 35545 | 31200 | 4190 | 27
53QDMT48-518 | 0.32 | Low | 320 | 21 | 23 | 52 | 35015 | 32145 | 4275 | 27
53QDMT48-518 | 0.36 | High | 1043 | 21 | 15 | 35 | 38300 | 30655 | 3815 | 27
53QDMT48-518 | 0.36 | High | 1043 | 21 | 15 | 43 | 36650 | 30880 | 3935 | 27
53QDMT48-518 | 0.36 | High | 1043 | 21 | 15 | 46 | 35830 | 30470 | 3975 | 27
53QDMT48-518 | 0.36 | High | 1043 | 21 | 15 | 52 | 34190 | 29630 | 4060 | 27
53QDMT48-518 | 0.36 | High | 1043 | 24 | 17 | 35 | 39535 | 32040 | 4000 | 27
53QDMT48-518 | 0.36 | High | 1043 | 24 | 17 | 43 | 37060 | 31125 | 4210 | 27
53QDMT48-518 | 0.36 | High | 1043 | 24 | 17 | 46 | 36240 | 30805 | 4290 | 27
53QDMT48-518 | 0.36 | High | 1043 | 24 | 17 | 52 | 34605 | 30170 | 4445 | 27
53QDMT48-518 | 0.36 | High | 1043 | 27 | 19 | 35 | 41155 | 32115 | 4060 | 27
53QDMT48-518 | 0.36 | High | 1043 | 27 | 19 | 43 | 38280 | 31405 | 4260 | 27
53QDMT48-518 | 0.36 | High | 1043 | 27 | 19 | 46 | 37050 | 30755 | 4340 | 27
53QDMT48-518 | 0.36 | High | 1043 | 27 | 19 | 52 | 34590 | 29460 | 4490 | 27
53QDMT48-518 | 0.36 | High | 1043 | 32 | 23 | 35 | 42805 | 37665 | 4270 | 27
53QDMT48-518 | 0.36 | High | 1043 | 32 | 23 | 43 | 38575 | 36760 | 4445 | 27
53QDMT48-518 | 0.36 | High | 1043 | 32 | 23 | 46 | 38290 | 36375 | 4490 | 27
53QDMT48-518 | 0.36 | High | 1043 | 32 | 23 | 52 | 37715 | 37480 | 4585 | 27
53QDMT48-518 | 0.36 | Medium | 533 | 21 | 15 | 35 | 36770 | 28204 | 3700 | 27
53QDMT48-518 | 0.36 | Medium | 533 | 21 | 15 | 43 | 35185 | 28415 | 3820 | 27
53QDMT48-518 | 0.36 | Medium | 533 | 21 | 15 | 46 | 34400 | 28035 | 3855 | 27
53QDMT48-518 | 0.36 | Medium | 533 | 21 | 15 | 52 | 32825 | 27260 | 3940 | 27
53QDMT48-518 | 0.36 | Medium | 533 | 24 | 17 | 35 | 37955 | 29480 | 3885 | 27
53QDMT48-518 | 0.36 | Medium | 533 | 24 | 17 | 43 | 35580 | 28640 | 4085 | 27
53QDMT48-518 | 0.36 | Medium | 533 | 24 | 17 | 46 | 34795 | 28340 | 4160 | 27
53QDMT48-518 | 0.36 | Medium | 533 | 24 | 17 | 52 | 33225 | 27760 | 4310 | 27
53QDMT48-518 | 0.36 | Medium | 533 | 27 | 19 | 35 | 39515 | 29545 | 3940 | 27
53QDMT48-518 | 0.36 | Medium | 533 | 27 | 19 | 43 | 36750 | 28890 | 4135 | 27
53QDMT48-518 | 0.36 | Medium | 533 | 27 | 19 | 46 | 35570 | 28295 | 4210 | 27
53QDMT48-518 | 0.36 | Medium | 533 | 27 | 19 | 52 | 33210 | 27105 | 4355 | 27
53QDMT48-518 | 0.36 | Medium | 533 | 32 | 23 | 35 | 41095 | 34655 | 4145 | 27
53QDMT48-518 | 0.36 | Medium | 533 | 32 | 23 | 43 | 37035 | 33820 | 4310 | 27
53QDMT48-518 | 0.36 | Medium | 533 | 32 | 23 | 46 | 36760 | 33465 | 4355 | 27
53QDMT48-518 | 0.36 | Medium | 533 | 32 | 23 | 52 | 36210 | 34485 | 4450 | 27
53QDMT48-518 | 0.36 | Low | 263 | 21 | 15 | 35 | 35235 | 26059 | 3400 | 27
53QDMT48-518 | 0.36 | Low | 263 | 21 | 15 | 43 | 33720 | 26250 | 3660 | 27
53QDMT48-518 | 0.36 | Low | 263 | 21 | 15 | 46 | 32965 | 25900 | 3700 | 27
53QDMT48-518 | 0.36 | Low | 263 | 21 | 15 | 52 | 31455 | 25190 | 3775 | 27
53QDMT48-518 | 0.36 | Low | 263 | 24 | 17 | 35 | 36370 | 27235 | 3720 | 27
53QDMT48-518 | 0.36 | Low | 263 | 24 | 17 | 43 | 34100 | 26455 | 3915 | 27
53QDMT48-518 | 0.36 | Low | 263 | 24 | 17 | 46 | 33345 | 26185 | 4000 | 27
53QDMT48-518 | 0.36 | Low | 263 | 24 | 17 | 52 | 31835 | 25650 | 4130 | 27
53QDMT48-518 | 0.36 | Low | 263 | 27 | 19 | 35 | 37865 | 27299 | 3775 | 27
53QDMT48-518 | 0.36 | Low | 263 | 27 | 19 | 43 | 35220 | 26695 | 3965 | 27
53QDMT48-518 | 0.36 | Low | 263 | 27 | 19 | 46 | 34090 | 26145 | 4040 | 27
53QDMT48-518 | 0.36 | Low | 263 | 27 | 19 | 52 | 31825 | 25045 | 4175 | 27
53QDMT48-518 | 0.36 | Low | 263 | 21 | 23 | 35 | 39380 | 32018 | 3975 | 27
53QDMT48-518 | 0.36 | Low | 263 | 21 | 23 | 43 | 35490 | 31245 | 4135 | 27
53QDMT48-518 | 0.36 | Low | 263 | 21 | 23 | 46 | 35230 | 30920 | 4175 | 27
53QDMT48-518 | 0.36 | Low | 263 | 21 | 23 | 52 | 34700 | 31860 | 4265 | 27
53QDMT48-518 | 0.4 | High | 1007 | 21 | 15 | 35 | 37960 | 30382 | 3800 | 27
53QDMT48-518 | 0.4 | High | 1007 | 21 | 15 | 43 | 36320 | 30605 | 3920 | 27
53QDMT48-518 | 0.4 | High | 1007 | 21 | 15 | 46 | 35510 | 30200 | 3960 | 27
53QDMT48-518 | 0.4 | High | 1007 | 21 | 15 | 52 | 33885 | 29365 | 4045 | 27
53QDMT48-518 | 0.4 | High | 1007 | 24 | 17 | 35 | 39180 | 31756 | 3990 | 27
53QDMT48-518 | 0.4 | High | 1007 | 24 | 17 | 43 | 36730 | 30850 | 4200 | 27
53QDMT48-518 | 0.4 | High | 1007 | 24 | 17 | 46 | 35920 | 30530 | 4275 | 27
53QDMT48-518 | 0.4 | High | 1007 | 24 | 17 | 52 | 34295 | 29905 | 4435 | 27
53QDMT48-518 | 0.4 | High | 1007 | 27 | 19 | 35 | 40785 | 31824 | 4045 | 27
53QDMT48-518 | 0.4 | High | 1007 | 27 | 19 | 43 | 37935 | 31120 | 4245 | 27
53QDMT48-518 | 0.4 | High | 1007 | 27 | 19 | 46 | 36715 | 30475 | 4325 | 27
53QDMT48-518 | 0.4 | High | 1007 | 27 | 19 | 52 | 34280 | 29200 | 4475 | 27
53QDMT48-518 | 0.4 | High | 1007 | 32 | 23 | 35 | 42420 | 37320 | 4255 | 27
53QDMT48-518 | 0.4 | High | 1007 | 32 | 23 | 43 | 38225 | 36430 | 4430 | 27
53QDMT48-518 | 0.4 | High | 1007 | 32 | 23 | 46 | 37945 | 36045 | 4475 | 27
53QDMT48-518 | 0.4 | High | 1007 | 32 | 23 | 52 | 37375 | 37140 | 4570 | 27
53QDMT48-518 | 0.4 | Medium | 493 | 21 | 15 | 35 | 36440 | 27951 | 3685 | 27
53QDMT48-518 | 0.4 | Medium | 493 | 21 | 15 | 43 | 34870 | 28160 | 3805 | 27
53QDMT48-518 | 0.4 | Medium | 493 | 21 | 15 | 46 | 34090 | 27780 | 3840 | 27
53QDMT48-518 | 0.4 | Medium | 493 | 21 | 15 | 52 | 32530 | 27020 | 3925 | 27
53QDMT48-518 | 0.4 | Medium | 493 | 24 | 17 | 35 | 37615 | 29218 | 3870 | 27
53QDMT48-518 | 0.4 | Medium | 493 | 24 | 17 | 43 | 35265 | 28385 | 4075 | 27
53QDMT48-518 | 0.4 | Medium | 493 | 24 | 17 | 46 | 34485 | 28090 | 4150 | 27
53QDMT48-518 | 0.4 | Medium | 493 | 24 | 17 | 52 | 32930 | 27515 | 4305 | 27
53QDMT48-518 | 0.4 | Medium | 493 | 27 | 19 | 35 | 39155 | 29281 | 3925 | 27
53QDMT48-518 | 0.4 | Medium | 493 | 27 | 19 | 43 | 36420 | 28635 | 4120 | 27
53QDMT48-518 | 0.4 | Medium | 493 | 27 | 19 | 46 | 35250 | 28040 | 4195 | 27
53QDMT48-518 | 0.4 | Medium | 493 | 27 | 19 | 52 | 32910 | 26870 | 4340 | 27
53QDMT48-518 | 0.4 | Medium | 493 | 32 | 23 | 35 | 40720 | 34342 | 4130 | 27
53QDMT48-518 | 0.4 | Medium | 493 | 32 | 23 | 43 | 36700 | 33515 | 4300 | 27
53QDMT48-518 | 0.4 | Medium | 493 | 32 | 23 | 46 | 36430 | 33165 | 4340 | 27
53QDMT48-518 | 0.4 | Medium | 493 | 32 | 23 | 52 | 35885 | 34175 | 4435 | 27
53QDMT48-518 | 0.4 | Low | 206 | 21 | 15 | 35 | 34920 | 25824 | 3235 | 27
53QDMT48-518 | 0.4 | Low | 206 | 21 | 15 | 43 | 33415 | 26015 | 3645 | 27
53QDMT48-518 | 0.4 | Low | 206 | 21 | 15 | 46 | 32670 | 25670 | 3685 | 27
53QDMT48-518 | 0.4 | Low | 206 | 21 | 15 | 52 | 31175 | 24965 | 3765 | 27
53QDMT48-518 | 0.4 | Low | 206 | 24 | 17 | 35 | 36045 | 26993 | 3710 | 27
53QDMT48-518 | 0.4 | Low | 206 | 24 | 17 | 43 | 33795 | 26220 | 3910 | 27
53QDMT48-518 | 0.4 | Low | 206 | 24 | 17 | 46 | 33050 | 25955 | 3980 | 27
53QDMT48-518 | 0.4 | Low | 206 | 24 | 17 | 52 | 31550 | 25420 | 4120 | 27
53QDMT48-518 | 0.4 | Low | 206 | 27 | 19 | 35 | 37525 | 27051 | 3765 | 27
53QDMT48-518 | 0.4 | Low | 206 | 27 | 19 | 43 | 34900 | 26455 | 3950 | 27
53QDMT48-518 | 0.4 | Low | 206 | 27 | 19 | 46 | 33780 | 25910 | 4025 | 27
53QDMT48-518 | 0.4 | Low | 206 | 27 | 19 | 52 | 31545 | 24825 | 4165 | 27
53QDMT48-518 | 0.4 | Low | 206 | 21 | 23 | 35 | 39025 | 31726 | 3960 | 27
53QDMT48-518 | 0.4 | Low | 206 | 21 | 23 | 43 | 35170 | 30965 | 4120 | 27
53QDMT48-518 | 0.4 | Low | 206 | 21 | 23 | 46 | 34910 | 30645 | 4165 | 27
53QDMT48-518 | 0.4 | Low | 206 | 21 | 23 | 52 | 34390 | 31570 | 4250 | 27
53QDMT60-518 | 0 | High | 1470 | 21 | 15 | 35 | 48640 | 38900 | 4445 | 28
53QDMT60-518 | 0 | High | 1470 | 21 | 15 | 43 | 46550 | 39100 | 4590 | 28
53QDMT60-518 | 0 | High | 1470 | 21 | 15 | 46 | 45505 | 38685 | 4635 | 28
53QDMT60-518 | 0 | High | 1470 | 21 | 15 | 52 | 43415 | 37855 | 4725 | 28
53QDMT60-518 | 0 | High | 1470 | 24 | 17 | 35 | 50210 | 40665 | 4630 | 28
53QDMT60-518 | 0 | High | 1470 | 24 | 17 | 43 | 47075 | 39560 | 4865 | 28
53QDMT60-518 | 0 | High | 1470 | 24 | 17 | 46 | 46030 | 39125 | 4955 | 28
53QDMT60-518 | 0 | High | 1470 | 24 | 17 | 52 | 43940 | 38255 | 5135 | 28
53QDMT60-518 | 0 | High | 1470 | 27 | 19 | 35 | 52300 | 40795 | 4725 | 28
53QDMT60-518 | 0 | High | 1470 | 27 | 19 | 43 | 48640 | 39880 | 4960 | 28
53QDMT60-518 | 0 | High | 1470 | 27 | 19 | 46 | 47075 | 39075 | 5050 | 28
53QDMT60-518 | 0 | High | 1470 | 27 | 19 | 52 | 43945 | 37465 | 5230 | 28
53QDMT60-518 | 0 | High | 1470 | 32 | 23 | 35 | 54395 | 47860 | 4960 | 28
53QDMT60-518 | 0 | High | 1470 | 32 | 23 | 43 | 50215 | 46685 | 5150 | 28
53QDMT60-518 | 0 | High | 1470 | 32 | 23 | 46 | 48650 | 46220 | 5200 | 28
53QDMT60-518 | 0 | High | 1470 | 32 | 23 | 52 | 45520 | 45290 | 5300 | 28
53QDMT60-518 | 0 | Medium | 1020 | 21 | 15 | 35 | 46695 | 35790 | 4315 | 28
53QDMT60-518 | 0 | Medium | 1020 | 21 | 15 | 43 | 44690 | 35975 | 4440 | 28
53QDMT60-518 | 0 | Medium | 1020 | 21 | 15 | 46 | 43685 | 35590 | 4485 | 28
53QDMT60-518 | 0 | Medium | 1020 | 21 | 15 | 52 | 41680 | 34830 | 4575 | 28
53QDMT60-518 | 0 | Medium | 1020 | 24 | 17 | 35 | 48205 | 37415 | 4490 | 28
53QDMT60-518 | 0 | Medium | 1020 | 24 | 17 | 43 | 45195 | 36395 | 4700 | 28
53QDMT60-518 | 0 | Medium | 1020 | 24 | 17 | 46 | 44190 | 35995 | 4785 | 28
53QDMT60-518 | 0 | Medium | 1020 | 24 | 17 | 52 | 42185 | 35195 | 4955 | 28
53QDMT60-518 | 0 | Medium | 1020 | 27 | 19 | 35 | 50210 | 37535 | 4585 | 28
53QDMT60-518 | 0 | Medium | 1020 | 27 | 19 | 43 | 46695 | 36690 | 4795 | 28
53QDMT60-518 | 0 | Medium | 1020 | 27 | 19 | 46 | 45195 | 35950 | 4880 | 28
53QDMT60-518 | 0 | Medium | 1020 | 27 | 19 | 52 | 42190 | 34470 | 5050 | 28
53QDMT60-518 | 0 | Medium | 1020 | 32 | 23 | 35 | 52220 | 44035 | 4810 | 28
53QDMT60-518 | 0 | Medium | 1020 | 32 | 23 | 43 | 48210 | 42950 | 4980 | 28
53QDMT60-518 | 0 | Medium | 1020 | 32 | 23 | 46 | 46705 | 42525 | 5030 | 28
53QDMT60-518 | 0 | Medium | 1020 | 32 | 23 | 52 | 43700 | 41670 | 5130 | 28
53QDMT60-518 | 0 | Low | 860 | 21 | 15 | 35 | 44750 | 33065 | 4135 | 28
53QDMT60-518 | 0 | Low | 860 | 21 | 15 | 43 | 42830 | 33235 | 4270 | 28
53QDMT60-518 | 0 | Low | 860 | 21 | 15 | 46 | 41865 | 32885 | 4315 | 28
53QDMT60-518 | 0 | Low | 860 | 21 | 15 | 52 | 39945 | 32180 | 4405 | 28
53QDMT60-518 | 0 | Low | 860 | 24 | 17 | 35 | 46195 | 34565 | 4305 | 28
53QDMT60-518 | 0 | Low | 860 | 24 | 17 | 43 | 43310 | 33630 | 4530 | 28
53QDMT60-518 | 0 | Low | 860 | 24 | 17 | 46 | 42350 | 33260 | 4610 | 28
53QDMT60-518 | 0 | Low | 860 | 24 | 17 | 52 | 40425 | 32520 | 4770 | 28
53QDMT60-518 | 0 | Low | 860 | 27 | 19 | 35 | 48120 | 34675 | 4395 | 28
53QDMT60-518 | 0 | Low | 860 | 27 | 19 | 43 | 44750 | 33900 | 4615 | 28
53QDMT60-518 | 0 | Low | 860 | 27 | 19 | 46 | 43310 | 33215 | 4700 | 28
53QDMT60-518 | 0 | Low | 860 | 27 | 19 | 52 | 40430 | 31840 | 4870 | 28
53QDMT60-518 | 0 | Low | 860 | 21 | 23 | 35 | 50045 | 40685 | 4615 | 28
53QDMT60-518 | 0 | Low | 860 | 21 | 23 | 43 | 46200 | 39685 | 4790 | 28
53QDMT60-518 | 0 | Low | 860 | 21 | 23 | 46 | 44760 | 39290 | 4840 | 28
53QDMT60-518 | 0 | Low | 860 | 21 | 23 | 52 | 41880 | 38500 | 4940 | 28
53QDMT60-518 | 0.08 | High | 1405 | 21 | 15 | 35 | 47825 | 38250 | 4415 | 28
53QDMT60-518 | 0.08 | High | 1405 | 21 | 15 | 43 | 45770 | 38445 | 4558 | 28
53QDMT60-518 | 0.08 | High | 1405 | 21 | 15 | 46 | 44743 | 38040 | 4602 | 28
53QDMT60-518 | 0.08 | High | 1405 | 21 | 15 | 52 | 42690 | 37227 | 4692 | 28
53QDMT60-518 | 0.08 | High | 1405 | 24 | 17 | 35 | 49370 | 39985 | 4600 | 28
53QDMT60-518 | 0.08 | High | 1405 | 24 | 17 | 43 | 46285 | 38920 | 4830 | 28
53QDMT60-518 | 0.08 | High | 1405 | 24 | 17 | 46 | 45260 | 38470 | 4920 | 28
53QDMT60-518 | 0.08 | High | 1405 | 24 | 17 | 52 | 43208 | 37573 | 5097 | 28
53QDMT60-518 | 0.08 | High | 1405 | 27 | 19 | 35 | 51420 | 40610 | 4690 | 28
53QDMT60-518 | 0.08 | High | 1405 | 27 | 19 | 43 | 47825 | 39215 | 4925 | 28
53QDMT60-518 | 0.08 | High | 1405 | 27 | 19 | 46 | 46285 | 38423 | 5015 | 28
53QDMT60-518 | 0.08 | High | 1405 | 27 | 19 | 52 | 43210 | 36837 | 5194 | 28
53QDMT60-518 | 0.08 | High | 1405 | 32 | 23 | 35 | 53485 | 47060 | 4925 | 28
53QDMT60-518 | 0.08 | High | 1405 | 32 | 23 | 43 | 49370 | 45905 | 5115 | 28
53QDMT60-518 | 0.08 | High | 1405 | 32 | 23 | 46 | 47835 | 45448 | 5165 | 28
53QDMT60-518 | 0.08 | High | 1405 | 32 | 23 | 52 | 44765 | 44538 | 5264 | 28
53QDMT60-518 | 0.08 | Medium | 968 | 21 | 15 | 35 | 45915 | 35190 | 4285 | 28
53QDMT60-518 | 0.08 | Medium | 968 | 21 | 15 | 43 | 43940 | 35375 | 4410 | 28
53QDMT60-518 | 0.08 | Medium | 968 | 21 | 15 | 46 | 42955 | 34883 | 4455 | 28
53QDMT60-518 | 0.08 | Medium | 968 | 21 | 15 | 52 | 40985 | 34253 | 4545 | 28
53QDMT60-518 | 0.08 | Medium | 968 | 24 | 17 | 35 | 47400 | 36790 | 4460 | 28
53QDMT60-518 | 0.08 | Medium | 968 | 24 | 17 | 43 | 44440 | 35785 | 4665 | 28
53QDMT60-518 | 0.08 | Medium | 968 | 24 | 17 | 46 | 43450 | 35395 | 4750 | 28
53QDMT60-518 | 0.08 | Medium | 968 | 24 | 17 | 52 | 41483 | 34568 | 4920 | 28
53QDMT60-518 | 0.08 | Medium | 968 | 27 | 19 | 35 | 49370 | 37365 | 4555 | 28
53QDMT60-518 | 0.08 | Medium | 968 | 27 | 19 | 43 | 45920 | 36075 | 4758 | 28
53QDMT60-518 | 0.08 | Medium | 968 | 27 | 19 | 46 | 44438 | 35350 | 4843 | 28
53QDMT60-518 | 0.08 | Medium | 968 | 27 | 19 | 52 | 41484 | 33893 | 5013 | 28
53QDMT60-518 | 0.08 | Medium | 968 | 32 | 23 | 35 | 51345 | 43295 | 4780 | 28
53QDMT60-518 | 0.08 | Medium | 968 | 32 | 23 | 43 | 47405 | 42235 | 4945 | 28
53QDMT60-518 | 0.08 | Medium | 968 | 32 | 23 | 46 | 45923 | 41815 | 4995 | 28
53QDMT60-518 | 0.08 | Medium | 968 | 32 | 23 | 52 | 42975 | 40978 | 5095 | 28
53QDMT60-518 | 0.08 | Low | 800 | 21 | 15 | 35 | 44000 | 32510 | 4105 | 28
53QDMT60-518 | 0.08 | Low | 800 | 21 | 15 | 43 | 32720 | 32680 | 4243 | 28
53QDMT60-518 | 0.08 | Low | 800 | 21 | 15 | 46 | 41165 | 32230 | 4288 | 28
53QDMT60-518 | 0.08 | Low | 800 | 21 | 15 | 52 | 39280 | 31645 | 4378 | 28
53QDMT60-518 | 0.08 | Low | 800 | 24 | 17 | 35 | 45420 | 33990 | 4280 | 28
53QDMT60-518 | 0.08 | Low | 800 | 24 | 17 | 43 | 42585 | 33065 | 4498 | 28
53QDMT60-518 | 0.08 | Low | 800 | 24 | 17 | 46 | 41640 | 31220 | 4578 | 28
53QDMT60-518 | 0.08 | Low | 800 | 24 | 17 | 52 | 39752 | 31940 | 4738 | 28
53QDMT60-518 | 0.08 | Low | 800 | 27 | 19 | 35 | 47310 | 34520 | 4365 | 28
53QDMT60-518 | 0.08 | Low | 800 | 27 | 19 | 43 | 44000 | 33330 | 4580 | 28
53QDMT60-518 | 0.08 | Low | 800 | 27 | 19 | 46 | 42585 | 31380 | 4665 | 28
53QDMT60-518 | 0.08 | Low | 800 | 27 | 19 | 52 | 39755 | 31310 | 4835 | 28
53QDMT60-518 | 0.08 | Low | 800 | 21 | 23 | 35 | 49210 | 40005 | 4495 | 28
53QDMT60-518 | 0.08 | Low | 800 | 21 | 23 | 43 | 45425 | 39020 | 4665 | 28
53QDMT60-518 | 0.08 | Low | 800 | 21 | 23 | 46 | 44015 | 37115 | 4735 | 28
53QDMT60-518 | 0.08 | Low | 800 | 21 | 23 | 52 | 41185 | 37860 | 4875 | 28
53QDMT60-518 | 0.12 | High | 1380 | 21 | 15 | 35 | 47415 | 37920 | 4395 | 28
53QDMT60-518 | 0.12 | High | 1380 | 21 | 15 | 43 | 45380 | 38120 | 4540 | 28
53QDMT60-518 | 0.12 | High | 1380 | 21 | 15 | 46 | 44365 | 37720 | 4585 | 28
53QDMT60-518 | 0.12 | High | 1380 | 21 | 15 | 52 | 42335 | 36920 | 4675 | 28
53QDMT60-518 | 0.12 | High | 1380 | 24 | 17 | 35 | 48945 | 39645 | 4580 | 28
53QDMT60-518 | 0.12 | High | 1380 | 24 | 17 | 43 | 45890 | 38656 | 4815 | 28
53QDMT60-518 | 0.12 | High | 1380 | 24 | 17 | 46 | 44875 | 38145 | 4905 | 28
53QDMT60-518 | 0.12 | High | 1380 | 24 | 17 | 52 | 42845 | 37125 | 5085 | 28
53QDMT60-518 | 0.12 | High | 1380 | 27 | 19 | 35 | 50980 | 40775 | 4675 | 28
53QDMT60-518 | 0.12 | High | 1380 | 27 | 19 | 43 | 47415 | 38880 | 4910 | 28
53QDMT60-518 | 0.12 | High | 1380 | 27 | 19 | 46 | 45890 | 38095 | 5000 | 28
53QDMT60-518 | 0.12 | High | 1380 | 27 | 19 | 52 | 42840 | 36525 | 5180 | 28
53QDMT60-518 | 0.12 | High | 1380 | 32 | 23 | 35 | 53025 | 46655 | 4910 | 28
53QDMT60-518 | 0.12 | High | 1380 | 32 | 23 | 43 | 48950 | 45510 | 5100 | 28
53QDMT60-518 | 0.12 | High | 1380 | 32 | 23 | 46 | 47425 | 45060 | 5150 | 28
53QDMT60-518 | 0.12 | High | 1380 | 32 | 23 | 52 | 44375 | 44160 | 5250 | 28
53QDMT60-518 | 0.12 | Medium | 948 | 21 | 15 | 35 | 45520 | 34890 | 4265 | 28
53QDMT60-518 | 0.12 | Medium | 948 | 21 | 15 | 43 | 43565 | 35070 | 4395 | 28
53QDMT60-518 | 0.12 | Medium | 948 | 21 | 15 | 46 | 42590 | 34245 | 4440 | 28
53QDMT60-518 | 0.12 | Medium | 948 | 21 | 15 | 52 | 40645 | 33970 | 4530 | 28
53QDMT60-518 | 0.12 | Medium | 948 | 24 | 17 | 35 | 46990 | 36475 | 4445 | 28
53QDMT60-518 | 0.12 | Medium | 948 | 24 | 17 | 43 | 44055 | 35480 | 4650 | 28
53QDMT60-518 | 0.12 | Medium | 948 | 24 | 17 | 46 | 43080 | 35095 | 4735 | 28
53QDMT60-518 | 0.12 | Medium | 948 | 24 | 17 | 52 | 41135 | 34155 | 4905 | 28
53QDMT60-518 | 0.12 | Medium | 948 | 27 | 19 | 35 | 48945 | 37515 | 4535 | 28
53QDMT60-518 | 0.12 | Medium | 948 | 27 | 19 | 43 | 45520 | 35770 | 4740 | 28
53QDMT60-518 | 0.12 | Medium | 948 | 27 | 19 | 46 | 44055 | 35050 | 4825 | 28
53QDMT60-518 | 0.12 | Medium | 948 | 27 | 19 | 52 | 41126 | 33605 | 4995 | 28
53QDMT60-518 | 0.12 | Medium | 948 | 32 | 23 | 35 | 50905 | 42925 | 4765 | 28
53QDMT60-518 | 0.12 | Medium | 948 | 32 | 23 | 43 | 46995 | 41870 | 4930 | 28
53QDMT60-518 | 0.12 | Medium | 948 | 32 | 23 | 46 | 45530 | 41455 | 4980 | 28
53QDMT60-518 | 0.12 | Medium | 948 | 32 | 23 | 52 | 42600 | 40630 | 5080 | 28
53QDMT60-518 | 0.12 | Low | 762 | 21 | 15 | 35 | 43625 | 32235 | 4090 | 28
53QDMT60-518 | 0.12 | Low | 762 | 21 | 15 | 43 | 4175 | 32405 | 4230 | 28
53QDMT60-518 | 0.12 | Low | 762 | 21 | 15 | 46 | 40820 | 31640 | 4275 | 28
53QDMT60-518 | 0.12 | Low | 762 | 21 | 15 | 52 | 38950 | 31385 | 4365 | 28
53QDMT60-518 | 0.12 | Low | 762 | 24 | 17 | 35 | 45030 | 33700 | 4265 | 28
53QDMT60-518 | 0.12 | Low | 762 | 24 | 17 | 43 | 42220 | 32780 | 4485 | 28
53QDMT60-518 | 0.12 | Low | 762 | 24 | 17 | 46 | 41285 | 29035 | 4565 | 28
53QDMT60-518 | 0.12 | Low | 762 | 24 | 17 | 52 | 39420 | 31560 | 4725 | 28
53QDMT60-518 | 0.12 | Low | 762 | 27 | 19 | 35 | 46905 | 34660 | 4345 | 28
53QDMT60-518 | 0.12 | Low | 762 | 27 | 19 | 43 | 43625 | 33050 | 4565 | 28
53QDMT60-518 | 0.12 | Low | 762 | 27 | 19 | 46 | 42220 | 29795 | 4650 | 28
53QDMT60-518 | 0.12 | Low | 762 | 27 | 19 | 52 | 39415 | 31050 | 4820 | 28
53QDMT60-518 | 0.12 | Low | 762 | 21 | 23 | 35 | 48785 | 39660 | 4430 | 28
53QDMT60-518 | 0.12 | Low | 762 | 21 | 23 | 43 | 45035 | 38685 | 4600 | 28
53QDMT60-518 | 0.12 | Low | 762 | 21 | 23 | 46 | 43635 | 35240 | 4740 | 28
53QDMT60-518 | 0.12 | Low | 762 | 21 | 23 | 52 | 40825 | 37540 | 5020 | 28
53QDMT60-518 | 0.16 | High | 1345 | 21 | 15 | 35 | 47010 | 37595 | 4380 | 28
53QDMT60-518 | 0.16 | High | 1345 | 21 | 15 | 43 | 44990 | 37790 | 4525 | 28
53QDMT60-518 | 0.16 | High | 1345 | 21 | 15 | 46 | 43980 | 37395 | 4568 | 28
53QDMT60-518 | 0.16 | High | 1345 | 21 | 15 | 52 | 41965 | 36598 | 4658 | 28
53QDMT60-518 | 0.16 | High | 1345 | 24 | 17 | 35 | 48525 | 39305 | 4565 | 28
53QDMT60-518 | 0.16 | High | 1345 | 24 | 17 | 43 | 45495 | 38280 | 4795 | 28
53QDMT60-518 | 0.16 | High | 1345 | 24 | 17 | 46 | 44490 | 37815 | 4885 | 28
53QDMT60-518 | 0.16 | High | 1345 | 24 | 17 | 52 | 42475 | 36890 | 5058 | 28
53QDMT60-518 | 0.16 | High | 1345 | 27 | 19 | 35 | 50540 | 40425 | 4655 | 28
53QDMT60-518 | 0.16 | High | 1345 | 27 | 19 | 43 | 47005 | 38550 | 4890 | 28
53QDMT60-518 | 0.16 | High | 1345 | 27 | 19 | 46 | 45495 | 37770 | 4980 | 28
53QDMT60-518 | 0.16 | High | 1345 | 27 | 19 | 52 | 42475 | 36208 | 5158 | 28
53QDMT60-518 | 0.16 | High | 1345 | 32 | 23 | 35 | 52570 | 46255 | 4890 | 28
53QDMT60-518 | 0.16 | High | 1345 | 32 | 23 | 43 | 48525 | 45120 | 5080 | 28
53QDMT60-518 | 0.16 | High | 1345 | 32 | 23 | 46 | 47020 | 44675 | 5130 | 28
53QDMT60-518 | 0.16 | High | 1345 | 32 | 23 | 52 | 44010 | 43785 | 5228 | 28
53QDMT60-518 | 0.16 | Medium | 914 | 21 | 15 | 35 | 45130 | 34590 | 4250 | 28
53QDMT60-518 | 0.16 | Medium | 914 | 21 | 15 | 43 | 43190 | 34770 | 4380 | 28
53QDMT60-518 | 0.16 | Medium | 914 | 21 | 15 | 46 | 42225 | 34175 | 4425 | 28
53QDMT60-518 | 0.16 | Medium | 914 | 21 | 15 | 52 | 40290 | 33675 | 4515 | 28
53QDMT60-518 | 0.16 | Medium | 914 | 24 | 17 | 35 | 46590 | 36160 | 4430 | 28
53QDMT60-518 | 0.16 | Medium | 914 | 24 | 17 | 43 | 43680 | 35175 | 4630 | 28
53QDMT60-518 | 0.16 | Medium | 914 | 24 | 17 | 46 | 42710 | 34795 | 4715 | 28
53QDMT60-518 | 0.16 | Medium | 914 | 24 | 17 | 52 | 40780 | 33940 | 4885 | 28
53QDMT60-518 | 0.16 | Medium | 914 | 27 | 19 | 35 | 48525 | 37190 | 4520 | 28
53QDMT60-518 | 0.16 | Medium | 914 | 27 | 19 | 43 | 45130 | 35460 | 4720 | 28
53QDMT60-518 | 0.16 | Medium | 914 | 27 | 19 | 46 | 43680 | 34750 | 4805 | 28
53QDMT60-518 | 0.16 | Medium | 914 | 27 | 19 | 52 | 40778 | 33315 | 4975 | 28
53QDMT60-518 | 0.16 | Medium | 914 | 32 | 23 | 35 | 50470 | 42555 | 4745 | 28
53QDMT60-518 | 0.16 | Medium | 914 | 32 | 23 | 43 | 46595 | 41515 | 4910 | 28
53QDMT60-518 | 0.16 | Medium | 914 | 32 | 23 | 46 | 45140 | 41105 | 4960 | 28
53QDMT60-518 | 0.16 | Medium | 914 | 32 | 23 | 52 | 42250 | 40285 | 5060 | 28
53QDMT60-518 | 0.16 | Low | 728 | 21 | 15 | 35 | 43250 | 31955 | 4075 | 28
53QDMT60-518 | 0.16 | Low | 728 | 21 | 15 | 43 | 22605 | 32125 | 4215 | 28
53QDMT60-518 | 0.16 | Low | 728 | 21 | 15 | 46 | 40465 | 31575 | 4260 | 28
53QDMT60-518 | 0.16 | Low | 728 | 21 | 15 | 52 | 38615 | 31110 | 4350 | 28
53QDMT60-518 | 0.16 | Low | 728 | 24 | 17 | 35 | 44645 | 33410 | 4250 | 28
53QDMT60-518 | 0.16 | Low | 728 | 24 | 17 | 43 | 41860 | 32500 | 4465 | 28
53QDMT60-518 | 0.16 | Low | 728 | 24 | 17 | 46 | 40930 | 29180 | 4545 | 28
53QDMT60-518 | 0.16 | Low | 728 | 24 | 17 | 52 | 39078 | 31360 | 4705 | 28
53QDMT60-518 | 0.16 | Low | 728 | 27 | 19 | 35 | 46500 | 34360 | 4330 | 28
53QDMT60-518 | 0.16 | Low | 728 | 27 | 19 | 43 | 43250 | 32760 | 4545 | 28
53QDMT60-518 | 0.16 | Low | 728 | 27 | 19 | 46 | 41860 | 29540 | 4630 | 28
53QDMT60-518 | 0.16 | Low | 728 | 27 | 19 | 52 | 39080 | 30780 | 4795 | 28
53QDMT60-518 | 0.16 | Low | 728 | 21 | 23 | 35 | 48370 | 39320 | 4370 | 28
53QDMT60-518 | 0.16 | Low | 728 | 21 | 23 | 43 | 44650 | 38355 | 4535 | 28
53QDMT60-518 | 0.16 | Low | 728 | 21 | 23 | 46 | 43265 | 34940 | 4625 | 28
53QDMT60-518 | 0.16 | Low | 728 | 21 | 23 | 52 | 40490 | 37220 | 4810 | 28
53QDMT60-518 | 0.2 | High | 1314 | 21 | 15 | 35 | 46600 | 37265 | 4360 | 28
53QDMT60-518 | 0.2 | High | 1314 | 21 | 15 | 43 | 44595 | 37460 | 4505 | 28
53QDMT60-518 | 0.2 | High | 1314 | 21 | 15 | 46 | 43595 | 37065 | 4550 | 28
53QDMT60-518 | 0.2 | High | 1314 | 21 | 15 | 52 | 41595 | 36275 | 4640 | 28
53QDMT60-518 | 0.2 | High | 1314 | 24 | 17 | 35 | 48105 | 38960 | 4545 | 28
53QDMT60-518 | 0.2 | High | 1314 | 24 | 17 | 43 | 45100 | 37900 | 4775 | 28
53QDMT60-518 | 0.2 | High | 1314 | 24 | 17 | 46 | 44100 | 37485 | 4860 | 28
53QDMT60-518 | 0.2 | High | 1314 | 24 | 17 | 52 | 42100 | 36655 | 5030 | 28
53QDMT60-518 | 0.2 | High | 1314 | 27 | 19 | 35 | 50100 | 40070 | 4635 | 28
53QDMT60-518 | 0.2 | High | 1314 | 27 | 19 | 43 | 46595 | 38215 | 4865 | 28
53QDMT60-518 | 0.2 | High | 1314 | 27 | 19 | 46 | 45100 | 37440 | 4955 | 28
53QDMT60-518 | 0.2 | High | 1314 | 27 | 19 | 52 | 42110 | 35890 | 5135 | 28
53QDMT60-518 | 0.2 | High | 1314 | 32 | 23 | 35 | 52115 | 45850 | 4870 | 28
53QDMT60-518 | 0.2 | High | 1314 | 32 | 23 | 43 | 48100 | 44730 | 5055 | 28
53QDMT60-518 | 0.2 | High | 1314 | 32 | 23 | 46 | 46615 | 44290 | 5105 | 28
53QDMT60-518 | 0.2 | High | 1314 | 32 | 23 | 52 | 43645 | 43410 | 5205 | 28
53QDMT60-518 | 0.2 | Medium | 880 | 21 | 15 | 35 | 44740 | 34285 | 4230 | 28
53QDMT60-518 | 0.2 | Medium | 880 | 21 | 15 | 43 | 42815 | 34465 | 4360 | 28
53QDMT60-518 | 0.2 | Medium | 880 | 21 | 15 | 46 | 41855 | 34100 | 4405 | 28
53QDMT60-518 | 0.2 | Medium | 880 | 21 | 15 | 52 | 39935 | 33375 | 4495 | 28
53QDMT60-518 | 0.2 | Medium | 880 | 24 | 17 | 35 | 46185 | 35845 | 4410 | 28
53QDMT60-518 | 0.2 | Medium | 880 | 24 | 17 | 43 | 43300 | 34870 | 4610 | 28
53QDMT60-518 | 0.2 | Medium | 880 | 24 | 17 | 46 | 42340 | 34490 | 4695 | 28
53QDMT60-518 | 0.2 | Medium | 880 | 24 | 17 | 52 | 40420 | 33725 | 4865 | 28
53QDMT60-518 | 0.2 | Medium | 880 | 27 | 19 | 35 | 48100 | 36865 | 4500 | 28
53QDMT60-518 | 0.2 | Medium | 880 | 27 | 19 | 43 | 44735 | 35150 | 4700 | 28
53QDMT60-518 | 0.2 | Medium | 880 | 27 | 19 | 46 | 43300 | 34445 | 4785 | 28
53QDMT60-518 | 0.2 | Medium | 880 | 27 | 19 | 52 | 40430 | 33020 | 4955 | 28
53QDMT60-518 | 0.2 | Medium | 880 | 32 | 23 | 35 | 50030 | 42185 | 4725 | 28
53QDMT60-518 | 0.2 | Medium | 880 | 32 | 23 | 43 | 46190 | 41155 | 4890 | 28
53QDMT60-518 | 0.2 | Medium | 880 | 32 | 23 | 46 | 44750 | 40750 | 4940 | 28
53QDMT60-518 | 0.2 | Medium | 880 | 32 | 23 | 52 | 41900 | 39940 | 5040 | 28
53QDMT60-518 | 0.2 | Low | 703 | 21 | 15 | 35 | 42875 | 31675 | 4060 | 28
53QDMT60-518 | 0.2 | Low | 703 | 21 | 15 | 43 | 41030 | 31845 | 4200 | 28
53QDMT60-518 | 0.2 | Low | 703 | 21 | 15 | 46 | 40110 | 31505 | 4245 | 28
53QDMT60-518 | 0.2 | Low | 703 | 21 | 15 | 52 | 38280 | 30835 | 4335 | 28
53QDMT60-518 | 0.2 | Low | 703 | 24 | 17 | 35 | 44260 | 33120 | 4230 | 28
53QDMT60-518 | 0.2 | Low | 703 | 24 | 17 | 43 | 41495 | 32215 | 4445 | 28
53QDMT60-518 | 0.2 | Low | 703 | 24 | 17 | 46 | 40575 | 29320 | 4525 | 28
53QDMT60-518 | 0.2 | Low | 703 | 24 | 17 | 52 | 38735 | 31160 | 4685 | 28
53QDMT60-518 | 0.2 | Low | 703 | 27 | 19 | 35 | 46095 | 34060 | 4310 | 28
53QDMT60-518 | 0.2 | Low | 703 | 27 | 19 | 43 | 42870 | 32470 | 4525 | 28
53QDMT60-518 | 0.2 | Low | 703 | 27 | 19 | 46 | 41495 | 29280 | 4605 | 28
53QDMT60-518 | 0.2 | Low | 703 | 27 | 19 | 52 | 38745 | 30510 | 4765 | 28
53QDMT60-518 | 0.2 | Low | 703 | 21 | 23 | 35 | 47950 | 38975 | 4300 | 28
53QDMT60-518 | 0.2 | Low | 703 | 21 | 23 | 43 | 44265 | 38025 | 4465 | 28
53QDMT60-518 | 0.2 | Low | 703 | 21 | 23 | 46 | 42890 | 34640 | 4510 | 28
53QDMT60-518 | 0.2 | Low | 703 | 21 | 23 | 52 | 40155 | 36900 | 4600 | 28
53QDMT60-518 | 0.24 | High | 1283 | 21 | 15 | 35 | 46190 | 36945 | 4340 | 29
53QDMT60-518 | 0.24 | High | 1283 | 21 | 15 | 43 | 44210 | 37140 | 4485 | 29
53QDMT60-518 | 0.24 | High | 1283 | 21 | 15 | 46 | 43215 | 36745 | 4530 | 29
53QDMT60-518 | 0.24 | High | 1283 | 21 | 15 | 52 | 38525 | 33600 | 4620 | 29
53QDMT60-518 | 0.24 | High | 1283 | 24 | 17 | 35 | 47685 | 38625 | 4525 | 29
53QDMT60-518 | 0.24 | High | 1283 | 24 | 17 | 43 | 44715 | 37580 | 4755 | 29
53QDMT60-518 | 0.24 | High | 1283 | 24 | 17 | 46 | 43725 | 37170 | 4840 | 29
53QDMT60-518 | 0.24 | High | 1283 | 24 | 17 | 52 | 41745 | 36350 | 5010 | 29
53QDMT60-518 | 0.24 | High | 1283 | 27 | 19 | 35 | 49660 | 39720 | 4615 | 29
53QDMT60-518 | 0.24 | High | 1283 | 27 | 19 | 43 | 46185 | 37885 | 4850 | 29
53QDMT60-518 | 0.24 | High | 1283 | 27 | 19 | 46 | 44710 | 37120 | 4940 | 29
53QDMT60-518 | 0.24 | High | 1283 | 27 | 19 | 52 | 41760 | 35595 | 5125 | 29
53QDMT60-518 | 0.24 | High | 1283 | 32 | 23 | 35 | 51660 | 45455 | 4850 | 29
53QDMT60-518 | 0.24 | High | 1283 | 32 | 23 | 43 | 47675 | 44335 | 5035 | 29
53QDMT60-518 | 0.24 | High | 1283 | 32 | 23 | 46 | 46225 | 43920 | 5085 | 29
53QDMT60-518 | 0.24 | High | 1283 | 32 | 23 | 52 | 43325 | 43100 | 5185 | 29
53QDMT60-518 | 0.24 | Medium | 846 | 21 | 15 | 35 | 44345 | 33990 | 4210 | 29
53QDMT60-518 | 0.24 | Medium | 846 | 21 | 15 | 43 | 42445 | 34170 | 4350 | 29
53QDMT60-518 | 0.24 | Medium | 846 | 21 | 15 | 46 | 41490 | 33805 | 4395 | 29
53QDMT60-518 | 0.24 | Medium | 846 | 21 | 15 | 52 | 36985 | 30915 | 4480 | 29
53QDMT60-518 | 0.24 | Medium | 846 | 24 | 17 | 35 | 45780 | 35535 | 4390 | 29
53QDMT60-518 | 0.24 | Medium | 846 | 24 | 17 | 43 | 42930 | 34575 | 4615 | 29
53QDMT60-518 | 0.24 | Medium | 846 | 24 | 17 | 46 | 41980 | 34200 | 4695 | 29
53QDMT60-518 | 0.24 | Medium | 846 | 24 | 17 | 52 | 40075 | 33445 | 4860 | 29
53QDMT60-518 | 0.24 | Medium | 846 | 27 | 19 | 35 | 47675 | 36545 | 4475 | 29
53QDMT60-518 | 0.24 | Medium | 846 | 27 | 19 | 43 | 44340 | 34855 | 4705 | 29
53QDMT60-518 | 0.24 | Medium | 846 | 27 | 19 | 46 | 42925 | 34150 | 4795 | 29
53QDMT60-518 | 0.24 | Medium | 846 | 27 | 19 | 52 | 40090 | 32750 | 4970 | 29
53QDMT60-518 | 0.24 | Medium | 846 | 32 | 23 | 35 | 49595 | 41820 | 4705 | 29
53QDMT60-518 | 0.24 | Medium | 846 | 32 | 23 | 43 | 45770 | 40790 | 4885 | 29
53QDMT60-518 | 0.24 | Medium | 846 | 32 | 23 | 46 | 44380 | 40410 | 4935 | 29
53QDMT60-518 | 0.24 | Medium | 846 | 32 | 23 | 52 | 41595 | 39655 | 5030 | 29
53QDMT60-518 | 0.24 | Low | 678 | 21 | 15 | 35 | 42495 | 31405 | 4035 | 29
53QDMT60-518 | 0.24 | Low | 678 | 21 | 15 | 43 | 40675 | 31570 | 4170 | 29
53QDMT60-518 | 0.24 | Low | 678 | 21 | 15 | 46 | 39760 | 31235 | 4215 | 29
53QDMT60-518 | 0.24 | Low | 678 | 21 | 15 | 52 | 35445 | 28560 | 4300 | 29
53QDMT60-518 | 0.24 | Low | 678 | 24 | 17 | 35 | 43870 | 32835 | 4210 | 29
53QDMT60-518 | 0.24 | Low | 678 | 24 | 17 | 43 | 41140 | 31945 | 4425 | 29
53QDMT60-518 | 0.24 | Low | 678 | 24 | 17 | 46 | 40230 | 31595 | 4500 | 29
53QDMT60-518 | 0.24 | Low | 678 | 24 | 17 | 52 | 38405 | 30900 | 4660 | 29
53QDMT60-518 | 0.24 | Low | 678 | 27 | 19 | 35 | 45690 | 33765 | 4290 | 29
53QDMT60-518 | 0.24 | Low | 678 | 27 | 19 | 43 | 42490 | 32205 | 4510 | 29
53QDMT60-518 | 0.24 | Low | 678 | 27 | 19 | 46 | 41135 | 31555 | 4595 | 29
53QDMT60-518 | 0.24 | Low | 678 | 27 | 19 | 52 | 38420 | 30260 | 4765 | 29
53QDMT60-518 | 0.24 | Low | 678 | 21 | 23 | 35 | 47530 | 38640 | 4510 | 29
53QDMT60-518 | 0.24 | Low | 678 | 21 | 23 | 43 | 43865 | 37685 | 4685 | 29
53QDMT60-518 | 0.24 | Low | 678 | 21 | 23 | 46 | 42530 | 37335 | 4730 | 29
53QDMT60-518 | 0.24 | Low | 678 | 21 | 23 | 52 | 39860 | 36635 | 4825 | 29
53QDMT60-518 | 0.28 | High | 1252 | 21 | 15 | 35 | 45780 | 36620 | 4325 | 29
53QDMT60-518 | 0.28 | High | 1252 | 21 | 15 | 43 | 44820 | 37655 | 4470 | 29
53QDMT60-518 | 0.28 | High | 1252 | 21 | 15 | 46 | 43810 | 37255 | 4515 | 29
53QDMT60-518 | 0.28 | High | 1252 | 21 | 15 | 52 | 41795 | 36455 | 4605 | 29
53QDMT60-518 | 0.28 | High | 1252 | 24 | 17 | 35 | 47260 | 38280 | 4510 | 29
53QDMT60-518 | 0.28 | High | 1252 | 24 | 17 | 43 | 44315 | 37245 | 4740 | 29
53QDMT60-518 | 0.28 | High | 1252 | 24 | 17 | 46 | 43335 | 36840 | 4825 | 29
53QDMT60-518 | 0.28 | High | 1252 | 24 | 17 | 52 | 41365 | 36020 | 4995 | 29
53QDMT60-518 | 0.28 | High | 1252 | 27 | 19 | 35 | 49220 | 39370 | 4595 | 29
53QDMT60-518 | 0.28 | High | 1252 | 27 | 19 | 43 | 45775 | 37550 | 4825 | 29
53QDMT60-518 | 0.28 | High | 1252 | 27 | 19 | 46 | 44315 | 36795 | 4915 | 29
53QDMT60-518 | 0.28 | High | 1252 | 27 | 19 | 52 | 41390 | 35280 | 5095 | 29
53QDMT60-518 | 0.28 | High | 1252 | 32 | 23 | 35 | 51200 | 45050 | 4830 | 29
53QDMT60-518 | 0.28 | High | 1252 | 32 | 23 | 43 | 47250 | 43940 | 5015 | 29
53QDMT60-518 | 0.28 | High | 1252 | 32 | 23 | 46 | 45815 | 43530 | 5065 | 29
53QDMT60-518 | 0.28 | High | 1252 | 32 | 23 | 52 | 4290 | 42720 | 5165 | 29
53QDMT60-518 | 0.28 | Medium | 812 | 21 | 15 | 35 | 43950 | 33690 | 4195 | 29
53QDMT60-518 | 0.28 | Medium | 812 | 21 | 15 | 43 | 43030 | 34645 | 4335 | 29
53QDMT60-518 | 0.28 | Medium | 812 | 21 | 15 | 46 | 42060 | 34275 | 4380 | 29
53QDMT60-518 | 0.28 | Medium | 812 | 21 | 15 | 52 | 40125 | 33540 | 4470 | 29
53QDMT60-518 | 0.28 | Medium | 812 | 24 | 17 | 35 | 45375 | 35220 | 4275 | 29
53QDMT60-518 | 0.28 | Medium | 812 | 24 | 17 | 43 | 42545 | 34265 | 4600 | 29
53QDMT60-518 | 0.28 | Medium | 812 | 24 | 17 | 46 | 41605 | 33895 | 4680 | 29
53QDMT60-518 | 0.28 | Medium | 812 | 24 | 17 | 52 | 39710 | 33140 | 4845 | 29
53QDMT60-518 | 0.28 | Medium | 812 | 27 | 19 | 35 | 47255 | 36220 | 4460 | 29
53QDMT60-518 | 0.28 | Medium | 812 | 27 | 19 | 43 | 43945 | 34550 | 4680 | 29
53QDMT60-518 | 0.28 | Medium | 812 | 27 | 19 | 46 | 42545 | 3855 | 4770 | 29
53QDMT60-518 | 0.28 | Medium | 812 | 27 | 19 | 52 | 39735 | 32460 | 4945 | 29
53QDMT60-518 | 0.28 | Medium | 812 | 32 | 23 | 35 | 49155 | 41450 | 4685 | 29
53QDMT60-518 | 0.28 | Medium | 812 | 32 | 23 | 43 | 45360 | 40425 | 4865 | 29
53QDMT60-518 | 0.28 | Medium | 812 | 32 | 23 | 46 | 43985 | 40050 | 4915 | 29
53QDMT60-518 | 0.28 | Medium | 812 | 32 | 23 | 52 | 41225 | 39305 | 5010 | 29
53QDMT60-518 | 0.28 | Low | 653 | 21 | 15 | 35 | 42120 | 31130 | 4025 | 29
53QDMT60-518 | 0.28 | Low | 653 | 21 | 15 | 43 | 41235 | 32010 | 4160 | 29
53QDMT60-518 | 0.28 | Low | 653 | 21 | 15 | 46 | 40305 | 31670 | 4200 | 29
53QDMT60-518 | 0.28 | Low | 653 | 21 | 15 | 52 | 38455 | 30990 | 4285 | 29
53QDMT60-518 | 0.28 | Low | 653 | 24 | 17 | 35 | 43480 | 32450 | 4195 | 29
53QDMT60-518 | 0.28 | Low | 653 | 24 | 17 | 43 | 40770 | 31660 | 4410 | 29
53QDMT60-518 | 0.28 | Low | 653 | 24 | 17 | 46 | 39870 | 31315 | 4490 | 29
53QDMT60-518 | 0.28 | Low | 653 | 24 | 17 | 52 | 38060 | 30620 | 4645 | 29
53QDMT60-518 | 0.28 | Low | 653 | 27 | 19 | 35 | 45285 | 33465 | 4275 | 29
53QDMT60-518 | 0.28 | Low | 653 | 27 | 19 | 43 | 42115 | 31920 | 4490 | 29
53QDMT60-518 | 0.28 | Low | 653 | 27 | 19 | 46 | 40770 | 31280 | 4570 | 29
53QDMT60-518 | 0.28 | Low | 653 | 27 | 19 | 52 | 38080 | 29990 | 4740 | 29
53QDMT60-518 | 0.28 | Low | 653 | 21 | 23 | 35 | 47110 | 38295 | 4490 | 29
53QDMT60-518 | 0.28 | Low | 653 | 21 | 23 | 43 | 43470 | 37350 | 4665 | 29
53QDMT60-518 | 0.28 | Low | 653 | 21 | 23 | 46 | 42150 | 37000 | 4710 | 29
53QDMT60-518 | 0.28 | Low | 653 | 21 | 23 | 52 | 39505 | 36315 | 4805 | 29
53QDMT60-518 | 0.32 | High | 1221 | 21 | 15 | 35 | 45365 | 36285 | 4310 | 29
53QDMT60-518 | 0.32 | High | 1221 | 21 | 15 | 43 | 43420 | 36475 | 4455 | 29
53QDMT60-518 | 0.32 | High | 1221 | 21 | 15 | 46 | 42440 | 36085 | 4500 | 29
53QDMT60-518 | 0.32 | High | 1221 | 21 | 15 | 52 | 40485 | 35310 | 4590 | 29
53QDMT60-518 | 0.32 | High | 1221 | 24 | 17 | 35 | 46835 | 37935 | 4495 | 29
53QDMT60-518 | 0.32 | High | 1221 | 24 | 17 | 43 | 43915 | 36905 | 4725 | 29
53QDMT60-518 | 0.32 | High | 1221 | 24 | 17 | 46 | 42940 | 36500 | 4810 | 29
53QDMT60-518 | 0.32 | High | 1221 | 24 | 17 | 52 | 40985 | 35685 | 4980 | 29
53QDMT60-518 | 0.32 | High | 1221 | 27 | 19 | 35 | 48780 | 39015 | 4575 | 29
53QDMT60-518 | 0.32 | High | 1221 | 27 | 19 | 43 | 45365 | 37210 | 4805 | 29
53QDMT60-518 | 0.32 | High | 1221 | 27 | 19 | 46 | 43915 | 36460 | 4895 | 29
53QDMT60-518 | 0.32 | High | 1221 | 27 | 19 | 52 | 41015 | 34960 | 5075 | 29
53QDMT60-518 | 0.32 | High | 1221 | 32 | 23 | 35 | 50740 | 44645 | 4810 | 29
53QDMT60-518 | 0.32 | High | 1221 | 32 | 23 | 43 | 46825 | 43545 | 4995 | 29
53QDMT60-518 | 0.32 | High | 1221 | 32 | 23 | 46 | 45400 | 43135 | 5045 | 29
53QDMT60-518 | 0.32 | High | 1221 | 32 | 23 | 52 | 42550 | 42325 | 5145 | 29
53QDMT60-518 | 0.32 | Medium | 778 | 21 | 15 | 35 | 43550 | 33385 | 4180 | 29
53QDMT60-518 | 0.32 | Medium | 778 | 21 | 15 | 43 | 41685 | 33560 | 4320 | 29
53QDMT60-518 | 0.32 | Medium | 778 | 21 | 15 | 46 | 40745 | 33200 | 4365 | 29
53QDMT60-518 | 0.32 | Medium | 778 | 21 | 15 | 52 | 38870 | 32485 | 4455 | 29
53QDMT60-518 | 0.32 | Medium | 778 | 24 | 17 | 35 | 44965 | 34900 | 4360 | 29
53QDMT60-518 | 0.32 | Medium | 778 | 24 | 17 | 43 | 42160 | 33955 | 4585 | 29
53QDMT60-518 | 0.32 | Medium | 778 | 24 | 17 | 46 | 41225 | 33580 | 4665 | 29
53QDMT60-518 | 0.32 | Medium | 778 | 24 | 17 | 52 | 39350 | 32830 | 4830 | 29
53QDMT60-518 | 0.32 | Medium | 778 | 27 | 19 | 35 | 46830 | 35895 | 4440 | 29
53QDMT60-518 | 0.32 | Medium | 778 | 27 | 19 | 43 | 43550 | 34235 | 4660 | 29
53QDMT60-518 | 0.32 | Medium | 778 | 27 | 19 | 46 | 42160 | 33545 | 4750 | 29
53QDMT60-518 | 0.32 | Medium | 778 | 27 | 19 | 52 | 39375 | 32165 | 4925 | 29
53QDMT60-518 | 0.32 | Medium | 778 | 32 | 23 | 35 | 48710 | 41075 | 4670 | 29
53QDMT60-518 | 0.32 | Medium | 778 | 32 | 23 | 43 | 44955 | 40065 | 4845 | 29
53QDMT60-518 | 0.32 | Medium | 778 | 32 | 23 | 46 | 43585 | 36985 | 4895 | 29
53QDMT60-518 | 0.32 | Medium | 778 | 32 | 23 | 52 | 40850 | 38940 | 4990 | 29
53QDMT60-518 | 0.32 | Low | 628 | 21 | 15 | 35 | 41740 | 30845 | 4010 | 29
53QDMT60-518 | 0.32 | Low | 628 | 21 | 15 | 43 | 39950 | 31005 | 4145 | 29
53QDMT60-518 | 0.32 | Low | 628 | 21 | 15 | 46 | 39045 | 30675 | 4185 | 29
53QDMT60-518 | 0.32 | Low | 628 | 21 | 15 | 52 | 37250 | 30015 | 4270 | 29
53QDMT60-518 | 0.32 | Low | 628 | 24 | 17 | 35 | 43090 | 32245 | 4180 | 29
53QDMT60-518 | 0.32 | Low | 628 | 24 | 17 | 43 | 40405 | 31370 | 4395 | 29
53QDMT60-518 | 0.32 | Low | 628 | 24 | 17 | 46 | 39505 | 31025 | 4475 | 29
53QDMT60-518 | 0.32 | Low | 628 | 24 | 17 | 52 | 37710 | 30335 | 4630 | 29
53QDMT60-518 | 0.32 | Low | 628 | 27 | 19 | 35 | 44880 | 33165 | 4255 | 29
53QDMT60-518 | 0.32 | Low | 628 | 27 | 19 | 43 | 41740 | 31630 | 4470 | 29
53QDMT60-518 | 0.32 | Low | 628 | 27 | 19 | 46 | 40405 | 30995 | 4555 | 29
53QDMT60-518 | 0.32 | Low | 628 | 27 | 19 | 52 | 37735 | 29720 | 4720 | 29
53QDMT60-518 | 0.32 | Low | 628 | 21 | 23 | 35 | 46685 | 37950 | 4475 | 29
53QDMT60-518 | 0.32 | Low | 628 | 21 | 23 | 43 | 43080 | 37015 | 4645 | 29
53QDMT60-518 | 0.32 | Low | 628 | 21 | 23 | 46 | 41770 | 36665 | 4695 | 29
53QDMT60-518 | 0.32 | Low | 628 | 21 | 23 | 52 | 39150 | 35980 | 4785 | 29
53QDMT60-518 | 0.36 | High | 1190 | 21 | 15 | 35 | 44955 | 35960 | 4230 | 29
53QDMT60-518 | 0.36 | High | 1190 | 21 | 15 | 43 | 43030 | 36150 | 4440 | 29
53QDMT60-518 | 0.36 | High | 1190 | 21 | 15 | 46 | 42060 | 35760 | 4485 | 29
53QDMT60-518 | 0.36 | High | 1190 | 21 | 15 | 52 | 40115 | 34990 | 4575 | 29
53QDMT60-518 | 0.36 | High | 1190 | 24 | 17 | 35 | 46415 | 37595 | 4480 | 29
53QDMT60-518 | 0.36 | High | 1190 | 24 | 17 | 43 | 43525 | 36575 | 4710 | 29
53QDMT60-518 | 0.36 | High | 1190 | 24 | 17 | 46 | 42560 | 36175 | 4795 | 29
53QDMT60-518 | 0.36 | High | 1190 | 24 | 17 | 52 | 40615 | 35365 | 4965 | 29
53QDMT60-518 | 0.36 | High | 1190 | 27 | 19 | 35 | 48340 | 38665 | 4555 | 29
53QDMT60-518 | 0.36 | High | 1190 | 27 | 19 | 43 | 44960 | 36880 | 4785 | 29
53QDMT60-518 | 0.36 | High | 1190 | 27 | 19 | 46 | 43525 | 36135 | 4875 | 29
53QDMT60-518 | 0.36 | High | 1190 | 27 | 19 | 52 | 40650 | 34650 | 5055 | 29
53QDMT60-518 | 0.36 | High | 1190 | 32 | 23 | 35 | 50285 | 44245 | 4790 | 29
53QDMT60-518 | 0.36 | High | 1190 | 32 | 23 | 43 | 46405 | 43155 | 4975 | 29
53QDMT60-518 | 0.36 | High | 1190 | 32 | 23 | 46 | 44995 | 42750 | 5025 | 29
53QDMT60-518 | 0.36 | High | 1190 | 32 | 23 | 52 | 42185 | 41965 | 5125 | 29
53QDMT60-518 | 0.36 | Medium | 744 | 21 | 15 | 35 | 43160 | 33085 | 4105 | 29
53QDMT60-518 | 0.36 | Medium | 744 | 21 | 15 | 43 | 41310 | 33260 | 4308 | 29
53QDMT60-518 | 0.36 | Medium | 744 | 21 | 15 | 46 | 40380 | 32900 | 4350 | 29
53QDMT60-518 | 0.36 | Medium | 744 | 21 | 15 | 52 | 38515 | 32190 | 4440 | 29
53QDMT60-518 | 0.36 | Medium | 744 | 24 | 17 | 35 | 44560 | 34590 | 4345 | 29
53QDMT60-518 | 0.36 | Medium | 744 | 24 | 17 | 43 | 41785 | 33650 | 4570 | 29
53QDMT60-518 | 0.36 | Medium | 744 | 24 | 17 | 46 | 40860 | 33285 | 4653 | 29
53QDMT60-518 | 0.36 | Medium | 744 | 24 | 17 | 52 | 38995 | 32540 | 4815 | 29
53QDMT60-518 | 0.36 | Medium | 744 | 27 | 19 | 35 | 46410 | 35575 | 4420 | 29
53QDMT60-518 | 0.36 | Medium | 744 | 27 | 19 | 43 | 43160 | 33930 | 4643 | 29
53QDMT60-518 | 0.36 | Medium | 744 | 27 | 19 | 46 | 41785 | 33245 | 4730 | 29
53QDMT60-518 | 0.36 | Medium | 744 | 27 | 19 | 52 | 39025 | 31880 | 4905 | 29
53QDMT60-518 | 0.36 | Medium | 744 | 32 | 23 | 35 | 48275 | 22555 | 4650 | 29
53QDMT60-518 | 0.36 | Medium | 744 | 32 | 23 | 43 | 44555 | 39705 | 4825 | 29
53QDMT60-518 | 0.36 | Medium | 744 | 32 | 23 | 46 | 43200 | 37985 | 4875 | 29
53QDMT60-518 | 0.36 | Medium | 744 | 32 | 23 | 52 | 40500 | 38610 | 4973 | 29
53QDMT60-518 | 0.36 | Low | 603 | 21 | 15 | 35 | 41365 | 30570 | 3935 | 29
53QDMT60-518 | 0.36 | Low | 603 | 21 | 15 | 43 | 39590 | 30730 | 4130 | 29
53QDMT60-518 | 0.36 | Low | 603 | 21 | 15 | 46 | 38695 | 30400 | 4173 | 29
53QDMT60-518 | 0.36 | Low | 603 | 21 | 15 | 52 | 36910 | 29740 | 4255 | 29
53QDMT60-518 | 0.36 | Low | 603 | 24 | 17 | 35 | 42705 | 17705 | 4168 | 29
53QDMT60-518 | 0.36 | Low | 603 | 24 | 17 | 43 | 40045 | 31090 | 4380 | 29
53QDMT60-518 | 0.36 | Low | 603 | 24 | 17 | 46 | 39155 | 30750 | 4460 | 29
53QDMT60-518 | 0.36 | Low | 603 | 24 | 17 | 52 | 37370 | 30065 | 4618 | 29
53QDMT60-518 | 0.36 | Low | 603 | 27 | 19 | 35 | 44475 | 32870 | 4238 | 29
53QDMT60-518 | 0.36 | Low | 603 | 27 | 19 | 43 | 41365 | 31350 | 4450 | 29
53QDMT60-518 | 0.36 | Low | 603 | 27 | 19 | 46 | 40045 | 30720 | 4535 | 29
53QDMT60-518 | 0.36 | Low | 603 | 27 | 19 | 52 | 37400 | 29455 | 4703 | 29
53QDMT60-518 | 0.36 | Low | 603 | 21 | 23 | 35 | 46265 | 37610 | 4455 | 29
53QDMT60-518 | 0.36 | Low | 603 | 21 | 23 | 43 | 42695 | 36685 | 4628 | 29
53QDMT60-518 | 0.36 | Low | 603 | 21 | 23 | 46 | 41400 | 36340 | 4675 | 29
53QDMT60-518 | 0.36 | Low | 603 | 21 | 23 | 52 | 38815 | 35670 | 4768 | 29
53QDMT60-518 | 0.4 | High | 1159 | 21 | 15 | 35 | 44545 | 35630 | 4150 | 29
53QDMT60-518 | 0.4 | High | 1159 | 21 | 15 | 43 | 42635 | 35820 | 4425 | 29
53QDMT60-518 | 0.4 | High | 1159 | 21 | 15 | 46 | 41675 | 35435 | 4470 | 29
53QDMT60-518 | 0.4 | High | 1159 | 21 | 15 | 52 | 39745 | 34665 | 4560 | 29
53QDMT60-518 | 0.4 | High | 1159 | 24 | 17 | 35 | 45995 | 37255 | 4465 | 29
53QDMT60-518 | 0.4 | High | 1159 | 24 | 17 | 43 | 43130 | 36245 | 4695 | 29
53QDMT60-518 | 0.4 | High | 1159 | 24 | 17 | 46 | 42175 | 35850 | 4780 | 29
53QDMT60-518 | 0.4 | High | 1159 | 24 | 17 | 52 | 40245 | 35045 | 4950 | 29
53QDMT60-518 | 0.4 | High | 1159 | 27 | 19 | 35 | 47900 | 38315 | 4535 | 29
53QDMT60-518 | 0.4 | High | 1159 | 27 | 19 | 43 | 44550 | 36545 | 4765 | 29
53QDMT60-518 | 0.4 | High | 1159 | 27 | 19 | 46 | 43130 | 35810 | 4855 | 29
53QDMT60-518 | 0.4 | High | 1159 | 27 | 19 | 52 | 40285 | 34340 | 5035 | 29
53QDMT60-518 | 0.4 | High | 1159 | 32 | 23 | 35 | 49830 | 43845 | 4770 | 29
53QDMT60-518 | 0.4 | High | 1159 | 32 | 23 | 43 | 45985 | 42765 | 4955 | 29
53QDMT60-518 | 0.4 | High | 1159 | 32 | 23 | 46 | 44590 | 42365 | 5005 | 29
53QDMT60-518 | 0.4 | High | 1159 | 32 | 23 | 52 | 41820 | 41600 | 5105 | 29
53QDMT60-518 | 0.4 | Medium | 710 | 21 | 15 | 35 | 42765 | 32780 | 4025 | 29
53QDMT60-518 | 0.4 | Medium | 710 | 21 | 15 | 43 | 40930 | 32955 | 4295 | 29
53QDMT60-518 | 0.4 | Medium | 710 | 21 | 15 | 46 | 40010 | 32600 | 4335 | 29
53QDMT60-518 | 0.4 | Medium | 710 | 21 | 15 | 52 | 38155 | 31895 | 4425 | 29
53QDMT60-518 | 0.4 | Medium | 710 | 24 | 17 | 35 | 44155 | 34275 | 4330 | 29
53QDMT60-518 | 0.4 | Medium | 710 | 24 | 17 | 43 | 41405 | 33345 | 4555 | 29
53QDMT60-518 | 0.4 | Medium | 710 | 24 | 17 | 46 | 40490 | 32985 | 4640 | 29
53QDMT60-518 | 0.4 | Medium | 710 | 24 | 17 | 52 | 38635 | 32245 | 4800 | 29
53QDMT60-518 | 0.4 | Medium | 710 | 27 | 19 | 35 | 45985 | 35250 | 4400 | 29
53QDMT60-518 | 0.4 | Medium | 710 | 27 | 19 | 43 | 42770 | 33625 | 4625 | 29
53QDMT60-518 | 0.4 | Medium | 710 | 27 | 19 | 46 | 41405 | 32945 | 4710 | 29
53QDMT60-518 | 0.4 | Medium | 710 | 27 | 19 | 52 | 38675 | 31595 | 4885 | 29
53QDMT60-518 | 0.4 | Medium | 710 | 32 | 23 | 35 | 47840 | 4030 | 4630 | 29
53QDMT60-518 | 0.4 | Medium | 710 | 32 | 23 | 43 | 44150 | 39345 | 4805 | 29
53QDMT60-518 | 0.4 | Medium | 710 | 32 | 23 | 46 | 42810 | 38980 | 4855 | 29
53QDMT60-518 | 0.4 | Medium | 710 | 32 | 23 | 52 | 40150 | 38275 | 4955 | 29
53QDMT60-518 | 0.4 | Low | 578 | 21 | 15 | 35 | 40985 | 30290 | 3860 | 29
53QDMT60-518 | 0.4 | Low | 578 | 21 | 15 | 43 | 39225 | 30450 | 4115 | 29
53QDMT60-518 | 0.4 | Low | 578 | 21 | 15 | 46 | 38345 | 30120 | 4160 | 29
53QDMT60-518 | 0.4 | Low | 578 | 21 | 15 | 52 | 36565 | 29465 | 4240 | 29
53QDMT60-518 | 0.4 | Low | 578 | 24 | 17 | 35 | 42315 | 3160 | 4155 | 29
53QDMT60-518 | 0.4 | Low | 578 | 24 | 17 | 43 | 39680 | 30810 | 4365 | 29
53QDMT60-518 | 0.4 | Low | 578 | 24 | 17 | 46 | 38805 | 30475 | 4445 | 29
53QDMT60-518 | 0.4 | Low | 578 | 24 | 17 | 52 | 37025 | 29790 | 4605 | 29
53QDMT60-518 | 0.4 | Low | 578 | 27 | 19 | 35 | 44070 | 32570 | 4220 | 29
53QDMT60-518 | 0.4 | Low | 578 | 27 | 19 | 43 | 40990 | 31065 | 4430 | 29
53QDMT60-518 | 0.4 | Low | 578 | 27 | 19 | 46 | 39680 | 30440 | 4515 | 29
53QDMT60-518 | 0.4 | Low | 578 | 27 | 19 | 52 | 37065 | 29190 | 4685 | 29
53QDMT60-518 | 0.4 | Low | 578 | 21 | 23 | 35 | 45845 | 37270 | 4435 | 29
53QDMT60-518 | 0.4 | Low | 578 | 21 | 23 | 43 | 42310 | 36350 | 4610 | 29
53QDMT60-518 | 0.4 | Low | 578 | 21 | 23 | 46 | 41025 | 36010 | 4655 | 29
53QDMT60-518 | 0.4 | Low | 578 | 21 | 23 | 52 | 38475 | 35360 | 4750 | 29

## Heating_Performance
system_model | esp_inwg | fan_speed | airflow_cfm | indoor_db_c | outdoor_condition | total_capacity_btuh | input_w | source_page
53QDMT12-718 | 0 | High | 400 | 15 | 2/1°C | 10920 | 900 | 31
53QDMT12-718 | 0 | High | 400 | 15 | 24/18°C | 16505 | 1135 | 31
53QDMT12-718 | 0 | High | 400 | 15 | 7/6°C | 13335 | 980 | 31
53QDMT12-718 | 0 | High | 400 | 20 | 2/1°C | 10285 | 925 | 31
53QDMT12-718 | 0 | High | 400 | 20 | 24/18°C | 16000 | 1240 | 31
53QDMT12-718 | 0 | High | 400 | 20 | 7/6°C | 12700 | 1045 | 31
53QDMT12-718 | 0 | High | 400 | 27 | 2/1°C | 9650 | 995 | 31
53QDMT12-718 | 0 | High | 400 | 27 | 24/18°C | 14985 | 1320 | 31
53QDMT12-718 | 0 | High | 400 | 27 | 7/6°C | 11935 | 1135 | 31
53QDMT12-718 | 0 | Low | 250 | 15 | 2/1°C | 9940 | 825 | 31
53QDMT12-718 | 0 | Low | 250 | 15 | 24/18°C | 15025 | 1040 | 31
53QDMT12-718 | 0 | Low | 250 | 15 | 7/6°C | 12140 | 905 | 31
53QDMT12-718 | 0 | Low | 250 | 20 | 2/1°C | 9360 | 855 | 31
53QDMT12-718 | 0 | Low | 250 | 20 | 24/18°C | 14560 | 1150 | 31
53QDMT12-718 | 0 | Low | 250 | 20 | 7/6°C | 11555 | 975 | 31
53QDMT12-718 | 0 | Low | 250 | 27 | 2/1°C | 8785 | 920 | 31
53QDMT12-718 | 0 | Low | 250 | 27 | 24/18°C | 13640 | 1210 | 31
53QDMT12-718 | 0 | Low | 250 | 27 | 7/6°C | 10865 | 1040 | 31
53QDMT12-718 | 0 | Medium | 290 | 15 | 2/1°C | 10375 | 865 | 31
53QDMT12-718 | 0 | Medium | 290 | 15 | 24/18°C | 15680 | 1095 | 31
53QDMT12-718 | 0 | Medium | 290 | 15 | 7/6°C | 12665 | 935 | 31
53QDMT12-718 | 0 | Medium | 290 | 20 | 2/1°C | 9775 | 885 | 31
53QDMT12-718 | 0 | Medium | 290 | 20 | 24/18°C | 15200 | 1190 | 31
53QDMT12-718 | 0 | Medium | 290 | 20 | 7/6°C | 12065 | 1005 | 31
53QDMT12-718 | 0 | Medium | 290 | 27 | 2/1°C | 9170 | 965 | 31
53QDMT12-718 | 0 | Medium | 290 | 27 | 24/18°C | 14240 | 1260 | 31
53QDMT12-718 | 0 | Medium | 290 | 27 | 7/6°C | 11345 | 1095 | 31
53QDMT12-718 | 0.08 | High | 344 | 15 | 2/1°C | 10830 | 920 | 31
53QDMT12-718 | 0.08 | High | 344 | 15 | 24/18°C | 16370 | 1155 | 31
53QDMT12-718 | 0.08 | High | 344 | 15 | 7/6°C | 13220 | 995 | 31
53QDMT12-718 | 0.08 | High | 344 | 20 | 2/1°C | 10200 | 945 | 31
53QDMT12-718 | 0.08 | High | 344 | 20 | 24/18°C | 15865 | 1265 | 31
53QDMT12-718 | 0.08 | High | 344 | 20 | 7/6°C | 12595 | 1065 | 31
53QDMT12-718 | 0.08 | High | 344 | 27 | 2/1°C | 9570 | 1015 | 31
53QDMT12-718 | 0.08 | High | 344 | 27 | 24/18°C | 14860 | 1340 | 31
53QDMT12-718 | 0.08 | High | 344 | 27 | 7/6°C | 11840 | 1150 | 31
53QDMT12-718 | 0.08 | Low | 203 | 15 | 2/1°C | 9865 | 845 | 31
53QDMT12-718 | 0.08 | Low | 203 | 15 | 24/18°C | 14900 | 1065 | 31
53QDMT12-718 | 0.08 | Low | 203 | 15 | 7/6°C | 12035 | 920 | 31
53QDMT12-718 | 0.08 | Low | 203 | 20 | 2/1°C | 9285 | 870 | 31
53QDMT12-718 | 0.08 | Low | 203 | 20 | 24/18°C | 14445 | 1170 | 31
53QDMT12-718 | 0.08 | Low | 203 | 20 | 7/6°C | 11460 | 990 | 31
53QDMT12-718 | 0.08 | Low | 203 | 27 | 2/1°C | 8715 | 935 | 31
53QDMT12-718 | 0.08 | Low | 203 | 27 | 24/18°C | 13530 | 1230 | 31
53QDMT12-718 | 0.08 | Low | 203 | 27 | 7/6°C | 10780 | 1060 | 31
53QDMT12-718 | 0.08 | Medium | 242 | 15 | 2/1°C | 10290 | 880 | 31
53QDMT12-718 | 0.08 | Medium | 242 | 15 | 24/18°C | 15555 | 1115 | 31
53QDMT12-718 | 0.08 | Medium | 242 | 15 | 7/6°C | 12560 | 955 | 31
53QDMT12-718 | 0.08 | Medium | 242 | 20 | 2/1°C | 9695 | 905 | 31
53QDMT12-718 | 0.08 | Medium | 242 | 20 | 24/18°C | 15080 | 1210 | 31
53QDMT12-718 | 0.08 | Medium | 242 | 20 | 7/6°C | 11965 | 1025 | 31
53QDMT12-718 | 0.08 | Medium | 242 | 27 | 2/1°C | 9095 | 980 | 31
53QDMT12-718 | 0.08 | Medium | 242 | 27 | 24/18°C | 14120 | 1280 | 31
53QDMT12-718 | 0.08 | Medium | 242 | 27 | 7/6°C | 11250 | 1110 | 31
53QDMT12-718 | 0.12 | High | 312 | 15 | 2/1°C | 10790 | 925 | 31
53QDMT12-718 | 0.12 | High | 312 | 15 | 24/18°C | 16300 | 1165 | 31
53QDMT12-718 | 0.12 | High | 312 | 15 | 7/6°C | 13170 | 1005 | 31
53QDMT12-718 | 0.12 | High | 312 | 20 | 2/1°C | 10165 | 955 | 31
53QDMT12-718 | 0.12 | High | 312 | 20 | 24/18°C | 15805 | 1275 | 31
53QDMT12-718 | 0.12 | High | 312 | 20 | 7/6°C | 12545 | 1100 | 31
53QDMT12-718 | 0.12 | High | 312 | 27 | 2/1°C | 9540 | 1030 | 31
53QDMT12-718 | 0.12 | High | 312 | 27 | 24/18°C | 14805 | 1360 | 31
53QDMT12-718 | 0.12 | High | 312 | 27 | 7/6°C | 11795 | 1175 | 31
53QDMT12-718 | 0.12 | Low | 180 | 15 | 2/1°C | 9820 | 855 | 31
53QDMT12-718 | 0.12 | Low | 180 | 15 | 24/18°C | 14835 | 1075 | 31
53QDMT12-718 | 0.12 | Low | 180 | 15 | 7/6°C | 11985 | 930 | 31
53QDMT12-718 | 0.12 | Low | 180 | 20 | 2/1°C | 9255 | 880 | 31
53QDMT12-718 | 0.12 | Low | 180 | 20 | 24/18°C | 14385 | 1185 | 31
53QDMT12-718 | 0.12 | Low | 180 | 20 | 7/6°C | 11420 | 1025 | 31
53QDMT12-718 | 0.12 | Low | 180 | 27 | 2/1°C | 8685 | 950 | 31
53QDMT12-718 | 0.12 | Low | 180 | 27 | 24/18°C | 13475 | 1245 | 31
53QDMT12-718 | 0.12 | Low | 180 | 27 | 7/6°C | 10735 | 1080 | 31
53QDMT12-718 | 0.12 | Medium | 220 | 15 | 2/1°C | 10250 | 890 | 31
53QDMT12-718 | 0.12 | Medium | 220 | 15 | 24/18°C | 15490 | 1125 | 31
53QDMT12-718 | 0.12 | Medium | 220 | 15 | 7/6°C | 12515 | 965 | 31
53QDMT12-718 | 0.12 | Medium | 220 | 20 | 2/1°C | 9655 | 915 | 31
53QDMT12-718 | 0.12 | Medium | 220 | 20 | 24/18°C | 15015 | 1225 | 31
53QDMT12-718 | 0.12 | Medium | 220 | 20 | 7/6°C | 11920 | 1060 | 31
53QDMT12-718 | 0.12 | Medium | 220 | 27 | 2/1°C | 9065 | 995 | 31
53QDMT12-718 | 0.12 | Medium | 220 | 27 | 24/18°C | 14065 | 1300 | 31
53QDMT12-718 | 0.12 | Medium | 220 | 27 | 7/6°C | 11205 | 1135 | 31
53QDMT12-718 | 0.16 | High | 275 | 15 | 2/1°C | 10740 | 930 | 31
53QDMT12-718 | 0.16 | High | 275 | 15 | 24/18°C | 16230 | 1175 | 31
53QDMT12-718 | 0.16 | High | 275 | 15 | 7/6°C | 13110 | 1010 | 31
53QDMT12-718 | 0.16 | High | 275 | 20 | 2/1°C | 10115 | 960 | 31
53QDMT12-718 | 0.16 | High | 275 | 20 | 24/18°C | 15735 | 1280 | 31
53QDMT12-718 | 0.16 | High | 275 | 20 | 7/6°C | 12485 | 1080 | 31
53QDMT12-718 | 0.16 | High | 275 | 27 | 2/1°C | 9495 | 1030 | 31
53QDMT12-718 | 0.16 | High | 275 | 27 | 24/18°C | 14740 | 1365 | 31
53QDMT12-718 | 0.16 | High | 275 | 27 | 7/6°C | 11740 | 1170 | 31
53QDMT12-718 | 0.16 | Low | 156 | 15 | 2/1°C | 9780 | 860 | 31
53QDMT12-718 | 0.16 | Low | 156 | 15 | 24/18°C | 14770 | 1085 | 31
53QDMT12-718 | 0.16 | Low | 156 | 15 | 7/6°C | 11930 | 935 | 31
53QDMT12-718 | 0.16 | Low | 156 | 20 | 2/1°C | 9205 | 885 | 31
53QDMT12-718 | 0.16 | Low | 156 | 20 | 24/18°C | 14325 | 1190 | 31
53QDMT12-718 | 0.16 | Low | 156 | 20 | 7/6°C | 11365 | 1005 | 31
53QDMT12-718 | 0.16 | Low | 156 | 27 | 2/1°C | 8640 | 950 | 31
53QDMT12-718 | 0.16 | Low | 156 | 27 | 24/18°C | 13420 | 1255 | 31
53QDMT12-718 | 0.16 | Low | 156 | 27 | 7/6°C | 10690 | 1080 | 31
53QDMT12-718 | 0.16 | Medium | 193 | 15 | 2/1°C | 10205 | 895 | 31
53QDMT12-718 | 0.16 | Medium | 193 | 15 | 24/18°C | 15425 | 1135 | 31
53QDMT12-718 | 0.16 | Medium | 193 | 15 | 7/6°C | 12455 | 970 | 31
53QDMT12-718 | 0.16 | Medium | 193 | 20 | 2/1°C | 9615 | 920 | 31
53QDMT12-718 | 0.16 | Medium | 193 | 20 | 24/18°C | 14950 | 1230 | 31
53QDMT12-718 | 0.16 | Medium | 193 | 20 | 7/6°C | 11865 | 1035 | 31
53QDMT12-718 | 0.16 | Medium | 193 | 27 | 2/1°C | 9020 | 995 | 31
53QDMT12-718 | 0.16 | Medium | 193 | 27 | 24/18°C | 14005 | 1305 | 31
53QDMT12-718 | 0.16 | Medium | 193 | 27 | 7/6°C | 11155 | 1130 | 31
53QDMT18-718 | 0 | High | 530 | 15 | 2/1°C | 16340 | 1355 | 32
53QDMT18-718 | 0 | High | 530 | 15 | 24/18°C | 24700 | 1835 | 32
53QDMT18-718 | 0 | High | 530 | 15 | 7/6°C | 19950 | 1570 | 32
53QDMT18-718 | 0 | High | 530 | 20 | 2/1°C | 15390 | 1490 | 32
53QDMT18-718 | 0 | High | 530 | 20 | 24/18°C | 23900 | 1995 | 32
53QDMT18-718 | 0 | High | 530 | 20 | 7/6°C | 19000 | 1695 | 32
53QDMT18-718 | 0 | High | 530 | 27 | 2/1°C | 14440 | 1605 | 32
53QDMT18-718 | 0 | High | 530 | 27 | 24/18°C | 22420 | 2110 | 32
53QDMT18-718 | 0 | High | 530 | 27 | 7/6°C | 17860 | 1830 | 32
53QDMT18-718 | 0 | Low | 295 | 15 | 2/1°C | 14870 | 1250 | 32
53QDMT18-718 | 0 | Low | 295 | 15 | 24/18°C | 24935 | 1685 | 32
53QDMT18-718 | 0 | Low | 295 | 15 | 7/6°C | 18155 | 1445 | 32
53QDMT18-718 | 0 | Low | 295 | 20 | 2/1°C | 14005 | 1375 | 32
53QDMT18-718 | 0 | Low | 295 | 20 | 24/18°C | 21750 | 1845 | 32
53QDMT18-718 | 0 | Low | 295 | 20 | 7/6°C | 17290 | 1560 | 32
53QDMT18-718 | 0 | Low | 295 | 27 | 2/1°C | 13145 | 1465 | 32
53QDMT18-718 | 0 | Low | 295 | 27 | 24/18°C | 20405 | 1950 | 32
53QDMT18-718 | 0 | Low | 295 | 27 | 7/6°C | 16255 | 1660 | 32
53QDMT18-718 | 0 | Medium | 350 | 15 | 2/1°C | 15525 | 1305 | 32
53QDMT18-718 | 0 | Medium | 350 | 15 | 24/18°C | 23465 | 1755 | 32
53QDMT18-718 | 0 | Medium | 350 | 15 | 7/6°C | 18955 | 1510 | 32
53QDMT18-718 | 0 | Medium | 350 | 20 | 2/1°C | 14620 | 1430 | 32
53QDMT18-718 | 0 | Medium | 350 | 20 | 24/18°C | 22705 | 1915 | 32
53QDMT18-718 | 0 | Medium | 350 | 20 | 7/6°C | 18050 | 1625 | 32
53QDMT18-718 | 0 | Medium | 350 | 27 | 2/1°C | 13720 | 1545 | 32
53QDMT18-718 | 0 | Medium | 350 | 27 | 24/18°C | 21300 | 2030 | 32
53QDMT18-718 | 0 | Medium | 350 | 27 | 7/6°C | 16970 | 1750 | 32
53QDMT18-718 | 0.08 | High | 487 | 15 | 2/1°C | 16255 | 1380 | 32
53QDMT18-718 | 0.08 | High | 487 | 15 | 24/18°C | 24570 | 1865 | 32
53QDMT18-718 | 0.08 | High | 487 | 15 | 7/6°C | 19845 | 1595 | 32
53QDMT18-718 | 0.08 | High | 487 | 20 | 2/1°C | 15310 | 1515 | 32
53QDMT18-718 | 0.08 | High | 487 | 20 | 24/18°C | 23775 | 2025 | 32
53QDMT18-718 | 0.08 | High | 487 | 20 | 7/6°C | 18900 | 1720 | 32
53QDMT18-718 | 0.08 | High | 487 | 27 | 2/1°C | 14365 | 1630 | 32
53QDMT18-718 | 0.08 | High | 487 | 27 | 24/18°C | 22305 | 2145 | 32
53QDMT18-718 | 0.08 | High | 487 | 27 | 7/6°C | 17770 | 1860 | 32
53QDMT18-718 | 0.08 | Low | 256 | 15 | 2/1°C | 14795 | 1270 | 32
53QDMT18-718 | 0.08 | Low | 256 | 15 | 24/18°C | 23590 | 1715 | 32
53QDMT18-718 | 0.08 | Low | 256 | 15 | 7/6°C | 18060 | 1470 | 32
53QDMT18-718 | 0.08 | Low | 256 | 20 | 2/1°C | 13935 | 1395 | 32
53QDMT18-718 | 0.08 | Low | 256 | 20 | 24/18°C | 21640 | 1870 | 32
53QDMT18-718 | 0.08 | Low | 256 | 20 | 7/6°C | 17200 | 1585 | 32
53QDMT18-718 | 0.08 | Low | 256 | 27 | 2/1°C | 13075 | 1495 | 32
53QDMT18-718 | 0.08 | Low | 256 | 27 | 24/18°C | 20300 | 1975 | 32
53QDMT18-718 | 0.08 | Low | 256 | 27 | 7/6°C | 16170 | 1700 | 32
53QDMT18-718 | 0.08 | Medium | 308 | 15 | 2/1°C | 15445 | 1330 | 32
53QDMT18-718 | 0.08 | Medium | 308 | 15 | 24/18°C | 23345 | 1785 | 32
53QDMT18-718 | 0.08 | Medium | 308 | 15 | 7/6°C | 18855 | 1535 | 32
53QDMT18-718 | 0.08 | Medium | 308 | 20 | 2/1°C | 14545 | 1455 | 32
53QDMT18-718 | 0.08 | Medium | 308 | 20 | 24/18°C | 22590 | 1945 | 32
53QDMT18-718 | 0.08 | Medium | 308 | 20 | 7/6°C | 17955 | 1650 | 32
53QDMT18-718 | 0.08 | Medium | 308 | 27 | 2/1°C | 13650 | 1570 | 32
53QDMT18-718 | 0.08 | Medium | 308 | 27 | 24/18°C | 21190 | 2065 | 32
53QDMT18-718 | 0.08 | Medium | 308 | 27 | 7/6°C | 16885 | 1780 | 32
53QDMT18-718 | 0.12 | High | 465 | 15 | 2/1°C | 16220 | 1390 | 32
53QDMT18-718 | 0.12 | High | 465 | 15 | 24/18°C | 24505 | 1880 | 32
53QDMT18-718 | 0.12 | High | 465 | 15 | 7/6°C | 19800 | 1610 | 32
53QDMT18-718 | 0.12 | High | 465 | 20 | 2/1°C | 15270 | 1530 | 32
53QDMT18-718 | 0.12 | High | 465 | 20 | 24/18°C | 23715 | 2040 | 32
53QDMT18-718 | 0.12 | High | 465 | 20 | 7/6°C | 18850 | 1735 | 32
53QDMT18-718 | 0.12 | High | 465 | 27 | 2/1°C | 14335 | 1650 | 32
53QDMT18-718 | 0.12 | High | 465 | 27 | 24/18°C | 22250 | 2160 | 32
53QDMT18-718 | 0.12 | High | 465 | 27 | 7/6°C | 17725 | 1875 | 32
53QDMT18-718 | 0.12 | Low | 237 | 15 | 2/1°C | 14760 | 1285 | 32
53QDMT18-718 | 0.12 | Low | 237 | 15 | 24/18°C | 22915 | 1730 | 32
53QDMT18-718 | 0.12 | Low | 237 | 15 | 7/6°C | 18015 | 1480 | 32
53QDMT18-718 | 0.12 | Low | 237 | 20 | 2/1°C | 13900 | 1415 | 32
53QDMT18-718 | 0.12 | Low | 237 | 20 | 24/18°C | 2185 | 1885 | 32
53QDMT18-718 | 0.12 | Low | 237 | 20 | 7/6°C | 17155 | 1600 | 32
53QDMT18-718 | 0.12 | Low | 237 | 27 | 2/1°C | 13045 | 1505 | 32
53QDMT18-718 | 0.12 | Low | 237 | 27 | 24/18°C | 20250 | 1990 | 32
53QDMT18-718 | 0.12 | Low | 237 | 27 | 7/6°C | 16130 | 1720 | 32
53QDMT18-718 | 0.12 | Medium | 288 | 15 | 2/1°C | 15410 | 1340 | 32
53QDMT18-718 | 0.12 | Medium | 288 | 15 | 24/18°C | 23285 | 1800 | 32
53QDMT18-718 | 0.12 | Medium | 288 | 15 | 7/6°C | 18805 | 1550 | 32
53QDMT18-718 | 0.12 | Medium | 288 | 20 | 2/1°C | 14510 | 1410 | 32
53QDMT18-718 | 0.12 | Medium | 288 | 20 | 24/18°C | 22530 | 1960 | 32
53QDMT18-718 | 0.12 | Medium | 288 | 20 | 7/6°C | 17910 | 1665 | 32
53QDMT18-718 | 0.12 | Medium | 288 | 27 | 2/1°C | 13620 | 1590 | 32
53QDMT18-718 | 0.12 | Medium | 288 | 27 | 24/18°C | 21135 | 2080 | 32
53QDMT18-718 | 0.12 | Medium | 288 | 27 | 7/6°C | 16840 | 1795 | 32
53QDMT18-718 | 0.16 | High | 444 | 15 | 2/1°C | 16170 | 1400 | 32
53QDMT18-718 | 0.16 | High | 444 | 15 | 24/18°C | 24440 | 1895 | 32
53QDMT18-718 | 0.16 | High | 444 | 15 | 7/6°C | 19740 | 1620 | 32
53QDMT18-718 | 0.16 | High | 444 | 20 | 2/1°C | 15230 | 1535 | 32
53QDMT18-718 | 0.16 | High | 444 | 20 | 24/18°C | 23650 | 2055 | 32
53QDMT18-718 | 0.16 | High | 444 | 20 | 7/6°C | 18800 | 1745 | 32
53QDMT18-718 | 0.16 | High | 444 | 27 | 2/1°C | 14290 | 1655 | 32
53QDMT18-718 | 0.16 | High | 444 | 27 | 24/18°C | 22190 | 2175 | 32
53QDMT18-718 | 0.16 | High | 444 | 27 | 7/6°C | 17675 | 1885 | 32
53QDMT18-718 | 0.16 | Low | 218 | 15 | 2/1°C | 14715 | 1285 | 32
53QDMT18-718 | 0.16 | Low | 218 | 15 | 24/18°C | 22240 | 1745 | 32
53QDMT18-718 | 0.16 | Low | 218 | 15 | 7/6°C | 17965 | 1490 | 32
53QDMT18-718 | 0.16 | Low | 218 | 20 | 2/1°C | 13860 | 1415 | 32
53QDMT18-718 | 0.16 | Low | 218 | 20 | 24/18°C | 21525 | 1895 | 32
53QDMT18-718 | 0.16 | Low | 218 | 20 | 7/6°C | 17110 | 1610 | 32
53QDMT18-718 | 0.16 | Low | 218 | 27 | 2/1°C | 13005 | 1520 | 32
53QDMT18-718 | 0.16 | Low | 218 | 27 | 24/18°C | 20195 | 2000 | 32
53QDMT18-718 | 0.16 | Low | 218 | 27 | 7/6°C | 16085 | 1735 | 32
53QDMT18-718 | 0.16 | Medium | 267 | 15 | 2/1°C | 15365 | 1350 | 32
53QDMT18-718 | 0.16 | Medium | 267 | 15 | 24/18°C | 23220 | 1815 | 32
53QDMT18-718 | 0.16 | Medium | 267 | 15 | 7/6°C | 18755 | 1560 | 32
53QDMT18-718 | 0.16 | Medium | 267 | 20 | 2/1°C | 14470 | 1475 | 32
53QDMT18-718 | 0.16 | Medium | 267 | 20 | 24/18°C | 22470 | 1975 | 32
53QDMT18-718 | 0.16 | Medium | 267 | 20 | 7/6°C | 17860 | 1675 | 32
53QDMT18-718 | 0.16 | Medium | 267 | 27 | 2/1°C | 13575 | 1595 | 32
53QDMT18-718 | 0.16 | Medium | 267 | 27 | 24/18°C | 21080 | 2095 | 32
53QDMT18-718 | 0.16 | Medium | 267 | 27 | 7/6°C | 16795 | 1805 | 32
53QDMT18-718 | 0.2 | High | 423 | 15 | 2/1°C | 16130 | 1410 | 33
53QDMT18-718 | 0.2 | High | 423 | 15 | 24/18°C | 24375 | 1910 | 33
53QDMT18-718 | 0.2 | High | 423 | 15 | 7/6°C | 19690 | 1635 | 33
53QDMT18-718 | 0.2 | High | 423 | 20 | 2/1°C | 15190 | 1550 | 33
53QDMT18-718 | 0.2 | High | 423 | 20 | 24/18°C | 23585 | 2070 | 33
53QDMT18-718 | 0.2 | High | 423 | 20 | 7/6°C | 18750 | 1760 | 33
53QDMT18-718 | 0.2 | High | 423 | 27 | 2/1°C | 14255 | 1665 | 33
53QDMT18-718 | 0.2 | High | 423 | 27 | 24/18°C | 22130 | 2190 | 33
53QDMT18-718 | 0.2 | High | 423 | 27 | 7/6°C | 17630 | 1900 | 33
53QDMT18-718 | 0.2 | Low | 199 | 15 | 2/1°C | 14680 | 1300 | 33
53QDMT18-718 | 0.2 | Low | 199 | 15 | 24/18°C | 22185 | 1760 | 33
53QDMT18-718 | 0.2 | Low | 199 | 15 | 7/6°C | 17920 | 1505 | 33
53QDMT18-718 | 0.2 | Low | 199 | 20 | 2/1°C | 13825 | 1425 | 33
53QDMT18-718 | 0.2 | Low | 199 | 20 | 24/18°C | 21465 | 1905 | 33
53QDMT18-718 | 0.2 | Low | 199 | 20 | 7/6°C | 17065 | 1620 | 33
53QDMT18-718 | 0.2 | Low | 199 | 27 | 2/1°C | 12975 | 1535 | 33
53QDMT18-718 | 0.2 | Low | 199 | 27 | 24/18°C | 20140 | 2015 | 33
53QDMT18-718 | 0.2 | Low | 199 | 27 | 7/6°C | 16045 | 1750 | 33
53QDMT18-718 | 0.2 | Medium | 246 | 15 | 2/1°C | 15325 | 1355 | 33
53QDMT18-718 | 0.2 | Medium | 246 | 15 | 24/18°C | 23160 | 1835 | 33
53QDMT18-718 | 0.2 | Medium | 246 | 15 | 7/6°C | 18705 | 1570 | 33
53QDMT18-718 | 0.2 | Medium | 246 | 20 | 2/1°C | 14430 | 1490 | 33
53QDMT18-718 | 0.2 | Medium | 246 | 20 | 24/18°C | 22410 | 1990 | 33
53QDMT18-718 | 0.2 | Medium | 246 | 20 | 7/6°C | 17815 | 1690 | 33
53QDMT18-718 | 0.2 | Medium | 246 | 27 | 2/1°C | 13545 | 1600 | 33
53QDMT18-718 | 0.2 | Medium | 246 | 27 | 24/18°C | 21025 | 2105 | 33
53QDMT18-718 | 0.2 | Medium | 246 | 27 | 7/6°C | 16750 | 1825 | 33
53QDMT18-718 | 0.24 | High | 401 | 15 | 2/1°C | 16090 | 1420 | 33
53QDMT18-718 | 0.24 | High | 401 | 15 | 24/18°C | 24310 | 1925 | 33
53QDMT18-718 | 0.24 | High | 401 | 15 | 7/6°C | 19640 | 1650 | 33
53QDMT18-718 | 0.24 | High | 401 | 20 | 2/1°C | 15150 | 1565 | 33
53QDMT18-718 | 0.24 | High | 401 | 20 | 24/18°C | 23520 | 2085 | 33
53QDMT18-718 | 0.24 | High | 401 | 20 | 7/6°C | 18700 | 1775 | 33
53QDMT18-718 | 0.24 | High | 401 | 27 | 2/1°C | 14220 | 1675 | 33
53QDMT18-718 | 0.24 | High | 401 | 27 | 24/18°C | 22070 | 2205 | 33
53QDMT18-718 | 0.24 | High | 401 | 27 | 7/6°C | 17585 | 1915 | 33
53QDMT18-718 | 0.24 | Low | 180 | 15 | 2/1°C | 14645 | 1315 | 33
53QDMT18-718 | 0.24 | Low | 180 | 15 | 24/18°C | 22130 | 1775 | 33
53QDMT18-718 | 0.24 | Low | 180 | 15 | 7/6°C | 17875 | 1520 | 33
53QDMT18-718 | 0.24 | Low | 180 | 20 | 2/1°C | 13790 | 1435 | 33
53QDMT18-718 | 0.24 | Low | 180 | 20 | 24/18°C | 21405 | 1915 | 33
53QDMT18-718 | 0.24 | Low | 180 | 20 | 7/6°C | 17020 | 1630 | 33
53QDMT18-718 | 0.24 | Low | 180 | 27 | 2/1°C | 12945 | 1550 | 33
53QDMT18-718 | 0.24 | Low | 180 | 27 | 24/18°C | 20085 | 2030 | 33
53QDMT18-718 | 0.24 | Low | 180 | 27 | 7/6°C | 16005 | 1765 | 33
53QDMT18-718 | 0.24 | Medium | 226 | 15 | 2/1°C | 15285 | 1360 | 33
53QDMT18-718 | 0.24 | Medium | 226 | 15 | 24/18°C | 23100 | 1855 | 33
53QDMT18-718 | 0.24 | Medium | 226 | 15 | 7/6°C | 18655 | 1580 | 33
53QDMT18-718 | 0.24 | Medium | 226 | 20 | 2/1°C | 14390 | 1505 | 33
53QDMT18-718 | 0.24 | Medium | 226 | 20 | 24/18°C | 22350 | 2005 | 33
53QDMT18-718 | 0.24 | Medium | 226 | 20 | 7/6°C | 17770 | 1705 | 33
53QDMT18-718 | 0.24 | Medium | 226 | 27 | 2/1°C | 13515 | 1605 | 33
53QDMT18-718 | 0.24 | Medium | 226 | 27 | 24/18°C | 20970 | 2115 | 33
53QDMT18-718 | 0.24 | Medium | 226 | 27 | 7/6°C | 16705 | 1845 | 33
53QDMT24-718 | 0 | High | 755 | 15 | 2/1°C | 20225 | 1710 | 34
53QDMT24-718 | 0 | High | 755 | 15 | 24/18°C | 30665 | 2300 | 34
53QDMT24-718 | 0 | High | 755 | 15 | 7/6°C | 24675 | 1980 | 34
53QDMT24-718 | 0 | High | 755 | 20 | 2/1°C | 19050 | 1870 | 34
53QDMT24-718 | 0 | High | 755 | 20 | 24/18°C | 29625 | 2515 | 34
53QDMT24-718 | 0 | High | 755 | 20 | 7/6°C | 23500 | 2125 | 34
53QDMT24-718 | 0 | High | 755 | 27 | 2/1°C | 17875 | 2025 | 34
53QDMT24-718 | 0 | High | 755 | 27 | 24/18°C | 27740 | 2665 | 34
53QDMT24-718 | 0 | High | 755 | 27 | 7/6°C | 22080 | 2295 | 34
53QDMT24-718 | 0 | Low | 430 | 15 | 2/1°C | 18405 | 1570 | 34
53QDMT24-718 | 0 | Low | 430 | 15 | 24/18°C | 27905 | 2115 | 34
53QDMT24-718 | 0 | Low | 430 | 15 | 7/6°C | 22455 | 1825 | 34
53QDMT24-718 | 0 | Low | 430 | 20 | 2/1°C | 17335 | 1720 | 34
53QDMT24-718 | 0 | Low | 430 | 20 | 24/18°C | 26960 | 2315 | 34
53QDMT24-718 | 0 | Low | 430 | 20 | 7/6°C | 21385 | 1960 | 34
53QDMT24-718 | 0 | Low | 430 | 27 | 2/1°C | 16270 | 1865 | 34
53QDMT24-718 | 0 | Low | 430 | 27 | 24/18°C | 25245 | 2445 | 34
53QDMT24-718 | 0 | Low | 430 | 27 | 7/6°C | 20095 | 2110 | 34
53QDMT24-718 | 0 | Medium | 495 | 15 | 2/1°C | 19215 | 1640 | 34
53QDMT24-718 | 0 | Medium | 495 | 15 | 24/18°C | 29135 | 2215 | 34
53QDMT24-718 | 0 | Medium | 495 | 15 | 7/6°C | 23445 | 1900 | 34
53QDMT24-718 | 0 | Medium | 495 | 20 | 2/1°C | 18100 | 1790 | 34
53QDMT24-718 | 0 | Medium | 495 | 20 | 24/18°C | 28145 | 2410 | 34
53QDMT24-718 | 0 | Medium | 495 | 20 | 7/6°C | 22325 | 2040 | 34
53QDMT24-718 | 0 | Medium | 495 | 27 | 2/1°C | 16985 | 1945 | 34
53QDMT24-718 | 0 | Medium | 495 | 27 | 24/18°C | 26355 | 2550 | 34
53QDMT24-718 | 0 | Medium | 495 | 27 | 7/6°C | 20980 | 2210 | 34
53QDMT24-718 | 0.08 | High | 683 | 15 | 2/1°C | 19075 | 1695 | 34
53QDMT24-718 | 0.08 | High | 683 | 15 | 24/18°C | 28915 | 2280 | 34
53QDMT24-718 | 0.08 | High | 683 | 15 | 7/6°C | 23270 | 1960 | 34
53QDMT24-718 | 0.08 | High | 683 | 20 | 2/1°C | 17970 | 1855 | 34
53QDMT24-718 | 0.08 | High | 683 | 20 | 24/18°C | 27935 | 2490 | 34
53QDMT24-718 | 0.08 | High | 683 | 20 | 7/6°C | 22160 | 2105 | 34
53QDMT24-718 | 0.08 | High | 683 | 27 | 2/1°C | 16860 | 2005 | 34
53QDMT24-718 | 0.08 | High | 683 | 27 | 24/18°C | 26160 | 2635 | 34
53QDMT24-718 | 0.08 | High | 683 | 27 | 7/6°C | 20820 | 2270 | 34
53QDMT24-718 | 0.08 | Low | 335 | 15 | 2/1°C | 17360 | 1555 | 34
53QDMT24-718 | 0.08 | Low | 335 | 15 | 24/18°C | 26315 | 2095 | 34
53QDMT24-718 | 0.08 | Low | 335 | 15 | 7/6°C | 21175 | 1810 | 34
53QDMT24-718 | 0.08 | Low | 335 | 20 | 2/1°C | 16350 | 1705 | 34
53QDMT24-718 | 0.08 | Low | 335 | 20 | 24/18°C | 25420 | 2290 | 34
53QDMT24-718 | 0.08 | Low | 335 | 20 | 7/6°C | 20165 | 1940 | 34
53QDMT24-718 | 0.08 | Low | 335 | 27 | 2/1°C | 15345 | 1850 | 34
53QDMT24-718 | 0.08 | Low | 335 | 27 | 24/18°C | 23810 | 2420 | 34
53QDMT24-718 | 0.08 | Low | 335 | 27 | 7/6°C | 18950 | 2090 | 34
53QDMT24-718 | 0.08 | Medium | 419 | 15 | 2/1°C | 18120 | 1625 | 34
53QDMT24-718 | 0.08 | Medium | 419 | 15 | 24/18°C | 27475 | 2195 | 34
53QDMT24-718 | 0.08 | Medium | 419 | 15 | 7/6°C | 22110 | 1885 | 34
53QDMT24-718 | 0.08 | Medium | 419 | 20 | 2/1°C | 17070 | 1775 | 34
53QDMT24-718 | 0.08 | Medium | 419 | 20 | 24/18°C | 26540 | 2385 | 34
53QDMT24-718 | 0.08 | Medium | 419 | 20 | 7/6°C | 21050 | 2020 | 34
53QDMT24-718 | 0.08 | Medium | 419 | 27 | 2/1°C | 16020 | 1930 | 34
53QDMT24-718 | 0.08 | Medium | 419 | 27 | 24/18°C | 24855 | 2525 | 34
53QDMT24-718 | 0.08 | Medium | 419 | 27 | 7/6°C | 19785 | 2190 | 34
53QDMT24-718 | 0.12 | High | 651 | 15 | 2/1°C | 18250 | 1680 | 34
53QDMT24-718 | 0.12 | High | 651 | 15 | 24/18°C | 27665 | 2260 | 34
53QDMT24-718 | 0.12 | High | 651 | 15 | 7/6°C | 22260 | 1945 | 34
53QDMT24-718 | 0.12 | High | 651 | 20 | 2/1°C | 17190 | 1840 | 34
53QDMT24-718 | 0.12 | High | 651 | 20 | 24/18°C | 26725 | 2470 | 34
53QDMT24-718 | 0.12 | High | 651 | 20 | 7/6°C | 21200 | 2085 | 34
53QDMT24-718 | 0.12 | High | 651 | 27 | 2/1°C | 16130 | 1990 | 34
53QDMT24-718 | 0.12 | High | 651 | 27 | 24/18°C | 25030 | 2615 | 34
53QDMT24-718 | 0.12 | High | 651 | 27 | 7/6°C | 19920 | 2250 | 34
53QDMT24-718 | 0.12 | Low | 288 | 15 | 2/1°C | 16610 | 1545 | 34
53QDMT24-718 | 0.12 | Low | 288 | 15 | 24/18°C | 25180 | 2080 | 34
53QDMT24-718 | 0.12 | Low | 288 | 15 | 7/6°C | 20260 | 1795 | 34
53QDMT24-718 | 0.12 | Low | 288 | 20 | 2/1°C | 15640 | 1690 | 34
53QDMT24-718 | 0.12 | Low | 288 | 20 | 24/18°C | 24320 | 2270 | 34
53QDMT24-718 | 0.12 | Low | 288 | 20 | 7/6°C | 19295 | 1925 | 34
53QDMT24-718 | 0.12 | Low | 288 | 27 | 2/1°C | 14680 | 1835 | 34
53QDMT24-718 | 0.12 | Low | 288 | 27 | 24/18°C | 22780 | 2400 | 34
53QDMT24-718 | 0.12 | Low | 288 | 27 | 7/6°C | 18130 | 2070 | 34
53QDMT24-718 | 0.12 | Medium | 373 | 15 | 2/1°C | 17340 | 1615 | 34
53QDMT24-718 | 0.12 | Medium | 373 | 15 | 24/18°C | 26285 | 2180 | 34
53QDMT24-718 | 0.12 | Medium | 373 | 15 | 7/6°C | 21150 | 1870 | 34
53QDMT24-718 | 0.12 | Medium | 373 | 20 | 2/1°C | 16330 | 1760 | 34
53QDMT24-718 | 0.12 | Medium | 373 | 20 | 24/18°C | 25390 | 2365 | 34
53QDMT24-718 | 0.12 | Medium | 373 | 20 | 7/6°C | 20140 | 2005 | 34
53QDMT24-718 | 0.12 | Medium | 373 | 27 | 2/1°C | 15325 | 1915 | 34
53QDMT24-718 | 0.12 | Medium | 373 | 27 | 24/18°C | 23780 | 2505 | 34
53QDMT24-718 | 0.12 | Medium | 373 | 27 | 7/6°C | 18925 | 2170 | 34
53QDMT24-718 | 0.16 | High | 614 | 15 | 2/1°C | 17920 | 1675 | 34
53QDMT24-718 | 0.16 | High | 614 | 15 | 24/18°C | 27165 | 2255 | 34
53QDMT24-718 | 0.16 | High | 614 | 15 | 7/6°C | 21860 | 1940 | 34
53QDMT24-718 | 0.16 | High | 614 | 20 | 2/1°C | 16880 | 1835 | 34
53QDMT24-718 | 0.16 | High | 614 | 20 | 24/18°C | 26240 | 2460 | 34
53QDMT24-718 | 0.16 | High | 614 | 20 | 7/6°C | 20815 | 2080 | 34
53QDMT24-718 | 0.16 | High | 614 | 27 | 2/1°C | 15840 | 1985 | 34
53QDMT24-718 | 0.16 | High | 614 | 27 | 24/18°C | 24580 | 2605 | 34
53QDMT24-718 | 0.16 | High | 614 | 27 | 7/6°C | 19560 | 2245 | 34
53QDMT24-718 | 0.16 | Low | 236 | 15 | 2/1°C | 16310 | 1540 | 34
53QDMT24-718 | 0.16 | Low | 236 | 15 | 24/18°C | 24725 | 2075 | 34
53QDMT24-718 | 0.16 | Low | 236 | 15 | 7/6°C | 19895 | 1790 | 34
53QDMT24-718 | 0.16 | Low | 236 | 20 | 2/1°C | 15360 | 1685 | 34
53QDMT24-718 | 0.16 | Low | 236 | 20 | 24/18°C | 23880 | 2265 | 34
53QDMT24-718 | 0.16 | Low | 236 | 20 | 7/6°C | 18945 | 1920 | 34
53QDMT24-718 | 0.16 | Low | 236 | 27 | 2/1°C | 14415 | 1830 | 34
53QDMT24-718 | 0.16 | Low | 236 | 27 | 24/18°C | 22370 | 2390 | 34
53QDMT24-718 | 0.16 | Low | 236 | 27 | 7/6°C | 17805 | 2065 | 34
53QDMT24-718 | 0.16 | Medium | 330 | 15 | 2/1°C | 17025 | 1610 | 34
53QDMT24-718 | 0.16 | Medium | 330 | 15 | 24/18°C | 25810 | 2175 | 34
53QDMT24-718 | 0.16 | Medium | 330 | 15 | 7/6°C | 20770 | 1865 | 34
53QDMT24-718 | 0.16 | Medium | 330 | 20 | 2/1°C | 16035 | 1755 | 34
53QDMT24-718 | 0.16 | Medium | 330 | 20 | 24/18°C | 24930 | 2360 | 34
53QDMT24-718 | 0.16 | Medium | 330 | 20 | 7/6°C | 19775 | 2000 | 34
53QDMT24-718 | 0.16 | Medium | 330 | 27 | 2/1°C | 15050 | 1910 | 34
53QDMT24-718 | 0.16 | Medium | 330 | 27 | 24/18°C | 23350 | 2495 | 34
53QDMT24-718 | 0.16 | Medium | 330 | 27 | 7/6°C | 18585 | 2165 | 34
53QDMT24-718 | 0.2 | High | 580 | 15 | 2/1°C | 17590 | 1670 | 35
53QDMT24-718 | 0.2 | High | 580 | 15 | 24/18°C | 26665 | 2245 | 35
53QDMT24-718 | 0.2 | High | 580 | 15 | 7/6°C | 21455 | 1930 | 35
53QDMT24-718 | 0.2 | High | 580 | 20 | 2/1°C | 16565 | 1825 | 35
53QDMT24-718 | 0.2 | High | 580 | 20 | 24/18°C | 25755 | 2450 | 35
53QDMT24-718 | 0.2 | High | 580 | 20 | 7/6°C | 20430 | 2070 | 35
53QDMT24-718 | 0.2 | High | 580 | 27 | 2/1°C | 15545 | 1975 | 35
53QDMT24-718 | 0.2 | High | 580 | 27 | 24/18°C | 24125 | 2595 | 35
53QDMT24-718 | 0.2 | High | 580 | 27 | 7/6°C | 19200 | 2235 | 35
53QDMT24-718 | 0.2 | Low | 188 | 15 | 2/1°C | 16010 | 1535 | 35
53QDMT24-718 | 0.2 | Low | 188 | 15 | 24/18°C | 24270 | 2065 | 35
53QDMT24-718 | 0.2 | Low | 188 | 15 | 7/6°C | 19525 | 1780 | 35
53QDMT24-718 | 0.2 | Low | 188 | 20 | 2/1°C | 15075 | 1680 | 35
53QDMT24-718 | 0.2 | Low | 188 | 20 | 24/18°C | 23440 | 2255 | 35
53QDMT24-718 | 0.2 | Low | 188 | 20 | 7/6°C | 18595 | 1910 | 35
53QDMT24-718 | 0.2 | Low | 188 | 27 | 2/1°C | 14150 | 1820 | 35
53QDMT24-718 | 0.2 | Low | 188 | 27 | 24/18°C | 21955 | 2380 | 35
53QDMT24-718 | 0.2 | Low | 188 | 27 | 7/6°C | 17475 | 2055 | 35
53QDMT24-718 | 0.2 | Medium | 290 | 15 | 2/1°C | 16710 | 1605 | 35
53QDMT24-718 | 0.2 | Medium | 290 | 15 | 24/18°C | 25335 | 2165 | 35
53QDMT24-718 | 0.2 | Medium | 290 | 15 | 7/6°C | 20385 | 1855 | 35
53QDMT24-718 | 0.2 | Medium | 290 | 20 | 2/1°C | 15740 | 1750 | 35
53QDMT24-718 | 0.2 | Medium | 290 | 20 | 24/18°C | 24470 | 2350 | 35
53QDMT24-718 | 0.2 | Medium | 290 | 20 | 7/6°C | 19410 | 1990 | 35
53QDMT24-718 | 0.2 | Medium | 290 | 27 | 2/1°C | 14770 | 1900 | 35
53QDMT24-718 | 0.2 | Medium | 290 | 27 | 24/18°C | 22920 | 2485 | 35
53QDMT24-718 | 0.2 | Medium | 290 | 27 | 7/6°C | 18240 | 2155 | 35
53QDMT24-718 | 0.24 | High | 545 | 15 | 2/1°C | 17260 | 1665 | 35
53QDMT24-718 | 0.24 | High | 545 | 15 | 24/18°C | 26165 | 2235 | 35
53QDMT24-718 | 0.24 | High | 545 | 15 | 7/6°C | 21050 | 1920 | 35
53QDMT24-718 | 0.24 | High | 545 | 20 | 2/1°C | 16250 | 1815 | 35
53QDMT24-718 | 0.24 | High | 545 | 20 | 24/18°C | 25270 | 2440 | 35
53QDMT24-718 | 0.24 | High | 545 | 20 | 7/6°C | 20045 | 2060 | 35
53QDMT24-718 | 0.24 | High | 545 | 27 | 2/1°C | 15250 | 1965 | 35
53QDMT24-718 | 0.24 | High | 545 | 27 | 24/18°C | 23670 | 2585 | 35
53QDMT24-718 | 0.24 | High | 545 | 27 | 7/6°C | 18840 | 2225 | 35
53QDMT24-718 | 0.24 | Low | 141 | 15 | 2/1°C | 15710 | 1530 | 35
53QDMT24-718 | 0.24 | Low | 141 | 15 | 24/18°C | 23815 | 2055 | 35
53QDMT24-718 | 0.24 | Low | 141 | 15 | 7/6°C | 19155 | 1770 | 35
53QDMT24-718 | 0.24 | Low | 141 | 20 | 2/1°C | 14790 | 1675 | 35
53QDMT24-718 | 0.24 | Low | 141 | 20 | 24/18°C | 23000 | 2245 | 35
53QDMT24-718 | 0.24 | Low | 141 | 20 | 7/6°C | 18245 | 1900 | 35
53QDMT24-718 | 0.24 | Low | 141 | 27 | 2/1°C | 13885 | 1810 | 35
53QDMT24-718 | 0.24 | Low | 141 | 27 | 24/18°C | 21540 | 2370 | 35
53QDMT24-718 | 0.24 | Low | 141 | 27 | 7/6°C | 17145 | 2045 | 35
53QDMT24-718 | 0.24 | Medium | 249 | 15 | 2/1°C | 16395 | 1600 | 35
53QDMT24-718 | 0.24 | Medium | 249 | 15 | 24/18°C | 24860 | 2155 | 35
53QDMT24-718 | 0.24 | Medium | 249 | 15 | 7/6°C | 20000 | 1845 | 35
53QDMT24-718 | 0.24 | Medium | 249 | 20 | 2/1°C | 15445 | 1745 | 35
53QDMT24-718 | 0.24 | Medium | 249 | 20 | 24/18°C | 24010 | 2340 | 35
53QDMT24-718 | 0.24 | Medium | 249 | 20 | 7/6°C | 19045 | 1980 | 35
53QDMT24-718 | 0.24 | Medium | 249 | 27 | 2/1°C | 14490 | 1890 | 35
53QDMT24-718 | 0.24 | Medium | 249 | 27 | 24/18°C | 22490 | 2475 | 35
53QDMT24-718 | 0.24 | Medium | 249 | 27 | 7/6°C | 17895 | 2145 | 35
53QDMT30-718 | 0 | High | 910 | 15 | 2/1°C | 26650 | 2225 | 36
53QDMT30-718 | 0 | High | 910 | 15 | 24/18°C | 40300 | 2995 | 36
53QDMT30-718 | 0 | High | 910 | 15 | 7/6°C | 32550 | 2575 | 36
53QDMT30-718 | 0 | High | 910 | 20 | 2/1°C | 25100 | 2430 | 36
53QDMT30-718 | 0 | High | 910 | 20 | 24/18°C | 39050 | 3255 | 36
53QDMT30-718 | 0 | High | 910 | 20 | 7/6°C | 31000 | 2755 | 36
53QDMT30-718 | 0 | High | 910 | 27 | 2/1°C | 23550 | 2635 | 36
53QDMT30-718 | 0 | High | 910 | 27 | 24/18°C | 36580 | 3460 | 36
53QDMT30-718 | 0 | High | 910 | 27 | 7/6°C | 29155 | 2985 | 36
53QDMT30-718 | 0 | Low | 645 | 15 | 2/1°C | 24255 | 2050 | 36
53QDMT30-718 | 0 | Low | 645 | 15 | 24/18°C | 36675 | 2755 | 36
53QDMT30-718 | 0 | Low | 645 | 15 | 7/6°C | 29620 | 2370 | 36
53QDMT30-718 | 0 | Low | 645 | 20 | 2/1°C | 22845 | 2235 | 36
53QDMT30-718 | 0 | Low | 645 | 20 | 24/18°C | 35535 | 2995 | 36
53QDMT30-718 | 0 | Low | 645 | 20 | 7/6°C | 28210 | 2535 | 36
53QDMT30-718 | 0 | Low | 645 | 27 | 2/1°C | 21430 | 2425 | 36
53QDMT30-718 | 0 | Low | 645 | 27 | 24/18°C | 33290 | 3185 | 36
53QDMT30-718 | 0 | Low | 645 | 27 | 7/6°C | 26535 | 2745 | 36
53QDMT30-718 | 0 | Medium | 730 | 15 | 2/1°C | 25320 | 2135 | 36
53QDMT30-718 | 0 | Medium | 730 | 15 | 24/18°C | 38285 | 2875 | 36
53QDMT30-718 | 0 | Medium | 730 | 15 | 7/6°C | 30925 | 2475 | 36
53QDMT30-718 | 0 | Medium | 730 | 20 | 2/1°C | 23845 | 2335 | 36
53QDMT30-718 | 0 | Medium | 730 | 20 | 24/18°C | 37100 | 3125 | 36
53QDMT30-718 | 0 | Medium | 730 | 20 | 7/6°C | 29450 | 2645 | 36
53QDMT30-718 | 0 | Medium | 730 | 27 | 2/1°C | 22375 | 2530 | 36
53QDMT30-718 | 0 | Medium | 730 | 27 | 24/18°C | 34755 | 3325 | 36
53QDMT30-718 | 0 | Medium | 730 | 27 | 7/6°C | 27700 | 2865 | 36
53QDMT30-718 | 0.08 | High | 850 | 15 | 2/1°C | 26430 | 2205 | 36
53QDMT30-718 | 0.08 | High | 850 | 15 | 24/18°C | 39965 | 2970 | 36
53QDMT30-718 | 0.08 | High | 850 | 15 | 7/6°C | 32280 | 2555 | 36
53QDMT30-718 | 0.08 | High | 850 | 20 | 2/1°C | 24895 | 2410 | 36
53QDMT30-718 | 0.08 | High | 850 | 20 | 24/18°C | 38725 | 3225 | 36
53QDMT30-718 | 0.08 | High | 850 | 20 | 7/6°C | 30745 | 2730 | 36
53QDMT30-718 | 0.08 | High | 850 | 27 | 2/1°C | 23355 | 2615 | 36
53QDMT30-718 | 0.08 | High | 850 | 27 | 24/18°C | 36275 | 3430 | 36
53QDMT30-718 | 0.08 | High | 850 | 27 | 7/6°C | 28915 | 2960 | 36
53QDMT30-718 | 0.08 | Low | 562 | 15 | 2/1°C | 24055 | 2030 | 36
53QDMT30-718 | 0.08 | Low | 562 | 15 | 24/18°C | 36370 | 2730 | 36
53QDMT30-718 | 0.08 | Low | 562 | 15 | 7/6°C | 29375 | 2350 | 36
53QDMT30-718 | 0.08 | Low | 562 | 20 | 2/1°C | 22655 | 2220 | 36
53QDMT30-718 | 0.08 | Low | 562 | 20 | 24/18°C | 35240 | 3000 | 36
53QDMT30-718 | 0.08 | Low | 562 | 20 | 7/6°C | 27975 | 2515 | 36
53QDMT30-718 | 0.08 | Low | 562 | 27 | 2/1°C | 21255 | 2405 | 36
53QDMT30-718 | 0.08 | Low | 562 | 27 | 24/18°C | 33095 | 3235 | 36
53QDMT30-718 | 0.08 | Low | 562 | 27 | 7/6°C | 26295 | 2725 | 36
53QDMT30-718 | 0.08 | Medium | 657 | 15 | 2/1°C | 25110 | 2120 | 36
53QDMT30-718 | 0.08 | Medium | 657 | 15 | 24/18°C | 37968 | 2850 | 36
53QDMT30-718 | 0.08 | Medium | 657 | 15 | 7/6°C | 30670 | 2455 | 36
53QDMT30-718 | 0.08 | Medium | 657 | 20 | 2/1°C | 23650 | 2315 | 36
53QDMT30-718 | 0.08 | Medium | 657 | 20 | 24/18°C | 36795 | 3100 | 36
53QDMT30-718 | 0.08 | Medium | 657 | 20 | 7/6°C | 29205 | 2625 | 36
53QDMT30-718 | 0.08 | Medium | 657 | 27 | 2/1°C | 22190 | 2510 | 36
53QDMT30-718 | 0.08 | Medium | 657 | 27 | 24/18°C | 34465 | 3375 | 36
53QDMT30-718 | 0.08 | Medium | 657 | 27 | 7/6°C | 27470 | 2840 | 36
53QDMT30-718 | 0.12 | High | 820 | 15 | 2/1°C | 26325 | 2195 | 36
53QDMT30-718 | 0.12 | High | 820 | 15 | 24/18°C | 39800 | 2955 | 36
53QDMT30-718 | 0.12 | High | 820 | 15 | 7/6°C | 32150 | 2540 | 36
53QDMT30-718 | 0.12 | High | 820 | 20 | 2/1°C | 24790 | 2400 | 36
53QDMT30-718 | 0.12 | High | 820 | 20 | 24/18°C | 38565 | 3210 | 36
53QDMT30-718 | 0.12 | High | 820 | 20 | 7/6°C | 30615 | 2720 | 36
53QDMT30-718 | 0.12 | High | 820 | 27 | 2/1°C | 23260 | 2600 | 36
53QDMT30-718 | 0.12 | High | 820 | 27 | 24/18°C | 36125 | 3415 | 36
53QDMT30-718 | 0.12 | High | 820 | 27 | 7/6°C | 28795 | 2954 | 36
53QDMT30-718 | 0.12 | Low | 525 | 15 | 2/1°C | 23960 | 2020 | 36
53QDMT30-718 | 0.12 | Low | 525 | 15 | 24/18°C | 36220 | 2720 | 36
53QDMT30-718 | 0.12 | Low | 525 | 15 | 7/6°C | 29260 | 2340 | 36
53QDMT30-718 | 0.12 | Low | 525 | 20 | 2/1°C | 22560 | 2210 | 36
53QDMT30-718 | 0.12 | Low | 525 | 20 | 24/18°C | 35095 | 2955 | 36
53QDMT30-718 | 0.12 | Low | 525 | 20 | 7/6°C | 27860 | 2505 | 36
53QDMT30-718 | 0.12 | Low | 525 | 27 | 2/1°C | 21170 | 2395 | 36
53QDMT30-718 | 0.12 | Low | 525 | 27 | 24/18°C | 32875 | 3145 | 36
53QDMT30-718 | 0.12 | Low | 525 | 27 | 7/6°C | 26205 | 2710 | 36
53QDMT30-718 | 0.12 | Medium | 624 | 15 | 2/1°C | 25010 | 2110 | 36
53QDMT30-718 | 0.12 | Medium | 624 | 15 | 24/18°C | 37810 | 2840 | 36
53QDMT30-718 | 0.12 | Medium | 624 | 15 | 7/6°C | 30545 | 2440 | 36
53QDMT30-718 | 0.12 | Medium | 624 | 20 | 2/1°C | 23550 | 2305 | 36
53QDMT30-718 | 0.12 | Medium | 624 | 20 | 24/18°C | 36640 | 3085 | 36
53QDMT30-718 | 0.12 | Medium | 624 | 20 | 7/6°C | 29085 | 2610 | 36
53QDMT30-718 | 0.12 | Medium | 624 | 27 | 2/1°C | 22100 | 2495 | 36
53QDMT30-718 | 0.12 | Medium | 624 | 27 | 24/18°C | 34320 | 3280 | 36
53QDMT30-718 | 0.12 | Medium | 624 | 27 | 7/6°C | 27355 | 2830 | 36
53QDMT30-718 | 0.16 | High | 790 | 15 | 2/1°C | 26210 | 2185 | 36
53QDMT30-718 | 0.16 | High | 790 | 15 | 24/18°C | 39630 | 2940 | 36
53QDMT30-718 | 0.16 | High | 790 | 15 | 7/6°C | 32010 | 2530 | 36
53QDMT30-718 | 0.16 | High | 790 | 20 | 2/1°C | 24685 | 2390 | 36
53QDMT30-718 | 0.16 | High | 790 | 20 | 24/18°C | 38400 | 3195 | 36
53QDMT30-718 | 0.16 | High | 790 | 20 | 7/6°C | 30485 | 2705 | 36
53QDMT30-718 | 0.16 | High | 790 | 27 | 2/1°C | 23160 | 2590 | 36
53QDMT30-718 | 0.16 | High | 790 | 27 | 24/18°C | 35970 | 3400 | 36
53QDMT30-718 | 0.16 | High | 790 | 27 | 7/6°C | 28670 | 2935 | 36
53QDMT30-718 | 0.16 | Low | 495 | 15 | 2/1°C | 23855 | 2010 | 36
53QDMT30-718 | 0.16 | Low | 495 | 15 | 24/18°C | 36065 | 2705 | 36
53QDMT30-718 | 0.16 | Low | 495 | 15 | 7/6°C | 29130 | 2330 | 36
53QDMT30-718 | 0.16 | Low | 495 | 20 | 2/1°C | 22465 | 2200 | 36
53QDMT30-718 | 0.16 | Low | 495 | 20 | 24/18°C | 34945 | 2940 | 36
53QDMT30-718 | 0.16 | Low | 495 | 20 | 7/6°C | 27740 | 2490 | 36
53QDMT30-718 | 0.16 | Low | 495 | 27 | 2/1°C | 21080 | 2385 | 36
53QDMT30-718 | 0.16 | Low | 495 | 27 | 24/18°C | 32900 | 3285 | 36
53QDMT30-718 | 0.16 | Low | 495 | 27 | 7/6°C | 26050 | 2700 | 36
53QDMT30-718 | 0.16 | Medium | 591 | 15 | 2/1°C | 24900 | 2100 | 36
53QDMT30-718 | 0.16 | Medium | 591 | 15 | 24/18°C | 37650 | 2825 | 36
53QDMT30-718 | 0.16 | Medium | 591 | 15 | 7/6°C | 30415 | 2430 | 36
53QDMT30-718 | 0.16 | Medium | 591 | 20 | 2/1°C | 23450 | 2295 | 36
53QDMT30-718 | 0.16 | Medium | 591 | 20 | 24/18°C | 36485 | 3070 | 36
53QDMT30-718 | 0.16 | Medium | 591 | 20 | 7/6°C | 28960 | 2600 | 36
53QDMT30-718 | 0.16 | Medium | 591 | 27 | 2/1°C | 22005 | 2485 | 36
53QDMT30-718 | 0.16 | Medium | 591 | 27 | 24/18°C | 34175 | 3425 | 36
53QDMT30-718 | 0.16 | Medium | 591 | 27 | 7/6°C | 27240 | 2815 | 36
53QDMT30-718 | 0.2 | High | 760 | 15 | 2/1°C | 26095 | 2175
53QDMT30-718 | 0.2 | High | 760 | 15 | 24/18°C | 39460 | 2925
53QDMT30-718 | 0.2 | High | 760 | 15 | 7/6°C | 31870 | 2515
53QDMT30-718 | 0.2 | High | 760 | 20 | 2/1°C | 24575 | 2375
53QDMT30-718 | 0.2 | High | 760 | 20 | 24/18°C | 38235 | 3180
53QDMT30-718 | 0.2 | High | 760 | 20 | 7/6°C | 30350 | 2690
53QDMT30-718 | 0.2 | High | 760 | 27 | 2/1°C | 23060 | 2575
53QDMT30-718 | 0.2 | High | 760 | 27 | 24/18°C | 35815 | 3380
53QDMT30-718 | 0.2 | High | 760 | 27 | 7/6°C | 28545 | 2915
53QDMT30-718 | 0.2 | Low | 453 | 15 | 2/1°C | 23750 | 2000
53QDMT30-718 | 0.2 | Low | 453 | 15 | 24/18°C | 35910 | 2690
53QDMT30-718 | 0.2 | Low | 453 | 15 | 7/6°C | 29000 | 2315
53QDMT30-718 | 0.2 | Low | 453 | 20 | 2/1°C | 22365 | 2185
53QDMT30-718 | 0.2 | Low | 453 | 20 | 24/18°C | 34795 | 2925
53QDMT30-718 | 0.2 | Low | 453 | 20 | 7/6°C | 27620 | 2475
53QDMT30-718 | 0.2 | Low | 453 | 27 | 2/1°C | 20985 | 2370
53QDMT30-718 | 0.2 | Low | 453 | 27 | 24/18°C | 32920 | 3425
53QDMT30-718 | 0.2 | Low | 453 | 27 | 7/6°C | 25890 | 2685
53QDMT30-718 | 0.2 | Medium | 550 | 15 | 2/1°C | 24790 | 2090
53QDMT30-718 | 0.2 | Medium | 550 | 15 | 24/18°C | 37490 | 2810
53QDMT30-718 | 0.2 | Medium | 550 | 15 | 7/6°C | 30280 | 2415
53QDMT30-718 | 0.2 | Medium | 550 | 20 | 2/1°C | 23350 | 2280
53QDMT30-718 | 0.2 | Medium | 550 | 20 | 24/18°C | 36325 | 3055
53QDMT30-718 | 0.2 | Medium | 550 | 20 | 7/6°C | 28835 | 2585
53QDMT30-718 | 0.2 | Medium | 550 | 27 | 2/1°C | 21910 | 2475
53QDMT30-718 | 0.2 | Medium | 550 | 27 | 24/18°C | 34025 | 3570
53QDMT30-718 | 0.2 | Medium | 550 | 27 | 7/6°C | 27120 | 2800
53QDMT30-718 | 0.24 | High | 730 | 15 | 2/1°C | 25983 | 2165 | 37
53QDMT30-718 | 0.24 | High | 730 | 15 | 24/18°C | 35690 | 2910 | 37
53QDMT30-718 | 0.24 | High | 730 | 15 | 7/6°C | 31733 | 2503 | 37
53QDMT30-718 | 0.24 | High | 730 | 20 | 2/1°C | 24470 | 2365 | 37
53QDMT30-718 | 0.24 | High | 730 | 20 | 24/18°C | 38070 | 3165 | 37
53QDMT30-718 | 0.24 | High | 730 | 20 | 7/6°C | 30220 | 2678 | 37
53QDMT30-718 | 0.24 | High | 730 | 27 | 2/1°C | 22963 | 2563 | 37
53QDMT30-718 | 0.24 | High | 730 | 27 | 24/18°C | 35660 | 3363 | 37
53QDMT30-718 | 0.24 | High | 730 | 27 | 7/6°C | 28423 | 2900 | 37
53QDMT30-718 | 0.24 | Low | 411 | 15 | 2/1°C | 23648 | 1993 | 37
53QDMT30-718 | 0.24 | Low | 411 | 15 | 24/18°C | 35755 | 2678 | 37
53QDMT30-718 | 0.24 | Low | 411 | 15 | 7/6°C | 28878 | 2303 | 37
53QDMT30-718 | 0.24 | Low | 411 | 20 | 2/1°C | 22270 | 2178 | 37
53QDMT30-718 | 0.24 | Low | 411 | 20 | 24/18°C | 34645 | 2913 | 37
53QDMT30-718 | 0.24 | Low | 411 | 20 | 7/6°C | 27503 | 2465 | 37
53QDMT30-718 | 0.24 | Low | 411 | 27 | 2/1°C | 20898 | 2358 | 37
53QDMT30-718 | 0.24 | Low | 411 | 27 | 24/18°C | 32615 | 3253 | 37
53QDMT30-718 | 0.24 | Low | 411 | 27 | 7/6°C | 25823 | 2670 | 37
53QDMT30-718 | 0.24 | Medium | 509 | 15 | 2/1°C | 24685 | 2080 | 37
53QDMT30-718 | 0.24 | Medium | 509 | 15 | 24/18°C | 37328 | 2795 | 37
53QDMT30-718 | 0.24 | Medium | 509 | 15 | 7/6°C | 30148 | 2403 | 37
53QDMT30-718 | 0.24 | Medium | 509 | 20 | 2/1°C | 23250 | 2270 | 37
53QDMT30-718 | 0.24 | Medium | 509 | 20 | 24/18°C | 36168 | 3040 | 37
53QDMT30-718 | 0.24 | Medium | 509 | 20 | 7/6°C | 28710 | 2573 | 37
53QDMT30-718 | 0.24 | Medium | 509 | 27 | 2/1°C | 21818 | 2463 | 37
53QDMT30-718 | 0.24 | Medium | 509 | 27 | 24/18°C | 33878 | 3390 | 37
53QDMT30-718 | 0.24 | Medium | 509 | 27 | 7/6°C | 27003 | 2785 | 37
53QDMT30-718 | 0.28 | High | 700 | 15 | 2/1°C | 25870 | 2155 | 37
53QDMT30-718 | 0.28 | High | 700 | 15 | 24/18°C | 31920 | 2895 | 37
53QDMT30-718 | 0.28 | High | 700 | 15 | 7/6°C | 31595 | 2490 | 37
53QDMT30-718 | 0.28 | High | 700 | 20 | 2/1°C | 24365 | 2355 | 37
53QDMT30-718 | 0.28 | High | 700 | 20 | 24/18°C | 37905 | 3150 | 37
53QDMT30-718 | 0.28 | High | 700 | 20 | 7/6°C | 30090 | 2665 | 37
53QDMT30-718 | 0.28 | High | 700 | 27 | 2/1°C | 22865 | 2550 | 37
53QDMT30-718 | 0.28 | High | 700 | 27 | 24/18°C | 35505 | 3345 | 37
53QDMT30-718 | 0.28 | High | 700 | 27 | 7/6°C | 28300 | 2885 | 37
53QDMT30-718 | 0.28 | Low | 369 | 15 | 2/1°C | 23545 | 1985 | 37
53QDMT30-718 | 0.28 | Low | 369 | 15 | 24/18°C | 35600 | 2665 | 37
53QDMT30-718 | 0.28 | Low | 369 | 15 | 7/6°C | 28755 | 2290 | 37
53QDMT30-718 | 0.28 | Low | 369 | 20 | 2/1°C | 22175 | 2170 | 37
53QDMT30-718 | 0.28 | Low | 369 | 20 | 24/18°C | 34495 | 2900 | 37
53QDMT30-718 | 0.28 | Low | 369 | 20 | 7/6°C | 27385 | 2455 | 37
53QDMT30-718 | 0.28 | Low | 369 | 27 | 2/1°C | 20810 | 2345 | 37
53QDMT30-718 | 0.28 | Low | 369 | 27 | 24/18°C | 32310 | 3080 | 37
53QDMT30-718 | 0.28 | Low | 369 | 27 | 7/6°C | 25755 | 2655 | 37
53QDMT30-718 | 0.28 | Medium | 468 | 15 | 2/1°C | 24580 | 2070 | 37
53QDMT30-718 | 0.28 | Medium | 468 | 15 | 24/18°C | 37165 | 2780 | 37
53QDMT30-718 | 0.28 | Medium | 468 | 15 | 7/6°C | 30015 | 2390 | 37
53QDMT30-718 | 0.28 | Medium | 468 | 20 | 2/1°C | 23150 | 2260 | 37
53QDMT30-718 | 0.28 | Medium | 468 | 20 | 24/18°C | 36010 | 3025 | 37
53QDMT30-718 | 0.28 | Medium | 468 | 20 | 7/6°C | 28585 | 2560 | 37
53QDMT30-718 | 0.28 | Medium | 468 | 27 | 2/1°C | 21725 | 2450 | 37
53QDMT30-718 | 0.28 | Medium | 468 | 27 | 24/18°C | 33730 | 3210 | 37
53QDMT30-718 | 0.28 | Medium | 468 | 27 | 7/6°C | 26885 | 2770 | 37
53QDMT30-718 | 0.32 | High | 670 | 15 | 2/1°C | 25760 | 2150 | 37
53QDMT30-718 | 0.32 | High | 670 | 15 | 24/18°C | 28150 | 2880 | 37
53QDMT30-718 | 0.32 | High | 670 | 15 | 7/6°C | 31460 | 2480 | 37
53QDMT30-718 | 0.32 | High | 670 | 20 | 2/1°C | 24260 | 2350 | 37
53QDMT30-718 | 0.32 | High | 670 | 20 | 24/18°C | 37740 | 3135 | 37
53QDMT30-718 | 0.32 | High | 670 | 20 | 7/6°C | 29960 | 2655 | 37
53QDMT30-718 | 0.32 | High | 670 | 27 | 2/1°C | 22770 | 2540 | 37
53QDMT30-718 | 0.32 | High | 670 | 27 | 24/18°C | 35350 | 3330 | 37
53QDMT30-718 | 0.32 | High | 670 | 27 | 7/6°C | 28180 | 2870 | 37
53QDMT30-718 | 0.32 | Low | 327 | 15 | 2/1°C | 23445 | 1980 | 37
53QDMT30-718 | 0.32 | Low | 327 | 15 | 24/18°C | 35445 | 2655 | 37
53QDMT30-718 | 0.32 | Low | 327 | 15 | 7/6°C | 28635 | 2280 | 37
53QDMT30-718 | 0.32 | Low | 327 | 20 | 2/1°C | 22080 | 2165 | 37
53QDMT30-718 | 0.32 | Low | 327 | 20 | 24/18°C | 34345 | 2890 | 37
53QDMT30-718 | 0.32 | Low | 327 | 20 | 7/6°C | 27270 | 2445 | 37
53QDMT30-718 | 0.32 | Low | 327 | 27 | 2/1°C | 20725 | 2335 | 37
53QDMT30-718 | 0.32 | Low | 327 | 27 | 24/18°C | 32005 | 2910 | 37
53QDMT30-718 | 0.32 | Low | 327 | 27 | 7/6°C | 25690 | 2640 | 37
53QDMT30-718 | 0.32 | Medium | 427 | 15 | 2/1°C | 24475 | 2060 | 37
53QDMT30-718 | 0.32 | Medium | 427 | 15 | 24/18°C | 37005 | 2765 | 37
53QDMT30-718 | 0.32 | Medium | 427 | 15 | 7/6°C | 29885 | 2380 | 37
53QDMT30-718 | 0.32 | Medium | 427 | 20 | 2/1°C | 23050 | 2250 | 37
53QDMT30-718 | 0.32 | Medium | 427 | 20 | 24/18°C | 35855 | 3010 | 37
53QDMT30-718 | 0.32 | Medium | 427 | 20 | 7/6°C | 28460 | 2550 | 37
53QDMT30-718 | 0.32 | Medium | 427 | 27 | 2/1°C | 21635 | 2440 | 37
53QDMT30-718 | 0.32 | Medium | 427 | 27 | 24/18°C | 33585 | 3030 | 37
53QDMT30-718 | 0.32 | Medium | 427 | 27 | 7/6°C | 26770 | 2755 | 37
53QDMT36-718 | 0 | High | 1080 | 15 | 2/1°C | 32235 | 2580 | 38
53QDMT36-718 | 0 | High | 1080 | 15 | 24/18°C | 48725 | 3480 | 38
53QDMT36-718 | 0 | High | 1080 | 15 | 7/6°C | 39355 | 2995 | 38
53QDMT36-718 | 0 | High | 1080 | 20 | 2/1°C | 30360 | 2835 | 38
53QDMT36-718 | 0 | High | 1080 | 20 | 24/18°C | 47225 | 3800 | 38
53QDMT36-718 | 0 | High | 1080 | 20 | 7/6°C | 37500 | 3220 | 38
53QDMT36-718 | 0 | High | 1080 | 27 | 2/1°C | 28485 | 3065 | 38
53QDMT36-718 | 0 | High | 1080 | 27 | 24/18°C | 44225 | 4035 | 38
53QDMT36-718 | 0 | High | 1080 | 27 | 7/6°C | 35230 | 3480 | 38
53QDMT36-718 | 0 | Low | 645 | 15 | 2/1°C | 29335 | 2370 | 38
53QDMT36-718 | 0 | Low | 645 | 15 | 24/18°C | 44345 | 3205 | 38
53QDMT36-718 | 0 | Low | 645 | 15 | 7/6°C | 35815 | 2755 | 38
53QDMT36-718 | 0 | Low | 645 | 20 | 2/1°C | 27630 | 2610 | 38
53QDMT36-718 | 0 | Low | 645 | 20 | 24/18°C | 42980 | 3500 | 38
53QDMT36-718 | 0 | Low | 645 | 20 | 7/6°C | 34110 | 2965 | 38
53QDMT36-718 | 0 | Low | 645 | 27 | 2/1°C | 25925 | 2820 | 38
53QDMT36-718 | 0 | Low | 645 | 27 | 24/18°C | 40250 | 3710 | 38
53QDMT36-718 | 0 | Low | 645 | 27 | 7/6°C | 32065 | 3205 | 38
53QDMT36-718 | 0 | Medium | 730 | 15 | 2/1°C | 30625 | 2475 | 38
53QDMT36-718 | 0 | Medium | 730 | 15 | 24/18°C | 46290 | 3345 | 38
53QDMT36-718 | 0 | Medium | 730 | 15 | 7/6°C | 37390 | 2875 | 38
53QDMT36-718 | 0 | Medium | 730 | 20 | 2/1°C | 28840 | 2725 | 38
53QDMT36-718 | 0 | Medium | 730 | 20 | 24/18°C | 44865 | 3650 | 38
53QDMT36-718 | 0 | Medium | 730 | 20 | 7/6°C | 35605 | 3095 | 38
53QDMT36-718 | 0 | Medium | 730 | 27 | 2/1°C | 27065 | 2940 | 38
53QDMT36-718 | 0 | Medium | 730 | 27 | 24/18°C | 42015 | 3870 | 38
53QDMT36-718 | 0 | Medium | 730 | 27 | 7/6°C | 33475 | 3345 | 38
53QDMT36-718 | 0.08 | High | 1005 | 15 | 2/1°C | 31405 | 2555 | 38
53QDMT36-718 | 0.08 | High | 1005 | 15 | 24/18°C | 47475 | 3450 | 38
53QDMT36-718 | 0.08 | High | 1005 | 15 | 7/6°C | 38345 | 2970 | 38
53QDMT36-718 | 0.08 | High | 1005 | 20 | 2/1°C | 29580 | 2805 | 38
53QDMT36-718 | 0.08 | High | 1005 | 20 | 24/18°C | 46015 | 3760 | 38
53QDMT36-718 | 0.08 | High | 1005 | 20 | 7/6°C | 36520 | 3190 | 38
53QDMT36-718 | 0.08 | High | 1005 | 27 | 2/1°C | 27755 | 3035 | 38
53QDMT36-718 | 0.08 | High | 1005 | 27 | 24/18°C | 43095 | 3995 | 38
53QDMT36-718 | 0.08 | High | 1005 | 27 | 7/6°C | 34330 | 3445 | 38
53QDMT36-718 | 0.08 | Low | 562 | 15 | 2/1°C | 28585 | 2350 | 38
53QDMT36-718 | 0.08 | Low | 562 | 15 | 24/18°C | 43210 | 3175 | 38
53QDMT36-718 | 0.08 | Low | 562 | 15 | 7/6°C | 34895 | 2730 | 38
53QDMT36-718 | 0.08 | Low | 562 | 20 | 2/1°C | 26925 | 2585 | 38
53QDMT36-718 | 0.08 | Low | 562 | 20 | 24/18°C | 41880 | 3465 | 38
53QDMT36-718 | 0.08 | Low | 562 | 20 | 7/6°C | 33235 | 2935 | 38
53QDMT36-718 | 0.08 | Low | 562 | 27 | 2/1°C | 25260 | 2800 | 38
53QDMT36-718 | 0.08 | Low | 562 | 27 | 24/18°C | 39220 | 3675 | 38
53QDMT36-718 | 0.08 | Low | 562 | 27 | 7/6°C | 31245 | 3175 | 38
53QDMT36-718 | 0.08 | Medium | 657 | 15 | 2/1°C | 29840 | 2455 | 38
53QDMT36-718 | 0.08 | Medium | 657 | 15 | 24/18°C | 45105 | 3315 | 38
53QDMT36-718 | 0.08 | Medium | 657 | 15 | 7/6°C | 36435 | 2850 | 38
53QDMT36-718 | 0.08 | Medium | 657 | 20 | 2/1°C | 28105 | 2700 | 38
53QDMT36-718 | 0.08 | Medium | 657 | 20 | 24/18°C | 43720 | 3615 | 38
53QDMT36-718 | 0.08 | Medium | 657 | 20 | 7/6°C | 34695 | 3065 | 38
53QDMT36-718 | 0.08 | Medium | 657 | 27 | 2/1°C | 26370 | 2920 | 38
53QDMT36-718 | 0.08 | Medium | 657 | 27 | 24/18°C | 40940 | 3835 | 38
53QDMT36-718 | 0.08 | Medium | 657 | 27 | 7/6°C | 32620 | 3315 | 38
53QDMT36-718 | 0.12 | High | 976 | 15 | 2/1°C | 30995 | 2545 | 38
53QDMT36-718 | 0.12 | High | 976 | 15 | 24/18°C | 46850 | 3430 | 38
53QDMT36-718 | 0.12 | High | 976 | 15 | 7/6°C | 37840 | 2955 | 38
53QDMT36-718 | 0.12 | High | 976 | 20 | 2/1°C | 29190 | 2790 | 38
53QDMT36-718 | 0.12 | High | 976 | 20 | 24/18°C | 45410 | 3740 | 38
53QDMT36-718 | 0.12 | High | 976 | 20 | 7/6°C | 36040 | 3170 | 38
53QDMT36-718 | 0.12 | High | 976 | 27 | 2/1°C | 27390 | 3020 | 38
53QDMT36-718 | 0.12 | High | 976 | 27 | 24/18°C | 42525 | 3975 | 38
53QDMT36-718 | 0.12 | High | 976 | 27 | 7/6°C | 33875 | 3430 | 38
53QDMT36-718 | 0.12 | Low | 525 | 15 | 2/1°C | 28205 | 2340 | 38
53QDMT36-718 | 0.12 | Low | 525 | 15 | 24/18°C | 42635 | 3155 | 38
53QDMT36-718 | 0.12 | Low | 525 | 15 | 7/6°C | 34440 | 2720 | 38
53QDMT36-718 | 0.12 | Low | 525 | 20 | 2/1°C | 26570 | 2570 | 38
53QDMT36-718 | 0.12 | Low | 525 | 20 | 24/18°C | 41325 | 3440 | 38
53QDMT36-718 | 0.12 | Low | 525 | 20 | 7/6°C | 32795 | 2915 | 38
53QDMT36-718 | 0.12 | Low | 525 | 27 | 2/1°C | 24925 | 2780 | 38
53QDMT36-718 | 0.12 | Low | 525 | 27 | 24/18°C | 38700 | 3660 | 38
53QDMT36-718 | 0.12 | Low | 525 | 27 | 7/6°C | 30830 | 3155 | 38
53QDMT36-718 | 0.12 | Medium | 624 | 15 | 2/1°C | 29445 | 2445 | 38
53QDMT36-718 | 0.12 | Medium | 624 | 15 | 24/18°C | 44510 | 3295 | 38
53QDMT36-718 | 0.12 | Medium | 624 | 15 | 7/6°C | 35955 | 2840 | 38
53QDMT36-718 | 0.12 | Medium | 624 | 20 | 2/1°C | 27735 | 2680 | 38
53QDMT36-718 | 0.12 | Medium | 624 | 20 | 24/18°C | 43140 | 3590 | 38
53QDMT36-718 | 0.12 | Medium | 624 | 20 | 7/6°C | 34240 | 3045 | 38
53QDMT36-718 | 0.12 | Medium | 624 | 27 | 2/1°C | 26020 | 2900 | 38
53QDMT36-718 | 0.12 | Medium | 624 | 27 | 24/18°C | 40400 | 3815 | 38
53QDMT36-718 | 0.12 | Medium | 624 | 27 | 7/6°C | 32185 | 3295 | 38
53QDMT36-718 | 0.16 | High | 947 | 15 | 2/1°C | 30580 | 2530 | 38
53QDMT36-718 | 0.16 | High | 947 | 15 | 24/18°C | 46225 | 3415 | 38
53QDMT36-718 | 0.16 | High | 947 | 15 | 7/6°C | 37335 | 2940 | 38
53QDMT36-718 | 0.16 | High | 947 | 20 | 2/1°C | 28805 | 2775 | 38
53QDMT36-718 | 0.16 | High | 947 | 20 | 24/18°C | 44805 | 3720 | 38
53QDMT36-718 | 0.16 | High | 947 | 20 | 7/6°C | 35560 | 3154 | 38
53QDMT36-718 | 0.16 | High | 947 | 27 | 2/1°C | 27025 | 3005 | 38
53QDMT36-718 | 0.16 | High | 947 | 27 | 24/18°C | 41960 | 3955 | 38
53QDMT36-718 | 0.16 | High | 947 | 27 | 7/6°C | 33425 | 3410 | 38
53QDMT36-718 | 0.16 | Low | 495 | 15 | 2/1°C | 27835 | 2330 | 38
53QDMT36-718 | 0.16 | Low | 495 | 15 | 24/18°C | 42070 | 3145 | 38
53QDMT36-718 | 0.16 | Low | 495 | 15 | 7/6°C | 33980 | 2705 | 38
53QDMT36-718 | 0.16 | Low | 495 | 20 | 2/1°C | 26215 | 2560 | 38
53QDMT36-718 | 0.16 | Low | 495 | 20 | 24/18°C | 40770 | 3425 | 38
53QDMT36-718 | 0.16 | Low | 495 | 20 | 7/6°C | 32360 | 2900 | 38
53QDMT36-718 | 0.16 | Low | 495 | 27 | 2/1°C | 24595 | 2765 | 38
53QDMT36-718 | 0.16 | Low | 495 | 27 | 24/18°C | 38185 | 3640 | 38
53QDMT36-718 | 0.16 | Low | 495 | 27 | 7/6°C | 30420 | 3140 | 38
53QDMT36-718 | 0.16 | Medium | 591 | 15 | 2/1°C | 29055 | 2430 | 38
53QDMT36-718 | 0.16 | Medium | 591 | 15 | 24/18°C | 43920 | 3280 | 38
53QDMT36-718 | 0.16 | Medium | 591 | 15 | 7/6°C | 35475 | 2825 | 38
53QDMT36-718 | 0.16 | Medium | 591 | 20 | 2/1°C | 27365 | 2670 | 38
53QDMT36-718 | 0.16 | Medium | 591 | 20 | 24/18°C | 42565 | 3575 | 38
53QDMT36-718 | 0.16 | Medium | 591 | 20 | 7/6°C | 33780 | 3030 | 38
53QDMT36-718 | 0.16 | Medium | 591 | 27 | 2/1°C | 25675 | 2885 | 38
53QDMT36-718 | 0.16 | Medium | 591 | 27 | 24/18°C | 39865 | 3795 | 38
53QDMT36-718 | 0.16 | Medium | 591 | 27 | 7/6°C | 31760 | 3280 | 38
53QDMT36-718 | 0.2 | High | 915 | 15 | 2/1°C | 30170 | 2515
53QDMT36-718 | 0.2 | High | 915 | 15 | 24/18°C | 45600 | 3395
53QDMT36-718 | 0.2 | High | 915 | 15 | 7/6°C | 36830 | 2920
53QDMT36-718 | 0.2 | High | 915 | 20 | 2/1°C | 28415 | 2760
53QDMT36-718 | 0.2 | High | 915 | 20 | 24/18°C | 44200 | 3700
53QDMT36-718 | 0.2 | High | 915 | 20 | 7/6°C | 35080 | 3135
53QDMT36-718 | 0.2 | High | 915 | 27 | 2/1°C | 26660 | 2985
53QDMT36-718 | 0.2 | High | 915 | 27 | 24/18°C | 41390 | 3930
53QDMT36-718 | 0.2 | High | 915 | 27 | 7/6°C | 32975 | 3390
53QDMT36-718 | 0.2 | Low | 453 | 15 | 2/1°C | 27455 | 2315
53QDMT36-718 | 0.2 | Low | 453 | 15 | 24/18°C | 41500 | 3130
53QDMT36-718 | 0.2 | Low | 453 | 15 | 7/6°C | 33515 | 2690
53QDMT36-718 | 0.2 | Low | 453 | 20 | 2/1°C | 25860 | 2545
53QDMT36-718 | 0.2 | Low | 453 | 20 | 24/18°C | 40220 | 3410
53QDMT36-718 | 0.2 | Low | 453 | 20 | 7/6°C | 31920 | 2885
53QDMT36-718 | 0.2 | Low | 453 | 27 | 2/1°C | 24260 | 2750
53QDMT36-718 | 0.2 | Low | 453 | 27 | 24/18°C | 37670 | 3615
53QDMT36-718 | 0.2 | Low | 453 | 27 | 7/6°C | 30010 | 3125
53QDMT36-718 | 0.2 | Medium | 550 | 15 | 2/1°C | 28660 | 2415
53QDMT36-718 | 0.2 | Medium | 550 | 15 | 24/18°C | 43325 | 3265
53QDMT36-718 | 0.2 | Medium | 550 | 15 | 7/6°C | 34990 | 2805
53QDMT36-718 | 0.2 | Medium | 550 | 20 | 2/1°C | 26995 | 2655
53QDMT36-718 | 0.2 | Medium | 550 | 20 | 24/18°C | 41990 | 3555
53QDMT36-718 | 0.2 | Medium | 550 | 20 | 7/6°C | 33325 | 3015
53QDMT36-718 | 0.2 | Medium | 550 | 27 | 2/1°C | 25325 | 2865
53QDMT36-718 | 0.2 | Medium | 550 | 27 | 24/18°C | 39325 | 3770
53QDMT36-718 | 0.2 | Medium | 550 | 27 | 7/6°C | 31325 | 3260
53QDMT36-718 | 0.24 | High | 883 | 15 | 2/1°C | 29755 | 2505 | 39
53QDMT36-718 | 0.24 | High | 883 | 15 | 24/18°C | 44975 | 3380 | 39
53QDMT36-718 | 0.24 | High | 883 | 15 | 7/6°C | 36330 | 2905 | 39
53QDMT36-718 | 0.24 | High | 883 | 20 | 2/1°C | 28025 | 2745 | 39
53QDMT36-718 | 0.24 | High | 883 | 20 | 24/18°C | 43595 | 3680 | 39
53QDMT36-718 | 0.24 | High | 883 | 20 | 7/6°C | 34600 | 3120 | 39
53QDMT36-718 | 0.24 | High | 883 | 27 | 2/1°C | 26295 | 2970 | 39
53QDMT36-718 | 0.24 | High | 883 | 27 | 24/18°C | 40825 | 3910 | 39
53QDMT36-718 | 0.24 | High | 883 | 27 | 7/6°C | 32520 | 3370 | 39
53QDMT36-718 | 0.24 | Low | 411 | 15 | 2/1°C | 27080 | 2305 | 39
53QDMT36-718 | 0.24 | Low | 411 | 15 | 24/18°C | 40930 | 3110 | 39
53QDMT36-718 | 0.24 | Low | 411 | 15 | 7/6°C | 33060 | 2675 | 39
53QDMT36-718 | 0.24 | Low | 411 | 20 | 2/1°C | 25505 | 2530 | 39
53QDMT36-718 | 0.24 | Low | 411 | 20 | 24/18°C | 39890 | 3390 | 39
53QDMT36-718 | 0.24 | Low | 411 | 20 | 7/6°C | 31485 | 2870 | 39
53QDMT36-718 | 0.24 | Low | 411 | 27 | 2/1°C | 23930 | 2735 | 39
53QDMT36-718 | 0.24 | Low | 411 | 27 | 24/18°C | 37355 | 3595 | 39
53QDMT36-718 | 0.24 | Low | 411 | 27 | 7/6°C | 29600 | 3105 | 39
53QDMT36-718 | 0.24 | Medium | 509 | 15 | 2/1°C | 28270 | 2405 | 39
53QDMT36-718 | 0.24 | Medium | 509 | 15 | 24/18°C | 42735 | 3245 | 39
53QDMT36-718 | 0.24 | Medium | 509 | 15 | 7/6°C | 34515 | 2790 | 39
53QDMT36-718 | 0.24 | Medium | 509 | 20 | 2/1°C | 26625 | 2640 | 39
53QDMT36-718 | 0.24 | Medium | 509 | 20 | 24/18°C | 41415 | 3535 | 39
53QDMT36-718 | 0.24 | Medium | 509 | 20 | 7/6°C | 32870 | 2995 | 39
53QDMT36-718 | 0.24 | Medium | 509 | 27 | 2/1°C | 24990 | 2850 | 39
53QDMT36-718 | 0.24 | Medium | 509 | 27 | 24/18°C | 38790 | 3750 | 39
53QDMT36-718 | 0.24 | Medium | 509 | 27 | 7/6°C | 30900 | 3240 | 39
53QDMT36-718 | 0.28 | High | 851 | 15 | 2/1°C | 29340 | 2490 | 39
53QDMT36-718 | 0.28 | High | 851 | 15 | 24/18°C | 44350 | 3360 | 39
53QDMT36-718 | 0.28 | High | 851 | 15 | 7/6°C | 35825 | 2890 | 39
53QDMT36-718 | 0.28 | High | 851 | 20 | 2/1°C | 27635 | 2730 | 39
53QDMT36-718 | 0.28 | High | 851 | 20 | 24/18°C | 42990 | 3660 | 39
53QDMT36-718 | 0.28 | High | 851 | 20 | 7/6°C | 34120 | 3100 | 39
53QDMT36-718 | 0.28 | High | 851 | 27 | 2/1°C | 25930 | 2950 | 39
53QDMT36-718 | 0.28 | High | 851 | 27 | 24/18°C | 40260 | 3885 | 39
53QDMT36-718 | 0.28 | High | 851 | 27 | 7/6°C | 32070 | 3350 | 39
53QDMT36-718 | 0.28 | Low | 369 | 15 | 2/1°C | 26705 | 2290 | 39
53QDMT36-718 | 0.28 | Low | 369 | 15 | 24/18°C | 40365 | 3090 | 39
53QDMT36-718 | 0.28 | Low | 369 | 15 | 7/6°C | 32600 | 2660 | 39
53QDMT36-718 | 0.28 | Low | 369 | 20 | 2/1°C | 25150 | 2510 | 39
53QDMT36-718 | 0.28 | Low | 369 | 20 | 24/18°C | 39550 | 3370 | 39
53QDMT36-718 | 0.28 | Low | 369 | 20 | 7/6°C | 31045 | 2855 | 39
53QDMT36-718 | 0.28 | Low | 369 | 27 | 2/1°C | 23600 | 2715 | 39
53QDMT36-718 | 0.28 | Low | 369 | 27 | 24/18°C | 37040 | 3575 | 39
53QDMT36-718 | 0.28 | Low | 369 | 27 | 7/6°C | 29190 | 3085 | 39
53QDMT36-718 | 0.28 | Medium | 468 | 15 | 2/1°C | 27875 | 2390 | 39
53QDMT36-718 | 0.28 | Medium | 468 | 15 | 24/18°C | 42135 | 3225 | 39
53QDMT36-718 | 0.28 | Medium | 468 | 15 | 7/6°C | 34035 | 2775 | 39
53QDMT36-718 | 0.28 | Medium | 468 | 20 | 2/1°C | 26255 | 2620 | 39
53QDMT36-718 | 0.28 | Medium | 468 | 20 | 24/18°C | 40840 | 3515 | 39
53QDMT36-718 | 0.28 | Medium | 468 | 20 | 7/6°C | 32410 | 2975 | 39
53QDMT36-718 | 0.28 | Medium | 468 | 27 | 2/1°C | 24635 | 2835 | 39
53QDMT36-718 | 0.28 | Medium | 468 | 27 | 24/18°C | 38245 | 3730 | 39
53QDMT36-718 | 0.28 | Medium | 468 | 27 | 7/6°C | 30470 | 3215 | 39
53QDMT36-718 | 0.32 | High | 819 | 15 | 2/1°C | 28930 | 2475 | 39
53QDMT36-718 | 0.32 | High | 819 | 15 | 24/18°C | 43730 | 3340 | 39
53QDMT36-718 | 0.32 | High | 819 | 15 | 7/6°C | 35320 | 2875 | 39
53QDMT36-718 | 0.32 | High | 819 | 20 | 2/1°C | 27245 | 2715 | 39
53QDMT36-718 | 0.32 | High | 819 | 20 | 24/18°C | 42380 | 3640 | 39
53QDMT36-718 | 0.32 | High | 819 | 20 | 7/6°C | 33635 | 3080 | 39
53QDMT36-718 | 0.32 | High | 819 | 27 | 2/1°C | 25565 | 2930 | 39
53QDMT36-718 | 0.32 | High | 819 | 27 | 24/18°C | 39690 | 3860 | 39
53QDMT36-718 | 0.32 | High | 819 | 27 | 7/6°C | 31620 | 3330 | 39
53QDMT36-718 | 0.32 | Low | 327 | 15 | 2/1°C | 26330 | 2275 | 39
53QDMT36-718 | 0.32 | Low | 327 | 15 | 24/18°C | 39795 | 3070 | 39
53QDMT36-718 | 0.32 | Low | 327 | 15 | 7/6°C | 32140 | 2645 | 39
53QDMT36-718 | 0.32 | Low | 327 | 20 | 2/1°C | 24795 | 2490 | 39
53QDMT36-718 | 0.32 | Low | 327 | 20 | 24/18°C | 39215 | 3350 | 39
53QDMT36-718 | 0.32 | Low | 327 | 20 | 7/6°C | 30610 | 2840 | 39
53QDMT36-718 | 0.32 | Low | 327 | 27 | 2/1°C | 23270 | 2695 | 39
53QDMT36-718 | 0.32 | Low | 327 | 27 | 24/18°C | 36720 | 3555 | 39
53QDMT36-718 | 0.32 | Low | 327 | 27 | 7/6°C | 28775 | 3065 | 39
53QDMT36-718 | 0.32 | Medium | 427 | 15 | 2/1°C | 27480 | 2375 | 39
53QDMT36-718 | 0.32 | Medium | 427 | 15 | 24/18°C | 41540 | 3205 | 39
53QDMT36-718 | 0.32 | Medium | 427 | 15 | 7/6°C | 33555 | 2760 | 39
53QDMT36-718 | 0.32 | Medium | 427 | 20 | 2/1°C | 25885 | 2600 | 39
53QDMT36-718 | 0.32 | Medium | 427 | 20 | 24/18°C | 40265 | 3495 | 39
53QDMT36-718 | 0.32 | Medium | 427 | 20 | 7/6°C | 31955 | 2955 | 39
53QDMT36-718 | 0.32 | Medium | 427 | 27 | 2/1°C | 24285 | 2820 | 39
53QDMT36-718 | 0.32 | Medium | 427 | 27 | 24/18°C | 37700 | 3710 | 39
53QDMT36-718 | 0.32 | Medium | 427 | 27 | 7/6°C | 30045 | 3190 | 39
53QDMT42-718 | 0 | High | 1370 | 15 | 2/1°C | 32235 | 2565 | 40
53QDMT42-718 | 0 | High | 1370 | 15 | 24/18°C | 48725 | 3460 | 40
53QDMT42-718 | 0 | High | 1370 | 15 | 7/6°C | 39355 | 2980 | 40
53QDMT42-718 | 0 | High | 1370 | 20 | 2/1°C | 30360 | 2820 | 40
53QDMT42-718 | 0 | High | 1370 | 20 | 24/18°C | 47225 | 3780 | 40
53QDMT42-718 | 0 | High | 1370 | 20 | 7/6°C | 37500 | 3200 | 40
53QDMT42-718 | 0 | High | 1370 | 27 | 2/1°C | 28485 | 3050 | 40
53QDMT42-718 | 0 | High | 1370 | 27 | 24/18°C | 44225 | 4015 | 40
53QDMT42-718 | 0 | High | 1370 | 27 | 7/6°C | 35230 | 3460 | 40
53QDMT42-718 | 0 | Low | 715 | 15 | 2/1°C | 29335 | 2360 | 40
53QDMT42-718 | 0 | Low | 715 | 15 | 24/18°C | 44345 | 3190 | 40
53QDMT42-718 | 0 | Low | 715 | 15 | 7/6°C | 35815 | 2740 | 40
53QDMT42-718 | 0 | Low | 715 | 20 | 2/1°C | 27630 | 2595 | 40
53QDMT42-718 | 0 | Low | 715 | 20 | 24/18°C | 42980 | 3480 | 40
53QDMT42-718 | 0 | Low | 715 | 20 | 7/6°C | 34110 | 2950 | 40
53QDMT42-718 | 0 | Low | 715 | 27 | 2/1°C | 25925 | 2805 | 40
53QDMT42-718 | 0 | Low | 715 | 27 | 24/18°C | 40250 | 3690 | 40
53QDMT42-718 | 0 | Low | 715 | 27 | 7/6°C | 32065 | 3190 | 40
53QDMT42-718 | 0 | Medium | 880 | 15 | 2/1°C | 30625 | 2460 | 40
53QDMT42-718 | 0 | Medium | 880 | 15 | 24/18°C | 46290 | 3325 | 40
53QDMT42-718 | 0 | Medium | 880 | 15 | 7/6°C | 37390 | 2860 | 40
53QDMT42-718 | 0 | Medium | 880 | 20 | 2/1°C | 28840 | 2710 | 40
53QDMT42-718 | 0 | Medium | 880 | 20 | 24/18°C | 44865 | 3630 | 40
53QDMT42-718 | 0 | Medium | 880 | 20 | 7/6°C | 35605 | 3080 | 40
53QDMT42-718 | 0 | Medium | 880 | 27 | 2/1°C | 27065 | 2925 | 40
53QDMT42-718 | 0 | Medium | 880 | 27 | 24/18°C | 42015 | 3850 | 40
53QDMT42-718 | 0 | Medium | 880 | 27 | 7/6°C | 33475 | 3325 | 40
53QDMT42-718 | 0.08 | High | 1300 | 15 | 2/1°C | 31405 | 2540 | 40
53QDMT42-718 | 0.08 | High | 1300 | 15 | 24/18°C | 47475 | 3430 | 40
53QDMT42-718 | 0.08 | High | 1300 | 15 | 7/6°C | 38345 | 2950 | 40
53QDMT42-718 | 0.08 | High | 1300 | 20 | 2/1°C | 29580 | 2790 | 40
53QDMT42-718 | 0.08 | High | 1300 | 20 | 24/18°C | 46015 | 3740 | 40
53QDMT42-718 | 0.08 | High | 1300 | 20 | 7/6°C | 36520 | 3170 | 40
53QDMT42-718 | 0.08 | High | 1300 | 27 | 2/1°C | 27755 | 3020 | 40
53QDMT42-718 | 0.08 | High | 1300 | 27 | 24/18°C | 43095 | 3975 | 40
53QDMT42-718 | 0.08 | High | 1300 | 27 | 7/6°C | 34330 | 3425 | 40
53QDMT42-718 | 0.08 | Low | 636 | 15 | 2/1°C | 28585 | 2340 | 40
53QDMT42-718 | 0.08 | Low | 636 | 15 | 24/18°C | 43210 | 3160 | 40
53QDMT42-718 | 0.08 | Low | 636 | 15 | 7/6°C | 34895 | 2715 | 40
53QDMT42-718 | 0.08 | Low | 636 | 20 | 2/1°C | 26925 | 2570 | 40
53QDMT42-718 | 0.08 | Low | 636 | 20 | 24/18°C | 41880 | 3445 | 40
53QDMT42-718 | 0.08 | Low | 636 | 20 | 7/6°C | 33235 | 2920 | 40
53QDMT42-718 | 0.08 | Low | 636 | 27 | 2/1°C | 25260 | 2780 | 40
53QDMT42-718 | 0.08 | Low | 636 | 27 | 24/18°C | 39220 | 3655 | 40
53QDMT42-718 | 0.08 | Low | 636 | 27 | 7/6°C | 31245 | 3160 | 40
53QDMT42-718 | 0.08 | Medium | 803 | 15 | 2/1°C | 29840 | 2440 | 40
53QDMT42-718 | 0.08 | Medium | 803 | 15 | 24/18°C | 45105 | 3295 | 40
53QDMT42-718 | 0.08 | Medium | 803 | 15 | 7/6°C | 36435 | 2835 | 40
53QDMT42-718 | 0.08 | Medium | 803 | 20 | 2/1°C | 28105 | 2685 | 40
53QDMT42-718 | 0.08 | Medium | 803 | 20 | 24/18°C | 43720 | 3595 | 40
53QDMT42-718 | 0.08 | Medium | 803 | 20 | 7/6°C | 34695 | 3050 | 40
53QDMT42-718 | 0.08 | Medium | 803 | 27 | 2/1°C | 26370 | 2895 | 40
53QDMT42-718 | 0.08 | Medium | 803 | 27 | 24/18°C | 40940 | 3810 | 40
53QDMT42-718 | 0.08 | Medium | 803 | 27 | 7/6°C | 32620 | 3295 | 40
53QDMT42-718 | 0.12 | High | 1255 | 15 | 2/1°C | 30995 | 2530 | 40
53QDMT42-718 | 0.12 | High | 1255 | 15 | 24/18°C | 46850 | 3410 | 40
53QDMT42-718 | 0.12 | High | 1255 | 15 | 7/6°C | 37840 | 2935 | 40
53QDMT42-718 | 0.12 | High | 1255 | 20 | 2/1°C | 29190 | 2775 | 40
53QDMT42-718 | 0.12 | High | 1255 | 20 | 24/18°C | 45410 | 3720 | 40
53QDMT42-718 | 0.12 | High | 1255 | 20 | 7/6°C | 36040 | 3155 | 40
53QDMT42-718 | 0.12 | High | 1255 | 27 | 2/1°C | 27390 | 3005 | 40
53QDMT42-718 | 0.12 | High | 1255 | 27 | 24/18°C | 42525 | 3955 | 40
53QDMT42-718 | 0.12 | High | 1255 | 27 | 7/6°C | 33875 | 3410 | 40
53QDMT42-718 | 0.12 | Low | 594 | 15 | 2/1°C | 28205 | 2330 | 40
53QDMT42-718 | 0.12 | Low | 594 | 15 | 24/18°C | 42635 | 3145 | 40
53QDMT42-718 | 0.12 | Low | 594 | 15 | 7/6°C | 34440 | 2705 | 40
53QDMT42-718 | 0.12 | Low | 594 | 20 | 2/1°C | 26570 | 2560 | 40
53QDMT42-718 | 0.12 | Low | 594 | 20 | 24/18°C | 41325 | 3430 | 40
53QDMT42-718 | 0.12 | Low | 594 | 20 | 7/6°C | 32795 | 2905 | 40
53QDMT42-718 | 0.12 | Low | 594 | 27 | 2/1°C | 24930 | 2765 | 40
53QDMT42-718 | 0.12 | Low | 594 | 27 | 24/18°C | 38700 | 3635 | 40
53QDMT42-718 | 0.12 | Low | 594 | 27 | 7/6°C | 30835 | 3145 | 40
53QDMT42-718 | 0.12 | Medium | 770 | 15 | 2/1°C | 29445 | 2425 | 40
53QDMT42-718 | 0.12 | Medium | 770 | 15 | 24/18°C | 44510 | 3280 | 40
53QDMT42-718 | 0.12 | Medium | 770 | 15 | 7/6°C | 35955 | 2820 | 40
53QDMT42-718 | 0.12 | Medium | 770 | 20 | 2/1°C | 27735 | 2670 | 40
53QDMT42-718 | 0.12 | Medium | 770 | 20 | 24/18°C | 43140 | 3575 | 40
53QDMT42-718 | 0.12 | Medium | 770 | 20 | 7/6°C | 34240 | 3035 | 40
53QDMT42-718 | 0.12 | Medium | 770 | 27 | 2/1°C | 26025 | 2880 | 40
53QDMT42-718 | 0.12 | Medium | 770 | 27 | 24/18°C | 40400 | 3790 | 40
53QDMT42-718 | 0.12 | Medium | 770 | 27 | 7/6°C | 32185 | 3275 | 40
53QDMT42-718 | 0.16 | High | 1223 | 15 | 2/1°C | 30580 | 2515 | 40
53QDMT42-718 | 0.16 | High | 1223 | 15 | 24/18°C | 46225 | 3393 | 40
53QDMT42-718 | 0.16 | High | 1223 | 15 | 7/6°C | 37335 | 2920 | 40
53QDMT42-718 | 0.16 | High | 1223 | 20 | 2/1°C | 28805 | 2760 | 40
53QDMT42-718 | 0.16 | High | 1223 | 20 | 24/18°C | 44805 | 3700 | 40
53QDMT42-718 | 0.16 | High | 1223 | 20 | 7/6°C | 35560 | 3138 | 40
53QDMT42-718 | 0.16 | High | 1223 | 27 | 2/1°C | 27025 | 2988 | 40
53QDMT42-718 | 0.16 | High | 1223 | 27 | 24/18°C | 41960 | 3933 | 40
53QDMT42-718 | 0.16 | High | 1223 | 27 | 7/6°C | 33425 | 3390 | 40
53QDMT42-718 | 0.16 | Low | 548 | 15 | 2/1°C | 27830 | 2318 | 40
53QDMT42-718 | 0.16 | Low | 548 | 15 | 24/18°C | 42070 | 3130 | 40
53QDMT42-718 | 0.16 | Low | 548 | 15 | 7/6°C | 33980 | 2690 | 40
53QDMT42-718 | 0.16 | Low | 548 | 20 | 2/1°C | 26215 | 2545 | 40
53QDMT42-718 | 0.16 | Low | 548 | 20 | 24/18°C | 40770 | 3410 | 40
53QDMT42-718 | 0.16 | Low | 548 | 20 | 7/6°C | 32360 | 2888 | 40
53QDMT42-718 | 0.16 | Low | 548 | 27 | 2/1°C | 24595 | 2750 | 40
53QDMT42-718 | 0.16 | Low | 548 | 27 | 24/18°C | 38185 | 3615 | 40
53QDMT42-718 | 0.16 | Low | 548 | 27 | 7/6°C | 30420 | 3128 | 40
53QDMT42-718 | 0.16 | Medium | 733 | 15 | 2/1°C | 29055 | 2413 | 40
53QDMT42-718 | 0.16 | Medium | 733 | 15 | 24/18°C | 43920 | 3263 | 40
53QDMT42-718 | 0.16 | Medium | 733 | 15 | 7/6°C | 35475 | 2805 | 40
53QDMT42-718 | 0.16 | Medium | 733 | 20 | 2/1°C | 27365 | 2655 | 40
53QDMT42-718 | 0.16 | Medium | 733 | 20 | 24/18°C | 42565 | 3555 | 40
53QDMT42-718 | 0.16 | Medium | 733 | 20 | 7/6°C | 33780 | 3018 | 40
53QDMT42-718 | 0.16 | Medium | 733 | 27 | 2/1°C | 25680 | 2865 | 40
53QDMT42-718 | 0.16 | Medium | 733 | 27 | 24/18°C | 39865 | 3770 | 40
53QDMT42-718 | 0.16 | Medium | 733 | 27 | 7/6°C | 31755 | 3258 | 40
53QDMT42-718 | 0.2 | High | 1187 | 15 | 2/1°C | 30170 | 2500 | 40
53QDMT42-718 | 0.2 | High | 1187 | 15 | 24/18°C | 45600 | 3375 | 40
53QDMT42-718 | 0.2 | High | 1187 | 15 | 7/6°C | 36830 | 2905 | 40
53QDMT42-718 | 0.2 | High | 1187 | 20 | 2/1°C | 28415 | 2745 | 40
53QDMT42-718 | 0.2 | High | 1187 | 20 | 24/18°C | 44200 | 3680 | 40
53QDMT42-718 | 0.2 | High | 1187 | 20 | 7/6°C | 35080 | 3120 | 40
53QDMT42-718 | 0.2 | High | 1187 | 27 | 2/1°C | 26660 | 2970 | 40
53QDMT42-718 | 0.2 | High | 1187 | 27 | 24/18°C | 41390 | 3910 | 40
53QDMT42-718 | 0.2 | High | 1187 | 27 | 7/6°C | 32975 | 3370 | 40
53QDMT42-718 | 0.2 | Low | 491 | 15 | 2/1°C | 27455 | 2305 | 40
53QDMT42-718 | 0.2 | Low | 491 | 15 | 24/18°C | 41500 | 3115 | 40
53QDMT42-718 | 0.2 | Low | 491 | 15 | 7/6°C | 33515 | 2675 | 40
53QDMT42-718 | 0.2 | Low | 491 | 20 | 2/1°C | 25860 | 2530 | 40
53QDMT42-718 | 0.2 | Low | 491 | 20 | 24/18°C | 40220 | 3390 | 40
53QDMT42-718 | 0.2 | Low | 491 | 20 | 7/6°C | 31920 | 2870 | 40
53QDMT42-718 | 0.2 | Low | 491 | 27 | 2/1°C | 24260 | 2735 | 40
53QDMT42-718 | 0.2 | Low | 491 | 27 | 24/18°C | 37670 | 3595 | 40
53QDMT42-718 | 0.2 | Low | 491 | 27 | 7/6°C | 30010 | 3110 | 40
53QDMT42-718 | 0.2 | Medium | 693 | 15 | 2/1°C | 28660 | 2400 | 40
53QDMT42-718 | 0.2 | Medium | 693 | 15 | 24/18°C | 43325 | 3245 | 40
53QDMT42-718 | 0.2 | Medium | 693 | 15 | 7/6°C | 34990 | 2790 | 40
53QDMT42-718 | 0.2 | Medium | 693 | 20 | 2/1°C | 26995 | 2640 | 40
53QDMT42-718 | 0.2 | Medium | 693 | 20 | 24/18°C | 41990 | 3535 | 40
53QDMT42-718 | 0.2 | Medium | 693 | 20 | 7/6°C | 33325 | 3000 | 40
53QDMT42-718 | 0.2 | Medium | 693 | 27 | 2/1°C | 25330 | 2850 | 40
53QDMT42-718 | 0.2 | Medium | 693 | 27 | 24/18°C | 39325 | 3750 | 40
53QDMT42-718 | 0.2 | Medium | 693 | 27 | 7/6°C | 31325 | 3240 | 40
53QDMT42-718 | 0.24 | High | 1151 | 15 | 2/1°C | 29755 | 2490
53QDMT42-718 | 0.24 | High | 1151 | 15 | 24/18°C | 44975 | 3360
53QDMT42-718 | 0.24 | High | 1151 | 15 | 7/6°C | 36330 | 2890
53QDMT42-718 | 0.24 | High | 1151 | 20 | 2/1°C | 28025 | 2735
53QDMT42-718 | 0.24 | High | 1151 | 20 | 24/18°C | 43595 | 3660
53QDMT42-718 | 0.24 | High | 1151 | 20 | 7/6°C | 34600 | 3105
53QDMT42-718 | 0.24 | High | 1151 | 27 | 2/1°C | 26295 | 2955
53QDMT42-718 | 0.24 | High | 1151 | 27 | 24/18°C | 40825 | 3890
53QDMT42-718 | 0.24 | High | 1151 | 27 | 7/6°C | 32520 | 3350
53QDMT42-718 | 0.24 | Low | 434 | 15 | 2/1°C | 27080 | 2295
53QDMT42-718 | 0.24 | Low | 434 | 15 | 24/18°C | 40930 | 3095
53QDMT42-718 | 0.24 | Low | 434 | 15 | 7/6°C | 33060 | 2660
53QDMT42-718 | 0.24 | Low | 434 | 20 | 2/1°C | 25505 | 2520
53QDMT42-718 | 0.24 | Low | 434 | 20 | 24/18°C | 39890 | 3370
53QDMT42-718 | 0.24 | Low | 434 | 20 | 7/6°C | 31485 | 2860
53QDMT42-718 | 0.24 | Low | 434 | 27 | 2/1°C | 23930 | 2720
53QDMT42-718 | 0.24 | Low | 434 | 27 | 24/18°C | 37355 | 3575
53QDMT42-718 | 0.24 | Low | 434 | 27 | 7/6°C | 29600 | 3090
53QDMT42-718 | 0.24 | Medium | 653 | 15 | 2/1°C | 28270 | 2390
53QDMT42-718 | 0.24 | Medium | 653 | 15 | 24/18°C | 42735 | 3230
53QDMT42-718 | 0.24 | Medium | 653 | 15 | 7/6°C | 34515 | 2775
53QDMT42-718 | 0.24 | Medium | 653 | 20 | 2/1°C | 26625 | 2625
53QDMT42-718 | 0.24 | Medium | 653 | 20 | 24/18°C | 41415 | 3515
53QDMT42-718 | 0.24 | Medium | 653 | 20 | 7/6°C | 32870 | 2985
53QDMT42-718 | 0.24 | Medium | 653 | 27 | 2/1°C | 24985 | 2835
53QDMT42-718 | 0.24 | Medium | 653 | 27 | 24/18°C | 38790 | 3730
53QDMT42-718 | 0.24 | Medium | 653 | 27 | 7/6°C | 30900 | 3220
53QDMT42-718 | 0.28 | High | 1115 | 15 | 2/1°C | 29340 | 2475 | 41
53QDMT42-718 | 0.28 | High | 1115 | 15 | 24/18°C | 44350 | 3340 | 41
53QDMT42-718 | 0.28 | High | 1115 | 15 | 7/6°C | 35825 | 2875 | 41
53QDMT42-718 | 0.28 | High | 1115 | 20 | 2/1°C | 27635 | 2720 | 41
53QDMT42-718 | 0.28 | High | 1115 | 20 | 24/18°C | 42990 | 3640 | 41
53QDMT42-718 | 0.28 | High | 1115 | 20 | 7/6°C | 34120 | 3090 | 41
53QDMT42-718 | 0.28 | High | 1115 | 27 | 2/1°C | 25930 | 2935 | 41
53QDMT42-718 | 0.28 | High | 1115 | 27 | 24/18°C | 40260 | 3865 | 41
53QDMT42-718 | 0.28 | High | 1115 | 27 | 7/6°C | 32070 | 3330 | 41
53QDMT42-718 | 0.28 | Low | 377 | 15 | 2/1°C | 26705 | 2280 | 41
53QDMT42-718 | 0.28 | Low | 377 | 15 | 24/18°C | 40365 | 3075 | 41
53QDMT42-718 | 0.28 | Low | 377 | 15 | 7/6°C | 32600 | 2645 | 41
53QDMT42-718 | 0.28 | Low | 377 | 20 | 2/1°C | 25150 | 2505 | 41
53QDMT42-718 | 0.28 | Low | 377 | 20 | 24/18°C | 39550 | 3350 | 41
53QDMT42-718 | 0.28 | Low | 377 | 20 | 7/6°C | 31045 | 2845 | 41
53QDMT42-718 | 0.28 | Low | 377 | 27 | 2/1°C | 23600 | 2700 | 41
53QDMT42-718 | 0.28 | Low | 377 | 27 | 24/18°C | 37040 | 3555 | 41
53QDMT42-718 | 0.28 | Low | 377 | 27 | 7/6°C | 29190 | 3065 | 41
53QDMT42-718 | 0.28 | Medium | 613 | 15 | 2/1°C | 27875 | 2375 | 41
53QDMT42-718 | 0.28 | Medium | 613 | 15 | 24/18°C | 42135 | 3210 | 41
53QDMT42-718 | 0.28 | Medium | 613 | 15 | 7/6°C | 34035 | 2760 | 41
53QDMT42-718 | 0.28 | Medium | 613 | 20 | 2/1°C | 26255 | 2610 | 41
53QDMT42-718 | 0.28 | Medium | 613 | 20 | 24/18°C | 40840 | 3495 | 41
53QDMT42-718 | 0.28 | Medium | 613 | 20 | 7/6°C | 32410 | 2965 | 41
53QDMT42-718 | 0.28 | Medium | 613 | 27 | 2/1°C | 24635 | 2820 | 41
53QDMT42-718 | 0.28 | Medium | 613 | 27 | 24/18°C | 38245 | 3710 | 41
53QDMT42-718 | 0.28 | Medium | 613 | 27 | 7/6°C | 30470 | 3200 | 41
53QDMT42-718 | 0.32 | High | 1079 | 15 | 2/1°C | 28930 | 2460 | 41
53QDMT42-718 | 0.32 | High | 1079 | 15 | 24/18°C | 43730 | 3320 | 41
53QDMT42-718 | 0.32 | High | 1079 | 15 | 7/6°C | 35320 | 2860 | 41
53QDMT42-718 | 0.32 | High | 1079 | 20 | 2/1°C | 27245 | 2705 | 41
53QDMT42-718 | 0.32 | High | 1079 | 20 | 24/18°C | 42380 | 3620 | 41
53QDMT42-718 | 0.32 | High | 1079 | 20 | 7/6°C | 33635 | 3075 | 41
53QDMT42-718 | 0.32 | High | 1079 | 27 | 2/1°C | 25565 | 2915 | 41
53QDMT42-718 | 0.32 | High | 1079 | 27 | 24/18°C | 39690 | 3840 | 41
53QDMT42-718 | 0.32 | High | 1079 | 27 | 7/6°C | 31620 | 3310 | 41
53QDMT42-718 | 0.32 | Low | 320 | 15 | 2/1°C | 26330 | 2265 | 41
53QDMT42-718 | 0.32 | Low | 320 | 15 | 24/18°C | 39795 | 3055 | 41
53QDMT42-718 | 0.32 | Low | 320 | 15 | 7/6°C | 32140 | 2630 | 41
53QDMT42-718 | 0.32 | Low | 320 | 20 | 2/1°C | 24795 | 2490 | 41
53QDMT42-718 | 0.32 | Low | 320 | 20 | 24/18°C | 39215 | 3330 | 41
53QDMT42-718 | 0.32 | Low | 320 | 20 | 7/6°C | 30610 | 2830 | 41
53QDMT42-718 | 0.32 | Low | 320 | 27 | 2/1°C | 23270 | 2680 | 41
53QDMT42-718 | 0.32 | Low | 320 | 27 | 24/18°C | 36720 | 3535 | 41
53QDMT42-718 | 0.32 | Low | 320 | 27 | 7/6°C | 28775 | 3040 | 41
53QDMT42-718 | 0.32 | Medium | 573 | 15 | 2/1°C | 27480 | 2360 | 41
53QDMT42-718 | 0.32 | Medium | 573 | 15 | 24/18°C | 41540 | 3190 | 41
53QDMT42-718 | 0.32 | Medium | 573 | 15 | 7/6°C | 33555 | 2745 | 41
53QDMT42-718 | 0.32 | Medium | 573 | 20 | 2/1°C | 25885 | 2595 | 41
53QDMT42-718 | 0.32 | Medium | 573 | 20 | 24/18°C | 40265 | 3475 | 41
53QDMT42-718 | 0.32 | Medium | 573 | 20 | 7/6°C | 31955 | 2945 | 41
53QDMT42-718 | 0.32 | Medium | 573 | 27 | 2/1°C | 24290 | 2805 | 41
53QDMT42-718 | 0.32 | Medium | 573 | 27 | 24/18°C | 37700 | 3690 | 41
53QDMT42-718 | 0.32 | Medium | 573 | 27 | 7/6°C | 30045 | 3180 | 41
53QDMT42-718 | 0.36 | High | 1043 | 15 | 2/1°C | 28515 | 2450 | 41
53QDMT42-718 | 0.36 | High | 1043 | 15 | 24/18°C | 43105 | 3305 | 41
53QDMT42-718 | 0.36 | High | 1043 | 15 | 7/6°C | 34815 | 2850 | 41
53QDMT42-718 | 0.36 | High | 1043 | 20 | 2/1°C | 26855 | 2690 | 41
53QDMT42-718 | 0.36 | High | 1043 | 20 | 24/18°C | 41775 | 3600 | 41
53QDMT42-718 | 0.36 | High | 1043 | 20 | 7/6°C | 33155 | 3060 | 41
53QDMT42-718 | 0.36 | High | 1043 | 27 | 2/1°C | 25200 | 2900 | 41
53QDMT42-718 | 0.36 | High | 1043 | 27 | 24/18°C | 39125 | 3820 | 41
53QDMT42-718 | 0.36 | High | 1043 | 27 | 7/6°C | 31165 | 3295 | 41
53QDMT42-718 | 0.36 | Low | 263 | 15 | 2/1°C | 25955 | 2255 | 41
53QDMT42-718 | 0.36 | Low | 263 | 15 | 24/18°C | 39230 | 3045 | 41
53QDMT42-718 | 0.36 | Low | 263 | 15 | 7/6°C | 31680 | 2620 | 41
53QDMT42-718 | 0.36 | Low | 263 | 20 | 2/1°C | 24445 | 2475 | 41
53QDMT42-718 | 0.36 | Low | 263 | 20 | 24/18°C | 38340 | 3315 | 41
53QDMT42-718 | 0.36 | Low | 263 | 20 | 7/6°C | 30175 | 2815 | 41
53QDMT42-718 | 0.36 | Low | 263 | 27 | 2/1°C | 22935 | 2670 | 41
53QDMT42-718 | 0.36 | Low | 263 | 27 | 24/18°C | 35905 | 3515 | 41
53QDMT42-718 | 0.36 | Low | 263 | 27 | 7/6°C | 28365 | 3030 | 41
53QDMT42-718 | 0.36 | Medium | 533 | 15 | 2/1°C | 27095 | 2355 | 41
53QDMT42-718 | 0.36 | Medium | 533 | 15 | 24/18°C | 40950 | 3175 | 41
53QDMT42-718 | 0.36 | Medium | 533 | 15 | 7/6°C | 33075 | 2735 | 41
53QDMT42-718 | 0.36 | Medium | 533 | 20 | 2/1°C | 25515 | 2585 | 41
53QDMT42-718 | 0.36 | Medium | 533 | 20 | 24/18°C | 39690 | 3460 | 41
53QDMT42-718 | 0.36 | Medium | 533 | 20 | 7/6°C | 31500 | 2935 | 41
53QDMT42-718 | 0.36 | Medium | 533 | 27 | 2/1°C | 23945 | 2790 | 41
53QDMT42-718 | 0.36 | Medium | 533 | 27 | 24/18°C | 37170 | 3670 | 41
53QDMT42-718 | 0.36 | Medium | 533 | 27 | 7/6°C | 29615 | 3165 | 41
53QDMT42-718 | 0.4 | High | 1007 | 15 | 2/1°C | 28100 | 2440 | 41
53QDMT42-718 | 0.4 | High | 1007 | 15 | 24/18°C | 42480 | 3290 | 41
53QDMT42-718 | 0.4 | High | 1007 | 15 | 7/6°C | 34310 | 2835 | 41
53QDMT42-718 | 0.4 | High | 1007 | 20 | 2/1°C | 26470 | 2675 | 41
53QDMT42-718 | 0.4 | High | 1007 | 20 | 24/18°C | 41170 | 3580 | 41
53QDMT42-718 | 0.4 | High | 1007 | 20 | 7/6°C | 32675 | 3040 | 41
53QDMT42-718 | 0.4 | High | 1007 | 27 | 2/1°C | 24835 | 2885 | 41
53QDMT42-718 | 0.4 | High | 1007 | 27 | 24/18°C | 38555 | 3800 | 41
53QDMT42-718 | 0.4 | High | 1007 | 27 | 7/6°C | 30715 | 3275 | 41
53QDMT42-718 | 0.4 | Low | 206 | 15 | 2/1°C | 25575 | 2245 | 41
53QDMT42-718 | 0.4 | Low | 206 | 15 | 24/18°C | 38660 | 3030 | 41
53QDMT42-718 | 0.4 | Low | 206 | 15 | 7/6°C | 31225 | 2610 | 41
53QDMT42-718 | 0.4 | Low | 206 | 20 | 2/1°C | 24090 | 2460 | 41
53QDMT42-718 | 0.4 | Low | 206 | 20 | 24/18°C | 37465 | 3295 | 41
53QDMT42-718 | 0.4 | Low | 206 | 20 | 7/6°C | 29735 | 2800 | 41
53QDMT42-718 | 0.4 | Low | 206 | 27 | 2/1°C | 22600 | 2655 | 41
53QDMT42-718 | 0.4 | Low | 206 | 27 | 24/18°C | 35090 | 3495 | 41
53QDMT42-718 | 0.4 | Low | 206 | 27 | 7/6°C | 27955 | 3015 | 41
53QDMT42-718 | 0.4 | Medium | 493 | 15 | 2/1°C | 26700 | 2345 | 41
53QDMT42-718 | 0.4 | Medium | 493 | 15 | 24/18°C | 40355 | 3160 | 41
53QDMT42-718 | 0.4 | Medium | 493 | 15 | 7/6°C | 32595 | 2725 | 41
53QDMT42-718 | 0.4 | Medium | 493 | 20 | 2/1°C | 25145 | 2570 | 41
53QDMT42-718 | 0.4 | Medium | 493 | 20 | 24/18°C | 39115 | 3440 | 41
53QDMT42-718 | 0.4 | Medium | 493 | 20 | 7/6°C | 31040 | 2920 | 41
53QDMT42-718 | 0.4 | Medium | 493 | 27 | 2/1°C | 23595 | 2770 | 41
53QDMT42-718 | 0.4 | Medium | 493 | 27 | 24/18°C | 36630 | 3650 | 41
53QDMT42-718 | 0.4 | Medium | 493 | 27 | 7/6°C | 29185 | 3145 | 41
53QDMT48-518 | 0 | High | 1370 | 15 | 2/1°C | 40850 | 3040 | 42
53QDMT48-518 | 0 | High | 1370 | 15 | 24/18°C | 61750 | 4105 | 42
53QDMT48-518 | 0 | High | 1370 | 15 | 7/6°C | 49875 | 3535 | 42
53QDMT48-518 | 0 | High | 1370 | 20 | 2/1°C | 38475 | 3340 | 42
53QDMT48-518 | 0 | High | 1370 | 20 | 24/18°C | 59850 | 4480 | 42
53QDMT48-518 | 0 | High | 1370 | 20 | 7/6°C | 47500 | 3795 | 42
53QDMT48-518 | 0 | High | 1370 | 27 | 2/1°C | 36100 | 3610 | 42
53QDMT48-518 | 0 | High | 1370 | 27 | 24/18°C | 56050 | 4750 | 42
53QDMT48-518 | 0 | High | 1370 | 27 | 7/6°C | 44650 | 4100 | 42
53QDMT48-518 | 0 | Low | 715 | 15 | 2/1°C | 37175 | 2800 | 42
53QDMT48-518 | 0 | Low | 715 | 15 | 24/18°C | 56195 | 3775 | 42
53QDMT48-518 | 0 | Low | 715 | 15 | 7/6°C | 45390 | 3255 | 42
53QDMT48-518 | 0 | Low | 715 | 20 | 2/1°C | 35015 | 3075 | 42
53QDMT48-518 | 0 | Low | 715 | 20 | 24/18°C | 54465 | 4125 | 42
53QDMT48-518 | 0 | Low | 715 | 20 | 7/6°C | 43225 | 3495 | 42
53QDMT48-518 | 0 | Low | 715 | 27 | 2/1°C | 32855 | 3320 | 42
53QDMT48-518 | 0 | Low | 715 | 27 | 24/18°C | 51005 | 4370 | 42
53QDMT48-518 | 0 | Low | 715 | 27 | 7/6°C | 40635 | 3770 | 42
53QDMT48-518 | 0 | Medium | 880 | 15 | 2/1°C | 38810 | 2920 | 42
53QDMT48-518 | 0 | Medium | 880 | 15 | 24/18°C | 58665 | 3940 | 42
53QDMT48-518 | 0 | Medium | 880 | 15 | 7/6°C | 47385 | 3390 | 42
53QDMT48-518 | 0 | Medium | 880 | 20 | 2/1°C | 36555 | 3210 | 42
53QDMT48-518 | 0 | Medium | 880 | 20 | 24/18°C | 56860 | 4300 | 42
53QDMT48-518 | 0 | Medium | 880 | 20 | 7/6°C | 45125 | 2645 | 42
53QDMT48-518 | 0 | Medium | 880 | 27 | 2/1°C | 34295 | 3465 | 42
53QDMT48-518 | 0 | Medium | 880 | 27 | 24/18°C | 53250 | 4560 | 42
53QDMT48-518 | 0 | Medium | 880 | 27 | 7/6°C | 42420 | 3935 | 42
53QDMT48-518 | 0.08 | High | 1300 | 15 | 2/1°C | 39820 | 3015 | 42
53QDMT48-518 | 0.08 | High | 1300 | 15 | 24/18°C | 60190 | 4065 | 42
53QDMT48-518 | 0.08 | High | 1300 | 15 | 7/6°C | 48615 | 3500 | 42
53QDMT48-518 | 0.08 | High | 1300 | 20 | 2/1°C | 37505 | 3310 | 42
53QDMT48-518 | 0.08 | High | 1300 | 20 | 24/18°C | 58340 | 4435 | 42
53QDMT48-518 | 0.08 | High | 1300 | 20 | 7/6°C | 46300 | 3755 | 42
53QDMT48-518 | 0.08 | High | 1300 | 27 | 2/1°C | 35190 | 3575 | 42
53QDMT48-518 | 0.08 | High | 1300 | 27 | 24/18°C | 54635 | 4703 | 42
53QDMT48-518 | 0.08 | High | 1300 | 27 | 7/6°C | 43525 | 4060 | 42
53QDMT48-518 | 0.08 | Low | 636 | 15 | 2/1°C | 36240 | 2775 | 42
53QDMT48-518 | 0.08 | Low | 636 | 15 | 24/18°C | 42525 | 3740 | 42
53QDMT48-518 | 0.08 | Low | 636 | 15 | 7/6°C | 44245 | 3225 | 42
53QDMT48-518 | 0.08 | Low | 636 | 20 | 2/1°C | 34135 | 3045 | 42
53QDMT48-518 | 0.08 | Low | 636 | 20 | 24/18°C | 53090 | 4085 | 42
53QDMT48-518 | 0.08 | Low | 636 | 20 | 7/6°C | 41860 | 3460 | 42
53QDMT48-518 | 0.08 | Low | 636 | 27 | 2/1°C | 32025 | 3290 | 42
53QDMT48-518 | 0.08 | Low | 636 | 27 | 24/18°C | 49720 | 4330 | 42
53QDMT48-518 | 0.08 | Low | 636 | 27 | 7/6°C | 39610 | 3735 | 42
53QDMT48-518 | 0.08 | Medium | 803 | 15 | 2/1°C | 37830 | 2895 | 42
53QDMT48-518 | 0.08 | Medium | 803 | 15 | 24/18°C | 57185 | 3900 | 42
53QDMT48-518 | 0.08 | Medium | 803 | 15 | 7/6°C | 46190 | 3360 | 42
53QDMT48-518 | 0.08 | Medium | 803 | 20 | 2/1°C | 35635 | 3180 | 42
53QDMT48-518 | 0.08 | Medium | 803 | 20 | 24/18°C | 55425 | 4257 | 42
53QDMT48-518 | 0.08 | Medium | 803 | 20 | 7/6°C | 43985 | 3010 | 42
53QDMT48-518 | 0.08 | Medium | 803 | 27 | 2/1°C | 33430 | 3420 | 42
53QDMT48-518 | 0.08 | Medium | 803 | 27 | 24/18°C | 51905 | 4515 | 42
53QDMT48-518 | 0.08 | Medium | 803 | 27 | 7/6°C | 41350 | 3895 | 42
53QDMT48-518 | 0.12 | High | 1255 | 15 | 2/1°C | 39305 | 3000 | 42
53QDMT48-518 | 0.12 | High | 1255 | 15 | 24/18°C | 59410 | 4045 | 42
53QDMT48-518 | 0.12 | High | 1255 | 15 | 7/6°C | 47985 | 3485 | 42
53QDMT48-518 | 0.12 | High | 1255 | 20 | 2/1°C | 37020 | 3290 | 42
53QDMT48-518 | 0.12 | High | 1255 | 20 | 24/18°C | 57585 | 4415 | 42
53QDMT48-518 | 0.12 | High | 1255 | 20 | 7/6°C | 45700 | 3735 | 42
53QDMT48-518 | 0.12 | High | 1255 | 27 | 2/1°C | 34735 | 3560 | 42
53QDMT48-518 | 0.12 | High | 1255 | 27 | 24/18°C | 53930 | 4680 | 42
53QDMT48-518 | 0.12 | High | 1255 | 27 | 7/6°C | 42960 | 4040 | 42
53QDMT48-518 | 0.12 | Low | 594 | 15 | 2/1°C | 35770 | 2760 | 42
53QDMT48-518 | 0.12 | Low | 594 | 15 | 24/18°C | 5065 | 3720 | 42
53QDMT48-518 | 0.12 | Low | 594 | 15 | 7/6°C | 43670 | 3210 | 42
53QDMT48-518 | 0.12 | Low | 594 | 20 | 2/1°C | 33690 | 3030 | 42
53QDMT48-518 | 0.12 | Low | 594 | 20 | 24/18°C | 52405 | 4065 | 42
53QDMT48-518 | 0.12 | Low | 594 | 20 | 7/6°C | 40495 | 3445 | 42
53QDMT48-518 | 0.12 | Low | 594 | 27 | 2/1°C | 31610 | 3275 | 42
53QDMT48-518 | 0.12 | Low | 594 | 27 | 24/18°C | 49075 | 4305 | 42
53QDMT48-518 | 0.12 | Low | 594 | 27 | 7/6°C | 39095 | 3715 | 42
53QDMT48-518 | 0.12 | Medium | 770 | 15 | 2/1°C | 37340 | 2880 | 42
53QDMT48-518 | 0.12 | Medium | 770 | 15 | 24/18°C | 56445 | 3880 | 42
53QDMT48-518 | 0.12 | Medium | 770 | 15 | 7/6°C | 45590 | 3340 | 42
53QDMT48-518 | 0.12 | Medium | 770 | 20 | 2/1°C | 35170 | 3160 | 42
53QDMT48-518 | 0.12 | Medium | 770 | 20 | 24/18°C | 54710 | 4235 | 42
53QDMT48-518 | 0.12 | Medium | 770 | 20 | 7/6°C | 43415 | 3190 | 42
53QDMT48-518 | 0.12 | Medium | 770 | 27 | 2/1°C | 33000 | 3420 | 42
53QDMT48-518 | 0.12 | Medium | 770 | 27 | 24/18°C | 51235 | 4495 | 42
53QDMT48-518 | 0.12 | Medium | 770 | 27 | 7/6°C | 40815 | 3875 | 42
53QDMT48-518 | 0.16 | High | 1233 | 15 | 2/1°C | 38790 | 2985 | 42
53QDMT48-518 | 0.16 | High | 1233 | 15 | 24/18°C | 58630 | 4023 | 42
53QDMT48-518 | 0.16 | High | 1233 | 15 | 7/6°C | 47355 | 3465 | 42
53QDMT48-518 | 0.16 | High | 1233 | 20 | 2/1°C | 36535 | 3275 | 42
53QDMT48-518 | 0.16 | High | 1233 | 20 | 24/18°C | 56828 | 4390 | 42
53QDMT48-518 | 0.16 | High | 1233 | 20 | 7/6°C | 45100 | 3715 | 42
53QDMT48-518 | 0.16 | High | 1233 | 27 | 2/1°C | 34280 | 3540 | 42
53QDMT48-518 | 0.16 | High | 1233 | 27 | 24/18°C | 53220 | 4655 | 42
53QDMT48-518 | 0.16 | High | 1233 | 27 | 7/6°C | 42395 | 4018 | 42
53QDMT48-518 | 0.16 | Low | 548 | 15 | 2/1°C | 35300 | 2750 | 42
53QDMT48-518 | 0.16 | Low | 548 | 15 | 24/18°C | 28855 | 3700 | 42
53QDMT48-518 | 0.16 | Low | 548 | 15 | 7/6°C | 43095 | 3193 | 42
53QDMT48-518 | 0.16 | Low | 548 | 20 | 2/1°C | 33250 | 3015 | 42
53QDMT48-518 | 0.16 | Low | 548 | 20 | 24/18°C | 51715 | 4043 | 42
53QDMT48-518 | 0.16 | Low | 548 | 20 | 7/6°C | 40495 | 3425 | 42
53QDMT48-518 | 0.16 | Low | 548 | 27 | 2/1°C | 31195 | 3260 | 42
53QDMT48-518 | 0.16 | Low | 548 | 27 | 24/18°C | 48430 | 4283 | 42
53QDMT48-518 | 0.16 | Low | 548 | 27 | 7/6°C | 38580 | 3695 | 42
53QDMT48-518 | 0.16 | Medium | 733 | 15 | 2/1°C | 36850 | 2865 | 42
53QDMT48-518 | 0.16 | Medium | 733 | 15 | 24/18°C | 55703 | 3860 | 42
53QDMT48-518 | 0.16 | Medium | 733 | 15 | 7/6°C | 44990 | 3323 | 42
53QDMT48-518 | 0.16 | Medium | 733 | 20 | 2/1°C | 34710 | 3145 | 42
53QDMT48-518 | 0.16 | Medium | 733 | 20 | 24/18°C | 53990 | 4213 | 42
53QDMT48-518 | 0.16 | Medium | 733 | 20 | 7/6°C | 42845 | 3370 | 42
53QDMT48-518 | 0.16 | Medium | 733 | 27 | 2/1°C | 32565 | 3375 | 42
53QDMT48-518 | 0.16 | Medium | 733 | 27 | 24/18°C | 50560 | 4470 | 42
53QDMT48-518 | 0.16 | Medium | 733 | 27 | 7/6°C | 40278 | 3855 | 42
53QDMT48-518 | 0.2 | High | 1187 | 15 | 2/1°C | 38270 | 2965 | 42
53QDMT48-518 | 0.2 | High | 1187 | 15 | 24/18°C | 57850 | 4000 | 42
53QDMT48-518 | 0.2 | High | 1187 | 15 | 7/6°C | 46725 | 3445 | 42
53QDMT48-518 | 0.2 | High | 1187 | 20 | 2/1°C | 36045 | 3255 | 42
53QDMT48-518 | 0.2 | High | 1187 | 20 | 24/18°C | 56070 | 4365 | 42
53QDMT48-518 | 0.2 | High | 1187 | 20 | 7/6°C | 44500 | 3695 | 42
53QDMT48-518 | 0.2 | High | 1187 | 27 | 2/1°C | 33820 | 3520 | 42
53QDMT48-518 | 0.2 | High | 1187 | 27 | 24/18°C | 52510 | 4630 | 42
53QDMT48-518 | 0.2 | High | 1187 | 27 | 7/6°C | 41830 | 3995 | 42
53QDMT48-518 | 0.2 | Low | 491 | 15 | 2/1°C | 34830 | 2735 | 42
53QDMT48-518 | 0.2 | Low | 491 | 15 | 24/18°C | 52645 | 3680 | 42
53QDMT48-518 | 0.2 | Low | 491 | 15 | 7/6°C | 42520 | 3175 | 42
53QDMT48-518 | 0.2 | Low | 491 | 20 | 2/1°C | 32805 | 3000 | 42
53QDMT48-518 | 0.2 | Low | 491 | 20 | 24/18°C | 51025 | 4020 | 42
53QDMT48-518 | 0.2 | Low | 491 | 20 | 7/6°C | 40495 | 3405 | 42
53QDMT48-518 | 0.2 | Low | 491 | 27 | 2/1°C | 30780 | 3240 | 42
53QDMT48-518 | 0.2 | Low | 491 | 27 | 24/18°C | 47785 | 4260 | 42
53QDMT48-518 | 0.2 | Low | 491 | 27 | 7/6°C | 38065 | 3675 | 42
53QDMT48-518 | 0.2 | Medium | 693 | 15 | 2/1°C | 36360 | 2850 | 42
53QDMT48-518 | 0.2 | Medium | 693 | 15 | 24/18°C | 54960 | 3840 | 42
53QDMT48-518 | 0.2 | Medium | 693 | 15 | 7/6°C | 44390 | 3305 | 42
53QDMT48-518 | 0.2 | Medium | 693 | 20 | 2/1°C | 34245 | 3130 | 42
53QDMT48-518 | 0.2 | Medium | 693 | 20 | 24/18°C | 53270 | 4190 | 42
53QDMT48-518 | 0.2 | Medium | 693 | 20 | 7/6°C | 42275 | 3550 | 42
53QDMT48-518 | 0.2 | Medium | 693 | 27 | 2/1°C | 32130 | 3330 | 42
53QDMT48-518 | 0.2 | Medium | 693 | 27 | 24/18°C | 49885 | 4445 | 42
53QDMT48-518 | 0.2 | Medium | 693 | 27 | 7/6°C | 39740 | 3835 | 42
53QDMT48-518 | 0.24 | High | 1151 | 15 | 2/1°C | 37755 | 2950
53QDMT48-518 | 0.24 | High | 1151 | 15 | 24/18°C | 57070 | 3980
53QDMT48-518 | 0.24 | High | 1151 | 15 | 7/6°C | 46095 | 3425
53QDMT48-518 | 0.24 | High | 1151 | 20 | 2/1°C | 35560 | 3240
53QDMT48-518 | 0.24 | High | 1151 | 20 | 24/18°C | 55315 | 4340
53QDMT48-518 | 0.24 | High | 1151 | 20 | 7/6°C | 43900 | 3675
53QDMT48-518 | 0.24 | High | 1151 | 27 | 2/1°C | 33365 | 3505
53QDMT48-518 | 0.24 | High | 1151 | 27 | 24/18°C | 51800 | 4605
53QDMT48-518 | 0.24 | High | 1151 | 27 | 7/6°C | 41265 | 3975
53QDMT48-518 | 0.24 | Low | 434 | 15 | 2/1°C | 34360 | 2715
53QDMT48-518 | 0.24 | Low | 434 | 15 | 24/18°C | 51935 | 3660
53QDMT48-518 | 0.24 | Low | 434 | 15 | 7/6°C | 41950 | 3155
53QDMT48-518 | 0.24 | Low | 434 | 20 | 2/1°C | 32365 | 2985
53QDMT48-518 | 0.24 | Low | 434 | 20 | 24/18°C | 50335 | 3995
53QDMT48-518 | 0.24 | Low | 434 | 20 | 7/6°C | 39950 | 3385
53QDMT48-518 | 0.24 | Low | 434 | 27 | 2/1°C | 30365 | 3225
53QDMT48-518 | 0.24 | Low | 434 | 27 | 24/18°C | 47140 | 4240
53QDMT48-518 | 0.24 | Low | 434 | 27 | 7/6°C | 37555 | 3660
53QDMT48-518 | 0.24 | Medium | 653 | 15 | 2/1°C | 35870 | 2835
53QDMT48-518 | 0.24 | Medium | 653 | 15 | 24/18°C | 54220 | 3820
53QDMT48-518 | 0.24 | Medium | 653 | 15 | 7/6°C | 43795 | 3290
53QDMT48-518 | 0.24 | Medium | 653 | 20 | 2/1°C | 33785 | 3110
53QDMT48-518 | 0.24 | Medium | 653 | 20 | 24/18°C | 52550 | 4170
53QDMT48-518 | 0.24 | Medium | 653 | 20 | 7/6°C | 41705 | 3530
53QDMT48-518 | 0.24 | Medium | 653 | 27 | 2/1°C | 31700 | 3340
53QDMT48-518 | 0.24 | Medium | 653 | 27 | 24/18°C | 49210 | 4425
53QDMT48-518 | 0.24 | Medium | 653 | 27 | 7/6°C | 39205 | 3820
53QDMT48-518 | 0.28 | High | 1115 | 15 | 2/1°C | 37240 | 2930 | 43
53QDMT48-518 | 0.28 | High | 1115 | 15 | 24/18°C | 56290 | 3955 | 43
53QDMT48-518 | 0.28 | High | 1115 | 15 | 7/6°C | 45465 | 3405 | 43
53QDMT48-518 | 0.28 | High | 1115 | 20 | 2/1°C | 35075 | 3220 | 43
53QDMT48-518 | 0.28 | High | 1115 | 20 | 24/18°C | 54555 | 4315 | 43
53QDMT48-518 | 0.28 | High | 1115 | 20 | 7/6°C | 43300 | 3655 | 43
53QDMT48-518 | 0.28 | High | 1115 | 27 | 2/1°C | 32910 | 3485 | 43
53QDMT48-518 | 0.28 | High | 1115 | 27 | 24/18°C | 51090 | 4580 | 43
53QDMT48-518 | 0.28 | High | 1115 | 27 | 7/6°C | 40700 | 3955 | 43
53QDMT48-518 | 0.28 | Low | 377 | 15 | 2/1°C | 33890 | 2695 | 43
53QDMT48-518 | 0.28 | Low | 377 | 15 | 24/18°C | 51225 | 3640 | 43
53QDMT48-518 | 0.28 | Low | 377 | 15 | 7/6°C | 41375 | 3135 | 43
53QDMT48-518 | 0.28 | Low | 377 | 20 | 2/1°C | 31920 | 2965 | 43
53QDMT48-518 | 0.28 | Low | 377 | 20 | 24/18°C | 49645 | 3970 | 43
53QDMT48-518 | 0.28 | Low | 377 | 20 | 7/6°C | 39405 | 3365 | 43
53QDMT48-518 | 0.28 | Low | 377 | 27 | 2/1°C | 29950 | 3205 | 43
53QDMT48-518 | 0.28 | Low | 377 | 27 | 24/18°C | 46495 | 4215 | 43
53QDMT48-518 | 0.28 | Low | 377 | 27 | 7/6°C | 37040 | 3640 | 43
53QDMT48-518 | 0.28 | Medium | 613 | 15 | 2/1°C | 35380 | 2815 | 43
53QDMT48-518 | 0.28 | Medium | 613 | 15 | 24/18°C | 53475 | 3800 | 43
53QDMT48-518 | 0.28 | Medium | 613 | 15 | 7/6°C | 43195 | 3270 | 43
53QDMT48-518 | 0.28 | Medium | 613 | 20 | 2/1°C | 33325 | 3090 | 43
53QDMT48-518 | 0.28 | Medium | 613 | 20 | 24/18°C | 51830 | 4145 | 43
53QDMT48-518 | 0.28 | Medium | 613 | 20 | 7/6°C | 41135 | 3510 | 43
53QDMT48-518 | 0.28 | Medium | 613 | 27 | 2/1°C | 31265 | 3345 | 43
53QDMT48-518 | 0.28 | Medium | 613 | 27 | 24/18°C | 48535 | 4400 | 43
53QDMT48-518 | 0.28 | Medium | 613 | 27 | 7/6°C | 38665 | 3800 | 43
53QDMT48-518 | 0.32 | High | 1079 | 15 | 2/1°C | 36725 | 2910 | 43
53QDMT48-518 | 0.32 | High | 1079 | 15 | 24/18°C | 55510 | 3930 | 43
53QDMT48-518 | 0.32 | High | 1079 | 15 | 7/6°C | 44835 | 3385 | 43
53QDMT48-518 | 0.32 | High | 1079 | 20 | 2/1°C | 34590 | 3200 | 43
53QDMT48-518 | 0.32 | High | 1079 | 20 | 24/18°C | 53795 | 4290 | 43
53QDMT48-518 | 0.32 | High | 1079 | 20 | 7/6°C | 42700 | 3635 | 43
53QDMT48-518 | 0.32 | High | 1079 | 27 | 2/1°C | 32455 | 3465 | 43
53QDMT48-518 | 0.32 | High | 1079 | 27 | 24/18°C | 50380 | 4555 | 43
53QDMT48-518 | 0.32 | High | 1079 | 27 | 7/6°C | 40135 | 3935 | 43
53QDMT48-518 | 0.32 | Low | 320 | 15 | 2/1°C | 33420 | 2675 | 43
53QDMT48-518 | 0.32 | Low | 320 | 15 | 24/18°C | 50515 | 3620 | 43
53QDMT48-518 | 0.32 | Low | 320 | 15 | 7/6°C | 40800 | 3115 | 43
53QDMT48-518 | 0.32 | Low | 320 | 20 | 2/1°C | 31475 | 2945 | 43
53QDMT48-518 | 0.32 | Low | 320 | 20 | 24/18°C | 48955 | 3945 | 43
53QDMT48-518 | 0.32 | Low | 320 | 20 | 7/6°C | 38860 | 3345 | 43
53QDMT48-518 | 0.32 | Low | 320 | 27 | 2/1°C | 29535 | 3185 | 43
53QDMT48-518 | 0.32 | Low | 320 | 27 | 24/18°C | 45850 | 4190 | 43
53QDMT48-518 | 0.32 | Low | 320 | 27 | 7/6°C | 36525 | 3620 | 43
53QDMT48-518 | 0.32 | Medium | 573 | 15 | 2/1°C | 34890 | 2795 | 43
53QDMT48-518 | 0.32 | Medium | 573 | 15 | 24/18°C | 52730 | 3780 | 43
53QDMT48-518 | 0.32 | Medium | 573 | 15 | 7/6°C | 42595 | 3250 | 43
53QDMT48-518 | 0.32 | Medium | 573 | 20 | 2/1°C | 32865 | 3070 | 43
53QDMT48-518 | 0.32 | Medium | 573 | 20 | 24/18°C | 51110 | 4120 | 43
53QDMT48-518 | 0.32 | Medium | 573 | 20 | 7/6°C | 40565 | 3490 | 43
53QDMT48-518 | 0.32 | Medium | 573 | 27 | 2/1°C | 30830 | 3350 | 43
53QDMT48-518 | 0.32 | Medium | 573 | 27 | 24/18°C | 47860 | 4375 | 43
53QDMT48-518 | 0.32 | Medium | 573 | 27 | 7/6°C | 38125 | 3780 | 43
53QDMT48-518 | 0.36 | High | 1043 | 15 | 2/1°C | 36210 | 2900 | 43
53QDMT48-518 | 0.36 | High | 1043 | 15 | 24/18°C | 54730 | 3910 | 43
53QDMT48-518 | 0.36 | High | 1043 | 15 | 7/6°C | 44205 | 3370 | 43
53QDMT48-518 | 0.36 | High | 1043 | 20 | 2/1°C | 34105 | 3185 | 43
53QDMT48-518 | 0.36 | High | 1043 | 20 | 24/18°C | 53040 | 4265 | 43
53QDMT48-518 | 0.36 | High | 1043 | 20 | 7/6°C | 42100 | 3615 | 43
53QDMT48-518 | 0.36 | High | 1043 | 27 | 2/1°C | 32000 | 3450 | 43
53QDMT48-518 | 0.36 | High | 1043 | 27 | 24/18°C | 49670 | 4530 | 43
53QDMT48-518 | 0.36 | High | 1043 | 27 | 7/6°C | 39570 | 3915 | 43
53QDMT48-518 | 0.36 | Low | 263 | 15 | 2/1°C | 32955 | 2665 | 43
53QDMT48-518 | 0.36 | Low | 263 | 15 | 24/18°C | 49805 | 3600 | 43
53QDMT48-518 | 0.36 | Low | 263 | 15 | 7/6°C | 40230 | 3100 | 43
53QDMT48-518 | 0.36 | Low | 263 | 20 | 2/1°C | 31035 | 2930 | 43
53QDMT48-518 | 0.36 | Low | 263 | 20 | 24/18°C | 48270 | 3925 | 43
53QDMT48-518 | 0.36 | Low | 263 | 20 | 7/6°C | 38315 | 3325 | 43
53QDMT48-518 | 0.36 | Low | 263 | 27 | 2/1°C | 29120 | 3170 | 43
53QDMT48-518 | 0.36 | Low | 263 | 27 | 24/18°C | 45205 | 4170 | 43
53QDMT48-518 | 0.36 | Low | 263 | 27 | 7/6°C | 36010 | 3600 | 43
53QDMT48-518 | 0.36 | Medium | 533 | 15 | 2/1°C | 34400 | 2785 | 43
53QDMT48-518 | 0.36 | Medium | 533 | 15 | 24/18°C | 51995 | 3760 | 43
53QDMT48-518 | 0.36 | Medium | 533 | 15 | 7/6°C | 42000 | 3235 | 43
53QDMT48-518 | 0.36 | Medium | 533 | 20 | 2/1°C | 32405 | 3055 | 43
53QDMT48-518 | 0.36 | Medium | 533 | 20 | 24/18°C | 50395 | 4095 | 43
53QDMT48-518 | 0.36 | Medium | 533 | 20 | 7/6°C | 39995 | 3470 | 43
53QDMT48-518 | 0.36 | Medium | 533 | 27 | 2/1°C | 30400 | 3325 | 43
53QDMT48-518 | 0.36 | Medium | 533 | 27 | 24/18°C | 47190 | 4350 | 43
53QDMT48-518 | 0.36 | Medium | 533 | 27 | 7/6°C | 37590 | 3760 | 43
53QDMT48-518 | 0.4 | High | 1007 | 15 | 2/1°C | 35690 | 2885 | 43
53QDMT48-518 | 0.4 | High | 1007 | 15 | 24/18°C | 53950 | 3890 | 43
53QDMT48-518 | 0.4 | High | 1007 | 15 | 7/6°C | 43575 | 3350 | 43
53QDMT48-518 | 0.4 | High | 1007 | 20 | 2/1°C | 33620 | 3165 | 43
53QDMT48-518 | 0.4 | High | 1007 | 20 | 24/18°C | 52285 | 4240 | 43
53QDMT48-518 | 0.4 | High | 1007 | 20 | 7/6°C | 41500 | 3590 | 43
53QDMT48-518 | 0.4 | High | 1007 | 27 | 2/1°C | 31540 | 3430 | 43
53QDMT48-518 | 0.4 | High | 1007 | 27 | 24/18°C | 48960 | 4505 | 43
53QDMT48-518 | 0.4 | High | 1007 | 27 | 7/6°C | 39005 | 3890 | 43
53QDMT48-518 | 0.4 | Low | 206 | 15 | 2/1°C | 32485 | 2655 | 43
53QDMT48-518 | 0.4 | Low | 206 | 15 | 24/18°C | 49095 | 3580 | 43
53QDMT48-518 | 0.4 | Low | 206 | 15 | 7/6°C | 39655 | 3085 | 43
53QDMT48-518 | 0.4 | Low | 206 | 20 | 2/1°C | 30595 | 2915 | 43
53QDMT48-518 | 0.4 | Low | 206 | 20 | 24/18°C | 47580 | 3900 | 43
53QDMT48-518 | 0.4 | Low | 206 | 20 | 7/6°C | 37765 | 3305 | 43
53QDMT48-518 | 0.4 | Low | 206 | 27 | 2/1°C | 28705 | 3155 | 43
53QDMT48-518 | 0.4 | Low | 206 | 27 | 24/18°C | 44555 | 4145 | 43
53QDMT48-518 | 0.4 | Low | 206 | 27 | 7/6°C | 35495 | 3580 | 43
53QDMT48-518 | 0.4 | Medium | 493 | 15 | 2/1°C | 33910 | 2770 | 43
53QDMT48-518 | 0.4 | Medium | 493 | 15 | 24/18°C | 51255 | 3735 | 43
53QDMT48-518 | 0.4 | Medium | 493 | 15 | 7/6°C | 41400 | 3215 | 43
53QDMT48-518 | 0.4 | Medium | 493 | 20 | 2/1°C | 31940 | 3040 | 43
53QDMT48-518 | 0.4 | Medium | 493 | 20 | 24/18°C | 49675 | 4070 | 43
53QDMT48-518 | 0.4 | Medium | 493 | 20 | 7/6°C | 39425 | 3445 | 43
53QDMT48-518 | 0.4 | Medium | 493 | 27 | 2/1°C | 29965 | 3295 | 43
53QDMT48-518 | 0.4 | Medium | 493 | 27 | 24/18°C | 46515 | 4325 | 43
53QDMT48-518 | 0.4 | Medium | 493 | 27 | 7/6°C | 37055 | 3735 | 43
53QDMT60-518 | 0 | High | 1470 | 15 | 2/1°C | 47560 | 3325 | 44
53QDMT60-518 | 0 | High | 1470 | 15 | 24/18°C | 71890 | 4485 | 44
53QDMT60-518 | 0 | High | 1470 | 15 | 7/6°C | 58065 | 3860 | 44
53QDMT60-518 | 0 | High | 1470 | 20 | 2/1°C | 44795 | 3655 | 44
53QDMT60-518 | 0 | High | 1470 | 20 | 24/18°C | 69680 | 4895 | 44
53QDMT60-518 | 0 | High | 1470 | 20 | 7/6°C | 55300 | 4155 | 44
53QDMT60-518 | 0 | High | 1470 | 27 | 2/1°C | 42030 | 3945 | 44
53QDMT60-518 | 0 | High | 1470 | 27 | 24/18°C | 65260 | 5200 | 44
53QDMT60-518 | 0 | High | 1470 | 27 | 7/6°C | 51985 | 4485 | 44
53QDMT60-518 | 0 | Low | 860 | 15 | 2/1°C | 43280 | 3055 | 44
53QDMT60-518 | 0 | Low | 860 | 15 | 24/18°C | 65420 | 4130 | 44
53QDMT60-518 | 0 | Low | 860 | 15 | 7/6°C | 52840 | 3555 | 44
53QDMT60-518 | 0 | Low | 860 | 20 | 2/1°C | 40765 | 3365 | 44
53QDMT60-518 | 0 | Low | 860 | 20 | 24/18°C | 63410 | 4515 | 44
53QDMT60-518 | 0 | Low | 860 | 20 | 7/6°C | 50325 | 3820 | 44
53QDMT60-518 | 0 | Low | 860 | 27 | 2/1°C | 38250 | 3630 | 44
53QDMT60-518 | 0 | Low | 860 | 27 | 24/18°C | 59390 | 4780 | 44
53QDMT60-518 | 0 | Low | 860 | 27 | 7/6°C | 47310 | 4130 | 44
53QDMT60-518 | 0 | Medium | 1020 | 15 | 2/1°C | 45185 | 3190 | 44
53QDMT60-518 | 0 | Medium | 1020 | 15 | 24/18°C | 68295 | 4310 | 44
53QDMT60-518 | 0 | Medium | 1020 | 15 | 7/6°C | 55165 | 3710 | 44
53QDMT60-518 | 0 | Medium | 1020 | 20 | 2/1°C | 42555 | 3510 | 44
53QDMT60-518 | 0 | Medium | 1020 | 20 | 24/18°C | 66195 | 4710 | 44
53QDMT60-518 | 0 | Medium | 1020 | 20 | 7/6°C | 52535 | 3990 | 44
53QDMT60-518 | 0 | Medium | 1020 | 27 | 2/1°C | 39930 | 3790 | 44
53QDMT60-518 | 0 | Medium | 1020 | 27 | 24/18°C | 62000 | 4990 | 44
53QDMT60-518 | 0 | Medium | 1020 | 27 | 7/6°C | 49385 | 4310 | 44
53QDMT60-518 | 0.08 | High | 1405 | 15 | 2/1°C | 46360 | 3295 | 44
53QDMT60-518 | 0.08 | High | 1405 | 15 | 24/18°C | 70070 | 4445 | 44
53QDMT60-518 | 0.08 | High | 1405 | 15 | 7/6°C | 56595 | 3825 | 44
53QDMT60-518 | 0.08 | High | 1405 | 20 | 2/1°C | 43665 | 3620 | 44
53QDMT60-518 | 0.08 | High | 1405 | 20 | 24/18°C | 67920 | 3345 | 44
53QDMT60-518 | 0.08 | High | 1405 | 20 | 7/6°C | 53900 | 4115 | 44
53QDMT60-518 | 0.08 | High | 1405 | 27 | 2/1°C | 40970 | 3505 | 44
53QDMT60-518 | 0.08 | High | 1405 | 27 | 24/18°C | 67510 | 5150 | 44
53QDMT60-518 | 0.08 | High | 1405 | 27 | 7/6°C | 50670 | 4440 | 44
53QDMT60-518 | 0.08 | Low | 800 | 15 | 2/1°C | 41935 | 3025 | 44
53QDMT60-518 | 0.08 | Low | 800 | 15 | 24/18°C | 63765 | 4090 | 44
53QDMT60-518 | 0.08 | Low | 800 | 15 | 7/6°C | 51505 | 3520 | 44
53QDMT60-518 | 0.08 | Low | 800 | 20 | 2/1°C | 39735 | 3335 | 44
53QDMT60-518 | 0.08 | Low | 800 | 20 | 24/18°C | 61810 | 4465 | 44
53QDMT60-518 | 0.08 | Low | 800 | 20 | 7/6°C | 49055 | 3780 | 44
53QDMT60-518 | 0.08 | Low | 800 | 27 | 2/1°C | 37285 | 3595 | 44
53QDMT60-518 | 0.08 | Low | 800 | 27 | 24/18°C | 57890 | 4735 | 44
53QDMT60-518 | 0.08 | Low | 800 | 27 | 7/6°C | 46115 | 4100 | 44
53QDMT60-518 | 0.08 | Medium | 968 | 15 | 2/1°C | 44045 | 3160 | 44
53QDMT60-518 | 0.08 | Medium | 968 | 15 | 24/18°C | 66570 | 4270 | 44
53QDMT60-518 | 0.08 | Medium | 968 | 15 | 7/6°C | 53770 | 3675 | 44
53QDMT60-518 | 0.08 | Medium | 968 | 20 | 2/1°C | 41480 | 3475 | 44
53QDMT60-518 | 0.08 | Medium | 968 | 20 | 24/18°C | 64525 | 4560 | 44
53QDMT60-518 | 0.08 | Medium | 968 | 20 | 7/6°C | 51205 | 3950 | 44
53QDMT60-518 | 0.08 | Medium | 968 | 27 | 2/1°C | 38920 | 3755 | 44
53QDMT60-518 | 0.08 | Medium | 968 | 27 | 24/18°C | 60435 | 4940 | 44
53QDMT60-518 | 0.08 | Medium | 968 | 27 | 7/6°C | 48135 | 4270 | 44
53QDMT60-518 | 0.12 | High | 1380 | 15 | 2/1°C | 45755 | 3275 | 44
53QDMT60-518 | 0.12 | High | 1380 | 15 | 24/18°C | 69160 | 4420 | 44
53QDMT60-518 | 0.12 | High | 1380 | 15 | 7/6°C | 55860 | 3805 | 44
53QDMT60-518 | 0.12 | High | 1380 | 20 | 2/1°C | 43095 | 3600 | 44
53QDMT60-518 | 0.12 | High | 1380 | 20 | 24/18°C | 67035 | 4820 | 44
53QDMT60-518 | 0.12 | High | 1380 | 20 | 7/6°C | 53200 | 4090 | 44
53QDMT60-518 | 0.12 | High | 1380 | 27 | 2/1°C | 40435 | 3285 | 44
53QDMT60-518 | 0.12 | High | 1380 | 27 | 24/18°C | 62790 | 5125 | 44
53QDMT60-518 | 0.12 | High | 1380 | 27 | 7/6°C | 50015 | 4420 | 44
53QDMT60-518 | 0.12 | Low | 762 | 15 | 2/1°C | 40640 | 3010 | 44
53QDMT60-518 | 0.12 | Low | 762 | 15 | 24/18°C | 62940 | 4065 | 44
53QDMT60-518 | 0.12 | Low | 762 | 15 | 7/6°C | 50835 | 3505 | 44
53QDMT60-518 | 0.12 | Low | 762 | 20 | 2/1°C | 39220 | 3315 | 44
53QDMT60-518 | 0.12 | Low | 762 | 20 | 24/18°C | 61005 | 4435 | 44
53QDMT60-518 | 0.12 | Low | 762 | 20 | 7/6°C | 48415 | 3760 | 44
53QDMT60-518 | 0.12 | Low | 762 | 27 | 2/1°C | 36800 | 3580 | 44
53QDMT60-518 | 0.12 | Low | 762 | 27 | 24/18°C | 57140 | 4715 | 44
53QDMT60-518 | 0.12 | Low | 762 | 27 | 7/6°C | 45515 | 4085 | 44
53QDMT60-518 | 0.12 | Medium | 948 | 15 | 2/1°C | 43470 | 3145 | 44
53QDMT60-518 | 0.12 | Medium | 948 | 15 | 24/18°C | 65705 | 4245 | 44
53QDMT60-518 | 0.12 | Medium | 948 | 15 | 7/6°C | 53070 | 3655 | 44
53QDMT60-518 | 0.12 | Medium | 948 | 20 | 2/1°C | 40945 | 3460 | 44
53QDMT60-518 | 0.12 | Medium | 948 | 20 | 24/18°C | 63685 | 4630 | 44
53QDMT60-518 | 0.12 | Medium | 948 | 20 | 7/6°C | 50540 | 3930 | 44
53QDMT60-518 | 0.12 | Medium | 948 | 27 | 2/1°C | 38415 | 3735 | 44
53QDMT60-518 | 0.12 | Medium | 948 | 27 | 24/18°C | 59650 | 4920 | 44
53QDMT60-518 | 0.12 | Medium | 948 | 27 | 7/6°C | 47510 | 4245 | 44
53QDMT60-518 | 0.16 | High | 1345 | 15 | 2/1°C | 45153 | 3258 | 44
53QDMT60-518 | 0.16 | High | 1345 | 15 | 24/18°C | 68250 | 4400 | 44
53QDMT60-518 | 0.16 | High | 1345 | 15 | 7/6°C | 55125 | 3785 | 44
53QDMT60-518 | 0.16 | High | 1345 | 20 | 2/1°C | 42528 | 3580 | 44
53QDMT60-518 | 0.16 | High | 1345 | 20 | 24/18°C | 66155 | 4795 | 44
53QDMT60-518 | 0.16 | High | 1345 | 20 | 7/6°C | 52500 | 4068 | 44
53QDMT60-518 | 0.16 | High | 1345 | 27 | 2/1°C | 39903 | 3065 | 44
53QDMT60-518 | 0.16 | High | 1345 | 27 | 24/18°C | 69760 | 5095 | 44
53QDMT60-518 | 0.16 | High | 1345 | 27 | 7/6°C | 49355 | 4395 | 44
53QDMT60-518 | 0.16 | Low | 728 | 15 | 2/1°C | 40590 | 2995 | 44
53QDMT60-518 | 0.16 | Low | 728 | 15 | 24/18°C | 62110 | 4050 | 44
53QDMT60-518 | 0.16 | Low | 728 | 15 | 7/6°C | 50165 | 3485 | 44
53QDMT60-518 | 0.16 | Low | 728 | 20 | 2/1°C | 38703 | 3298 | 44
53QDMT60-518 | 0.16 | Low | 728 | 20 | 24/18°C | 60205 | 4410 | 44
53QDMT60-518 | 0.16 | Low | 728 | 20 | 7/6°C | 47778 | 3740 | 44
53QDMT60-518 | 0.16 | Low | 728 | 27 | 2/1°C | 36315 | 3560 | 44
53QDMT60-518 | 0.16 | Low | 728 | 27 | 24/18°C | 56385 | 4690 | 44
53QDMT60-518 | 0.16 | Low | 728 | 27 | 7/6°C | 44915 | 4070 | 44
53QDMT60-518 | 0.16 | Medium | 914 | 15 | 2/1°C | 42898 | 3128 | 44
53QDMT60-518 | 0.16 | Medium | 914 | 15 | 24/18°C | 64840 | 4225 | 44
53QDMT60-518 | 0.16 | Medium | 914 | 15 | 7/6°C | 52370 | 3635 | 44
53QDMT60-518 | 0.16 | Medium | 914 | 20 | 2/1°C | 40405 | 3440 | 44
53QDMT60-518 | 0.16 | Medium | 914 | 20 | 24/18°C | 62850 | 4410 | 44
53QDMT60-518 | 0.16 | Medium | 914 | 20 | 7/6°C | 49875 | 3908 | 44
53QDMT60-518 | 0.16 | Medium | 914 | 27 | 2/1°C | 37910 | 3715 | 44
53QDMT60-518 | 0.16 | Medium | 914 | 27 | 24/18°C | 58865 | 4890 | 44
53QDMT60-518 | 0.16 | Medium | 914 | 27 | 7/6°C | 46885 | 4223 | 44
53QDMT60-518 | 0.2 | High | 1314 | 15 | 2/1°C | 44550 | 3240 | 44
53QDMT60-518 | 0.2 | High | 1314 | 15 | 24/18°C | 67340 | 4370 | 44
53QDMT60-518 | 0.2 | High | 1314 | 15 | 7/6°C | 54390 | 3765 | 44
53QDMT60-518 | 0.2 | High | 1314 | 20 | 2/1°C | 41960 | 3560 | 44
53QDMT60-518 | 0.2 | High | 1314 | 20 | 24/18°C | 65270 | 4770 | 44
53QDMT60-518 | 0.2 | High | 1314 | 20 | 7/6°C | 51800 | 4045 | 44
53QDMT60-518 | 0.2 | High | 1314 | 27 | 2/1°C | 39370 | 3845 | 44
53QDMT60-518 | 0.2 | High | 1314 | 27 | 24/18°C | 61130 | 5070 | 44
53QDMT60-518 | 0.2 | High | 1314 | 27 | 7/6°C | 48695 | 4370 | 44
53QDMT60-518 | 0.2 | Low | 703 | 15 | 2/1°C | 40540 | 2980 | 44
53QDMT60-518 | 0.2 | Low | 703 | 15 | 24/18°C | 61280 | 4025 | 44
53QDMT60-518 | 0.2 | Low | 703 | 15 | 7/6°C | 49495 | 3465 | 44
53QDMT60-518 | 0.2 | Low | 703 | 20 | 2/1°C | 38185 | 3280 | 44
53QDMT60-518 | 0.2 | Low | 703 | 20 | 24/18°C | 59400 | 4395 | 44
53QDMT60-518 | 0.2 | Low | 703 | 20 | 7/6°C | 47140 | 3720 | 44
53QDMT60-518 | 0.2 | Low | 703 | 27 | 2/1°C | 35830 | 3540 | 44
53QDMT60-518 | 0.2 | Low | 703 | 27 | 24/18°C | 55630 | 4660 | 44
53QDMT60-518 | 0.2 | Low | 703 | 27 | 7/6°C | 44315 | 4055 | 44
53QDMT60-518 | 0.2 | Medium | 880 | 15 | 2/1°C | 42325 | 3110 | 44
53QDMT60-518 | 0.2 | Medium | 880 | 15 | 24/18°C | 63975 | 4200 | 44
53QDMT60-518 | 0.2 | Medium | 880 | 15 | 7/6°C | 51670 | 3615 | 44
53QDMT60-518 | 0.2 | Medium | 880 | 20 | 2/1°C | 39865 | 3420 | 44
53QDMT60-518 | 0.2 | Medium | 880 | 20 | 24/18°C | 62010 | 4585 | 44
53QDMT60-518 | 0.2 | Medium | 880 | 20 | 7/6°C | 49210 | 3885 | 44
53QDMT60-518 | 0.2 | Medium | 880 | 27 | 2/1°C | 37405 | 3695 | 44
53QDMT60-518 | 0.2 | Medium | 880 | 27 | 24/18°C | 58075 | 4865 | 44
53QDMT60-518 | 0.2 | Medium | 880 | 27 | 7/6°C | 46260 | 4200 | 44
53QDMT60-518 | 0.24 | High | 1283 | 15 | 2/1°C | 43950 | 3225
53QDMT60-518 | 0.24 | High | 1283 | 15 | 24/18°C | 66430 | 4345
53QDMT60-518 | 0.24 | High | 1283 | 15 | 7/6°C | 53655 | 3745
53QDMT60-518 | 0.24 | High | 1283 | 20 | 2/1°C | 41395 | 3545
53QDMT60-518 | 0.24 | High | 1283 | 20 | 24/18°C | 64390 | 4745
53QDMT60-518 | 0.24 | High | 1283 | 20 | 7/6°C | 51100 | 4025
53QDMT60-518 | 0.24 | High | 1283 | 27 | 2/1°C | 38840 | 3825
53QDMT60-518 | 0.24 | High | 1283 | 27 | 24/18°C | 60300 | 5045
53QDMT60-518 | 0.24 | High | 1283 | 27 | 7/6°C | 48035 | 4350
53QDMT60-518 | 0.24 | Low | 678 | 15 | 2/1°C | 39995 | 2965
53QDMT60-518 | 0.24 | Low | 678 | 15 | 24/18°C | 60455 | 4000
53QDMT60-518 | 0.24 | Low | 678 | 15 | 7/6°C | 48830 | 3450
53QDMT60-518 | 0.24 | Low | 678 | 20 | 2/1°C | 37670 | 3265
53QDMT60-518 | 0.24 | Low | 678 | 20 | 24/18°C | 58595 | 4370
53QDMT60-518 | 0.24 | Low | 678 | 20 | 7/6°C | 46505 | 3705
53QDMT60-518 | 0.24 | Low | 678 | 27 | 2/1°C | 35345 | 3520
53QDMT60-518 | 0.24 | Low | 678 | 27 | 24/18°C | 54875 | 4640
53QDMT60-518 | 0.24 | Low | 678 | 27 | 7/6°C | 43715 | 4000
53QDMT60-518 | 0.24 | Medium | 846 | 15 | 2/1°C | 41755 | 3095
53QDMT60-518 | 0.24 | Medium | 846 | 15 | 24/18°C | 63110 | 4175
53QDMT60-518 | 0.24 | Medium | 846 | 15 | 7/6°C | 50975 | 3595
53QDMT60-518 | 0.24 | Medium | 846 | 20 | 2/1°C | 39330 | 3405
53QDMT60-518 | 0.24 | Medium | 846 | 20 | 24/18°C | 61170 | 4560
53QDMT60-518 | 0.24 | Medium | 846 | 20 | 7/6°C | 48545 | 3865
53QDMT60-518 | 0.24 | Medium | 846 | 27 | 2/1°C | 36900 | 3675
53QDMT60-518 | 0.24 | Medium | 846 | 27 | 24/18°C | 57290 | 4840
53QDMT60-518 | 0.24 | Medium | 846 | 27 | 7/6°C | 45635 | 4180
53QDMT60-518 | 0.28 | High | 1252 | 15 | 2/1°C | 43350 | 3205 | 45
53QDMT60-518 | 0.28 | High | 1252 | 15 | 24/18°C | 65520 | 4320 | 45
53QDMT60-518 | 0.28 | High | 1252 | 15 | 7/6°C | 52920 | 3725 | 45
53QDMT60-518 | 0.28 | High | 1252 | 20 | 2/1°C | 40830 | 3525 | 45
53QDMT60-518 | 0.28 | High | 1252 | 20 | 24/18°C | 63505 | 4720 | 45
53QDMT60-518 | 0.28 | High | 1252 | 20 | 7/6°C | 50400 | 4005 | 45
53QDMT60-518 | 0.28 | High | 1252 | 27 | 2/1°C | 38305 | 3805 | 45
53QDMT60-518 | 0.28 | High | 1252 | 27 | 24/18°C | 59470 | 5015 | 45
53QDMT60-518 | 0.28 | High | 1252 | 27 | 7/6°C | 47375 | 4325 | 45
53QDMT60-518 | 0.28 | Low | 653 | 15 | 2/1°C | 39450 | 2950 | 45
53QDMT60-518 | 0.28 | Low | 653 | 15 | 24/18°C | 59625 | 3975 | 45
53QDMT60-518 | 0.28 | Low | 653 | 15 | 7/6°C | 48160 | 3430 | 45
53QDMT60-518 | 0.28 | Low | 653 | 20 | 2/1°C | 37155 | 3245 | 45
53QDMT60-518 | 0.28 | Low | 653 | 20 | 24/18°C | 57790 | 4345 | 45
53QDMT60-518 | 0.28 | Low | 653 | 20 | 7/6°C | 45865 | 3685 | 45
53QDMT60-518 | 0.28 | Low | 653 | 27 | 2/1°C | 34860 | 3500 | 45
53QDMT60-518 | 0.28 | Low | 653 | 27 | 24/18°C | 54120 | 4615 | 45
53QDMT60-518 | 0.28 | Low | 653 | 27 | 7/6°C | 43115 | 3938 | 45
53QDMT60-518 | 0.28 | Medium | 812 | 15 | 2/1°C | 41185 | 3080 | 45
53QDMT60-518 | 0.28 | Medium | 812 | 15 | 24/18°C | 62245 | 4150 | 45
53QDMT60-518 | 0.28 | Medium | 812 | 15 | 7/6°C | 50275 | 3575 | 45
53QDMT60-518 | 0.28 | Medium | 812 | 20 | 2/1°C | 38790 | 3385 | 45
53QDMT60-518 | 0.28 | Medium | 812 | 20 | 24/18°C | 60330 | 4530 | 45
53QDMT60-518 | 0.28 | Medium | 812 | 20 | 7/6°C | 47880 | 3845 | 45
53QDMT60-518 | 0.28 | Medium | 812 | 27 | 2/1°C | 36390 | 3655 | 45
53QDMT60-518 | 0.28 | Medium | 812 | 27 | 24/18°C | 56500 | 4815 | 45
53QDMT60-518 | 0.28 | Medium | 812 | 27 | 7/6°C | 45010 | 4155 | 45
53QDMT60-518 | 0.32 | High | 1221 | 15 | 2/1°C | 42750 | 3185 | 45
53QDMT60-518 | 0.32 | High | 1221 | 15 | 24/18°C | 64610 | 4295 | 45
53QDMT60-518 | 0.32 | High | 1221 | 15 | 7/6°C | 52185 | 3705 | 45
53QDMT60-518 | 0.32 | High | 1221 | 20 | 2/1°C | 40265 | 3505 | 45
53QDMT60-518 | 0.32 | High | 1221 | 20 | 24/18°C | 62620 | 4695 | 45
53QDMT60-518 | 0.32 | High | 1221 | 20 | 7/6°C | 49700 | 3985 | 45
53QDMT60-518 | 0.32 | High | 1221 | 27 | 2/1°C | 37770 | 3785 | 45
53QDMT60-518 | 0.32 | High | 1221 | 27 | 24/18°C | 58640 | 4985 | 45
53QDMT60-518 | 0.32 | High | 1221 | 27 | 7/6°C | 46715 | 4300 | 45
53QDMT60-518 | 0.32 | Low | 628 | 15 | 2/1°C | 38905 | 2935 | 45
53QDMT60-518 | 0.32 | Low | 628 | 15 | 24/18°C | 58795 | 3950 | 45
53QDMT60-518 | 0.32 | Low | 628 | 15 | 7/6°C | 47490 | 3410 | 45
53QDMT60-518 | 0.32 | Low | 628 | 20 | 2/1°C | 36640 | 3225 | 45
53QDMT60-518 | 0.32 | Low | 628 | 20 | 24/18°C | 56985 | 4320 | 45
53QDMT60-518 | 0.32 | Low | 628 | 20 | 7/6°C | 45225 | 3665 | 45
53QDMT60-518 | 0.32 | Low | 628 | 27 | 2/1°C | 34375 | 3480 | 45
53QDMT60-518 | 0.32 | Low | 628 | 27 | 24/18°C | 53365 | 4590 | 45
53QDMT60-518 | 0.32 | Low | 628 | 27 | 7/6°C | 42515 | 3876 | 45
53QDMT60-518 | 0.32 | Medium | 778 | 15 | 2/1°C | 40615 | 3065 | 45
53QDMT60-518 | 0.32 | Medium | 778 | 15 | 24/18°C | 61380 | 4125 | 45
53QDMT60-518 | 0.32 | Medium | 778 | 15 | 7/6°C | 49575 | 3555 | 45
53QDMT60-518 | 0.32 | Medium | 778 | 20 | 2/1°C | 38250 | 3365 | 45
53QDMT60-518 | 0.32 | Medium | 778 | 20 | 24/18°C | 59490 | 4500 | 45
53QDMT60-518 | 0.32 | Medium | 778 | 20 | 7/6°C | 47215 | 3825 | 45
53QDMT60-518 | 0.32 | Medium | 778 | 27 | 2/1°C | 35880 | 3635 | 45
53QDMT60-518 | 0.32 | Medium | 778 | 27 | 24/18°C | 55710 | 4790 | 45
53QDMT60-518 | 0.32 | Medium | 778 | 27 | 7/6°C | 44385 | 4130 | 45
53QDMT60-518 | 0.36 | High | 1190 | 15 | 2/1°C | 42150 | 3170 | 45
53QDMT60-518 | 0.36 | High | 1190 | 15 | 24/18°C | 63700 | 4270 | 45
53QDMT60-518 | 0.36 | High | 1190 | 15 | 7/6°C | 51450 | 3685 | 45
53QDMT60-518 | 0.36 | High | 1190 | 20 | 2/1°C | 39700 | 3500 | 45
53QDMT60-518 | 0.36 | High | 1190 | 20 | 24/18°C | 61740 | 4670 | 45
53QDMT60-518 | 0.36 | High | 1190 | 20 | 7/6°C | 49000 | 3965 | 45
53QDMT60-518 | 0.36 | High | 1190 | 27 | 2/1°C | 37240 | 3765 | 45
53QDMT60-518 | 0.36 | High | 1190 | 27 | 24/18°C | 57810 | 4960 | 45
53QDMT60-518 | 0.36 | High | 1190 | 27 | 7/6°C | 46055 | 4280 | 45
53QDMT60-518 | 0.36 | Low | 603 | 15 | 2/1°C | 38360 | 2920 | 45
53QDMT60-518 | 0.36 | Low | 603 | 15 | 24/18°C | 57970 | 3930 | 45
53QDMT60-518 | 0.36 | Low | 603 | 15 | 7/6°C | 46825 | 3390 | 45
53QDMT60-518 | 0.36 | Low | 603 | 20 | 2/1°C | 36125 | 3210 | 45
53QDMT60-518 | 0.36 | Low | 603 | 20 | 24/18°C | 56185 | 4300 | 45
53QDMT60-518 | 0.36 | Low | 603 | 20 | 7/6°C | 44590 | 3645 | 45
53QDMT60-518 | 0.36 | Low | 603 | 27 | 2/1°C | 33890 | 3465 | 45
53QDMT60-518 | 0.36 | Low | 603 | 27 | 24/18°C | 52610 | 4565 | 45
53QDMT60-518 | 0.36 | Low | 603 | 27 | 7/6°C | 41915 | 3896 | 45
53QDMT60-518 | 0.36 | Medium | 744 | 15 | 2/1°C | 40045 | 3045 | 45
53QDMT60-518 | 0.36 | Medium | 744 | 15 | 24/18°C | 60515 | 4100 | 45
53QDMT60-518 | 0.36 | Medium | 744 | 15 | 7/6°C | 48880 | 3535 | 45
53QDMT60-518 | 0.36 | Medium | 744 | 20 | 2/1°C | 37715 | 3350 | 45
53QDMT60-518 | 0.36 | Medium | 744 | 20 | 24/18°C | 58655 | 4480 | 45
53QDMT60-518 | 0.36 | Medium | 744 | 20 | 7/6°C | 46550 | 3805 | 45
53QDMT60-518 | 0.36 | Medium | 744 | 27 | 2/1°C | 35375 | 3615 | 45
53QDMT60-518 | 0.36 | Medium | 744 | 27 | 24/18°C | 54925 | 4765 | 45
53QDMT60-518 | 0.36 | Medium | 744 | 27 | 7/6°C | 43755 | 4110 | 45
53QDMT60-518 | 0.4 | High | 1159 | 15 | 2/1°C | 41545 | 3150 | 45
53QDMT60-518 | 0.4 | High | 1159 | 15 | 24/18°C | 62790 | 4245 | 45
53QDMT60-518 | 0.4 | High | 1159 | 15 | 7/6°C | 50715 | 3660 | 45
53QDMT60-518 | 0.4 | High | 1159 | 20 | 2/1°C | 39130 | 3470 | 45
53QDMT60-518 | 0.4 | High | 1159 | 20 | 24/18°C | 60860 | 4645 | 45
53QDMT60-518 | 0.4 | High | 1159 | 20 | 7/6°C | 48300 | 3940 | 45
53QDMT60-518 | 0.4 | High | 1159 | 27 | 2/1°C | 36705 | 3745 | 45
53QDMT60-518 | 0.4 | High | 1159 | 27 | 24/18°C | 56980 | 4935 | 45
53QDMT60-518 | 0.4 | High | 1159 | 27 | 7/6°C | 45395 | 4255 | 45
53QDMT60-518 | 0.4 | Low | 578 | 15 | 2/1°C | 37810 | 2900 | 45
53QDMT60-518 | 0.4 | Low | 578 | 15 | 24/18°C | 57140 | 3905 | 45
53QDMT60-518 | 0.4 | Low | 578 | 15 | 7/6°C | 46155 | 3370 | 45
53QDMT60-518 | 0.4 | Low | 578 | 20 | 2/1°C | 35610 | 3195 | 45
53QDMT60-518 | 0.4 | Low | 578 | 20 | 24/18°C | 55385 | 4275 | 45
53QDMT60-518 | 0.4 | Low | 578 | 20 | 7/6°C | 43955 | 3625 | 45
53QDMT60-518 | 0.4 | Low | 578 | 27 | 2/1°C | 33405 | 3445 | 45
53QDMT60-518 | 0.4 | Low | 578 | 27 | 24/18°C | 51855 | 4540 | 45
53QDMT60-518 | 0.4 | Low | 578 | 27 | 7/6°C | 41310 | 3915 | 45
53QDMT60-518 | 0.4 | Medium | 710 | 15 | 2/1°C | 39470 | 3025 | 45
53QDMT60-518 | 0.4 | Medium | 710 | 15 | 24/18°C | 59650 | 4075 | 45
53QDMT60-518 | 0.4 | Medium | 710 | 15 | 7/6°C | 48180 | 3515 | 45
53QDMT60-518 | 0.4 | Medium | 710 | 20 | 2/1°C | 37175 | 3330 | 45
53QDMT60-518 | 0.4 | Medium | 710 | 20 | 24/18°C | 57820 | 4460 | 45
53QDMT60-518 | 0.4 | Medium | 710 | 20 | 7/6°C | 45885 | 3785 | 45
53QDMT60-518 | 0.4 | Medium | 710 | 27 | 2/1°C | 34870 | 3595 | 45
53QDMT60-518 | 0.4 | Medium | 710 | 27 | 24/18°C | 54135 | 4740 | 45
53QDMT60-518 | 0.4 | Medium | 710 | 27 | 7/6°C | 43125 | 4085 | 45